## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Low Voltage Cables - Mains/Submains (Pre-Energisation) | [5 empty] | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Pre-Energisation)
section | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Cable Size and Labelling
signoff | Checked By (Heyday):
section | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC/1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
signoff | Checked By (Heyday):
section | Continuity Testing
checkpoint | Red Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | White Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Blue Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Neutral
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Earth
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checklist | Low Voltage Cables - Mains/Submains (Energised) | [5 empty] | Testing & Commissioning - Low Voltage Cables - Mains/Submains (Energised)
section | Phase Rotation
checkpoint | Direction
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
section | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
checklist | Distribution Boards (Pre-Energisation) | [5 empty] | Testing & Commissioning - Distribution Boards (Pre-Energisation)
section | Physical Checks
checkpoint | Confirm board's dimensions are in accordance with approved shop drawings (provide drawings reference in the Comments section)
checkpoint | Confirm correct circuit identification and labelling
checkpoint | Confirm the board busbars and cables are tighten as per manufacturer recommendations and standards. Provide applied torque in the Comment section
checkpoint | Confirm correct phase identification of busbars and cables inside the board
checkpoint | Confirm correct size of earthing conductors
checkpoint | Confirm no visual damage to the equipment or meters. Mark the observed issues in a Comment section (if any)
section | Mechanical Checks
checkpoint | Repeat manual closing and opening of moulded case circuit breakers for 3 times
checkpoint | Repeat manual closing and opening of miniature circuit breakers for 3 times
checkpoint | Repeat mounting and dismounting of power fuses for 1 time
checkpoint | Repeat mounting and dismounting of control fuses 1 time
checkpoint | Conduct the torque test for all bolted connections and confirm the torque is in accordance with manufacturer recommendations and standards.
checkpoint | Conduct pull test for all cables connected to MCBs and Termination blocks
section | Preliminary Checks
checkpoint | 1. Confirm all fuses Removed in board’s Control Sections
checkpoint | 2. Confirm Main Breaker Closed
checkpoint | 3. Confirm Outgoing Breakers Closed
section | Insulation Resistance (500V)
checkpoint | 1. Between L1 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 2. Between L2 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 3. Between L3 Phase and Neutral
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 4. Between Neutral and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 5. Between L1 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 6. Between L2 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 7. Between L3 Phase and Earth
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 8. Between L1 Phase and L2 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 9. Between L1 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
checkpoint | 10. Between L2 Phase and L3 Phase
button | >10MΩ | YES,NO
textbox | Actual Reading if <10MΩ
signoff | Checked By (Heyday):
section | Earth Continuity Test
checkpoint | Earth Continuity
textbox | Incoming Earth Size (mm²)
textbox | From (MSB/DB)
textbox | Resistance (Ω)
signoff | Checked By (Heyday):
checklist | Distribution Boards (Energised) | [5 empty] | Testing & Commissioning - Distribution Boards (Energised)
section | Phase Voltage Reading
checkpoint | Red- Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
checkpoint | Neutral - Earth
textbox | Voltage (V)
checkpoint | Red- White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
section | Phase Rotation
checkpoint | Direction
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
checklist | Low Voltage Busduct (Pre-Energisation) | [5 empty] | Testing & Commissioning - Low Voltage Busduct (Pre-Energisation)
section | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Colour Code
checkpoint | Correct Size and Labelling
checkpoint | Correct Routing
signoff | Checked By (Heyday):
section | Continuity Testing
checkpoint | Red Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | White Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Blue Phase
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Neutral
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
checkpoint | Earth
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
section | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 500VDC, 1000VDC) | >500MΩ,>1000MΩ,N/A
textbox | Actual Reading if <500MΩ/<1000MΩ
signoff | Checked By (Heyday):
checklist | Low Voltage Busduct (Energised) | [5 empty] | Testing & Commissioning - Low Voltage Busduct (Energised)
section | Phase Rotation
checkpoint | Direction
button | Direction | Clockwise,Anti-Clockwise
signoff | Checked By (Heyday):
section | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
checklist | Subcircuits (Pre-Energisation) | [5 empty] | Testing & Commissioning - Subcircuits (Pre-Energisation)
section | Pre-requisite Works
checkpoint | Insulation Damage
checkpoint | Correct Type of Termination
checkpoint | Correct Colour Code
checkpoint | Correct Outlet Rating and Size
signoff | Checked By (Heyday):
checkpoint | Earth Continuity
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checkpoint | Polarity Check
button | No Transposition | YES,NO
button | Switch in Active | YES,NO
signoff | Checked By (Heyday):
section | Insulation Resistance
checkpoint | R-W
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-B
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | B-N
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | R-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | W-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | B-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
checkpoint | N-E
button | Insulation Resistance shall not be less than 1MΩ (Tested at 250VDC/500VDC) | >200MΩ,>500MΩ,N/A
textbox | Actual Reading if <200MΩ/<500MΩ
signoff | Checked By (Heyday):
checklist | Subcircuits (Energised) | [5 empty] | Testing & Commissioning - Subcircuits (Energised)
section | Voltage
checkpoint | Red - White
textbox | Voltage (V)
checkpoint | Red - Blue
textbox | Voltage (V)
checkpoint | White - Blue
textbox | Voltage (V)
checkpoint | Red - Neutral
textbox | Voltage (V)
checkpoint | White - Neutral
textbox | Voltage (V)
checkpoint | Blue - Neutral
textbox | Voltage (V)
checkpoint | Red - Earth
textbox | Voltage (V)
checkpoint | White - Earth
textbox | Voltage (V)
checkpoint | Blue - Earth
textbox | Voltage (V)
signoff | Checked By (Heyday):
section | Earth Fault Loop Impedance Test - (N/A if the circuit is RCD Protected)
checkpoint | Impedance
textbox | Record Inpedance (Ω)
textbox | Target Impedance (Ω)
checkpoint | RCD/RCBO Tripping Test
textbox | Trip Current (mA)
textbox | Trip Time (ms)
signoff | Checked By (Heyday):
checklist-flat | Earthing Systems - Construction Tests (Main Earth System) | [5 empty] | Testing & Commissioning - Earthing Systems - Construction Tests (Main Earth System)
checkpoint | RWV Industries – Earthing Test Report. Steel Reinforcement Continuity
checkpoint | RWV Industries – Earthing Test Report. Footing Earthing
checklist-flat | Earthing Systems - Construction Tests (Earth System Reticulation) | [5 empty] | Testing & Commissioning - Earthing Systems - Construction Tests (Earth System Reticulation)
checkpoint | Correct Cable Size and Labelling
checkpoint | Earth Continuity
textbox | Resistance (Ω)
textbox | Target Resistance (Ω)
signoff | Checked By (Heyday):
checklist-flat | PFC | [5 empty] | Testing & Commissioning - PFC
checkpoint | WSA20-MPX-04000-EL-ITC-31102000 - Construction Tests (Pre-energisation)
checkpoint | WSA20-MPX-04000-EL-ITC-31073000 - Component Test (Energised)
checkpoint | CT Ratio Verification (V,A,kVA) L1/L2/L3 - Component Test (Energised)
checkpoint | Power Factor Correction Controller Configuration as per manufacturers recommendations - Component Test (Energised)
signoff | Checked By (Heyday):
checklist-flat | UPS (Pre-Energistation) | [5 empty] | Testing & Commissioning - UPS (Pre-Energistation)
checkpoint | Commissioning & Installation / Start-up Report - System Room Check – Page 6
checkpoint | Commissioning & Installation / Start-up Report - System Check – Page 6.
checklist-flat | UPS (Energised) | [5 empty] | Testing & Commissioning - UPS (Energised)
checkpoint | Commissioning & Installation / Start-up Report - Unit pre start-up check – Page 7
checkpoint | Commissioning & Installation / Start-up Report - Unit Functional Check – Page 7
checkpoint | Commissioning & Installation / Start-up Report - Unit Final Inspection – Page 8
checklist-flat | UPS (System Commissioning) | [5 empty] | Testing & Commissioning - UPS (System Commissioning)
checkpoint | UPS – Functional Performance Test Report
label | The following tests are conducted (see Schneider Electric - Site Acceptance test protocol for results and trends):
label | ○ Load Transfer test
label | ○ Inverter to bypass transition on NO LOAD
label | ○ Inverter to bypass transition on FULL LOAD
label | ○ Load step test (0%-50%-0%)
label | ○ Load step test (25%-75%-25%)
label | ○ Load step test (50%-100%-50%)
label | ○ Load step test (75%-100%-75%)
label | ○ Load step test (0%-100%-0%)
label | ○ THDi and THDv measurements (0%, 25%, 50%,75%, 100%)
label | ○ Expected Results: Total Harmonic Distortion (THD) is to be under 5%
label | ○ UPS efficiency calculation (Unity PF@0%, 25%, 50%, 75%, 100%)
label | ○ UPS battery discharge test (15min EOL)
signoff | Checked By (Heyday):
checklist-flat | Solar Photovoltaic System (Pre-energisation) | [5 empty] | Testing & Commissioning - Solar Photovoltaic System (Pre-energisation)
checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – Inverter)
checklist-flat | Solar Photovoltaic System (Energised) | [5 empty] | Testing & Commissioning - Solar Photovoltaic System (Energised)
checkpoint | SCS Commissioning Checklist Section 5 (System Measurements – AC Measurements)
signoff | Checked By (Heyday):
checklist | PMCS - (Pre-Energisation) | [5 empty] | Testing & Commissioning - PMCS - (Pre-Energisation)
section | WSA20-MPX-04000-EL-ITC-31183000 - Component Tests
checkpoint | Schneider Point to Point Validation ITP - RIOM
checkpoint | Schneider Point to Point Validation ITP - PAC
checkpoint | Schneider Point to Point Validation ITP - EPS
checkpoint | Schneider Point to Point Validation ITP - PFC
checkpoint | Schneider Point to Point Validation ITP - UPS
checkpoint | Schneider Point to Point Validation ITP - EV
checkpoint | Schneider Point to Point Validation ITP - IEM
checkpoint | Schneider Point to Point Validation ITP - eGSE
checkpoint | Schneider Point to Point Validation ITP - GEN
checkpoint | Schneider Point to Point Validation ITP - LCS
checkpoint | Schneider Point to Point Validation ITP - EML
checkpoint | Schneider Point to Point Validation ITP - PV
signoff | Checked By (Heyday):
checklist | PMCS - Energised | [5 empty] | Testing & Commissioning - PMCS - Energised
section | WSA20-MPX-04000-EL-ITC-31184000 - System Acceptance Tests
checkpoint | Schneider WSA LV PMCS Cx ITP - RIOM
checkpoint | Schneider WSA LV PMCS Cx ITP - PAC
checkpoint | Schneider WSA LV PMCS Cx ITP - EPS
checkpoint | Schneider WSA LV PMCS Cx ITP - PFC
checkpoint | Schneider WSA LV PMCS Cx ITP - UPS
checkpoint | Schneider WSA LV PMCS Cx ITP - EV
checkpoint | Schneider WSA LV PMCS Cx ITP - IEM
checkpoint | Schneider WSA LV PMCS Cx ITP - eGSE
checkpoint | Schneider WSA LV PMCS Cx ITP - GEN
checkpoint | Schneider WSA LV PMCS Cx ITP - LCS
checkpoint | Schneider WSA LV PMCS Cx ITP - EML
checkpoint | Schneider WSA LV PMCS Cx ITP - PV
signoff | Checked By (Heyday):