## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
653201d0-bebe-448c-8979-d973b6964fb5 | checklist | ITP-307-STR-MSS-Bored Piling Rev 0 | itp | ITP-307-STR-MSS-Bored Piling
fadc8327-d98c-4cf3-94b2-b2ec5aee1c67 | section | 1. Referenced Documentation
3b3cc706-22dd-4ac6-a157-2e827191a99d | checkpoint-no-value | Referenced Documentation
b48af03f-d828-5e11-a444-1534e79613c1 | note | Document Title: ITP-307-STR-MSS-Bored Piling
b655fe2b-f1ef-5d2b-bfb5-c40852d8f4fc | note | ITP Description: MSS-Bored Piling
1c16ab7d-656b-554d-899f-47981f1b96b9 | note | Discipline (e.g. CIV/STR/RAIL): 307-STR
beba0483-7c45-5395-af6a-7a59b8ff49e7 | note | Revision Number: 0
61a9551f-2a61-5d5c-900b-b6ab9ef5bf97 | note | Revision Date: 27/08/2025
b52d6e9c-b857-5ea2-b184-adf1ae9cd6ec | note | ITP created by: Andrew Carlini
fb6a5744-62d8-593f-95d1-b10061e984f7 | note | ITP approved for use by: Romualdo Magpantay
623c7b85-413c-5e1b-971c-a4444fa0eb9c | note | 1.1 - Non Dependent
56963743-f072-5387-adb5-00ef6d746117 | note | Reference - DTP Section 606 July 2017
a0b2bd5f-4590-5af0-a3b5-9718b56e8e18 | note | 1.2 - Non Dependent
2b0c129d-6394-5f8a-9499-7f4752067934 | note | Reference - DTP Section 610 Feb 2020
c0a8f06f-5a4d-55f2-88f9-252bc1a02700 | note | 1.3 - Non Dependent
480d6584-29eb-5c42-a6e8-db7911889c3c | note | Reference - DTP Section 611 November 2018
1f99bcbc-9803-57a6-b270-86644011cc8c | note | 1.4 - Non Dependent
b2a02963-a5aa-587a-8cf0-f92cb7178289 | note | Reference - AS2159-2009
4c3d9ab8-a268-589a-97e7-67921358c6c4 | note | 1.5 - Non Dependent
37ff9cc2-7c16-5be7-89cc-fc3a47b04732 | note | Reference - AS3810.1 2018
342b5635-dbcf-5f8c-9c8b-53081316b178 | note | 1.6 - Non Dependent
e4a0fd77-fb9c-582a-ab3b-71d9ab001ec2 | note | Reference - AS5100.3-2017
1636809c-3aab-4a40-a717-67a2da7ff716 | section | 2. Preliminaries - Materials
1966faff-0ee2-400a-b127-aaec1e09f629 | checkpoint | 2.1 - Concrete Mix
f1655c3e-7cba-5d8b-ac84-474fbbc83249 | note | Reference - 610.07 Table 610.071
1a8769f0-5916-50cc-bd5a-1f19fe58d1ff | note | Acceptance Criteria - Concrete Mix is Registered with VicRoads.
71f9bc3e-8e38-52eb-bca4-b24c12a7e186 | note | ○ Concrete mix meets strength, grade, and maximum aggregate size as detailed on drawings.
99fe0163-70b4-5309-9968-ca2995d07b1f | textbox | Enter: Teambinder Material Approval number
76fd0901-fc41-5691-9159-6fd2e457732b | note | Method - Document Review
7c3adcef-51d5-5403-a96f-3bf446b52be5 | note | Frequency - Once, for each mix design, 4 weeks prior to placement of concrete
be79ac3c-83c5-5312-9af1-b7c246a481da | note | Category - HP
16de0310-7caa-5893-a5ca-e608af045d72 | note | Responsibility - Nominated Authority
5296f6dc-78d6-5c57-b339-14821708ae60 | note | Verifying Documents - ConQA Hold Point Release
85a9355a-0a37-513a-979c-af2b680457a8 | date | Date Completed:
2614f42b-fcc2-489f-ad40-33099a6296b9 | signoff | AUTHORITY HOLDPOINT
a1b63b3d-9698-4531-9a2a-9bdfbb400c15 | checkpoint | 2.2 - ACRS Certification (for Reinforcement)
dc46131c-53c3-565b-9483-17a181872599 | note | Reference - 611.05 (a)
baaa1323-56f1-5372-a630-b4d86bcf79c5 | note | Acceptance Criteria - Current ACRS certification for materials and for bar processing.
d6ec007d-beef-5510-8c39-7549b6d223c3 | note | ○ Note: ACRS certificate may cover both aspects or be for each separate portion (e.g 1 for the material supplier and another for the bar processor (bending, cropping and delivery)
a2c69ac4-a793-57cf-9562-cb6b001b3f16 | note | Enter: Teambinder Material Approval number
7bd70eb1-1cb7-5495-9f71-6dc980a5e88c | note | Method - Document Review
6c25d9fd-ffcd-566f-869a-ee91da4b3655 | note | Frequency - Once for each supplier, 14 days of award of contract
68668f2d-aed4-5a15-ab4c-eda6ab17bcf4 | note | Category - HP
bf6e2c54-afba-5e9f-87f4-b2631f696849 | note | Responsibility - Nominated Authority
2f304f91-557f-5e50-862c-48bd04eb4e72 | note | Verifying Documents - This ITP
56345cf2-1b08-57de-b3d0-2aa2fa404202 | date | Date Completed:
279fb4e7-2c38-49d4-9a70-3b38ec420679 | signoff | AUTHORITY HOLDPOINT
1cfb225e-6778-4ae4-95c7-38f1bf11ad70 | checkpoint | 2.3 - Bar Chairs/Aspros/wheels Certification
cb402f25-f95f-5f20-bbfc-2dd37391b32a | note | Reference - 610.26 (a)
d5d99d65-78e7-5d65-bf60-7b2872fba1a5 | note | Acceptance Criteria - Plastic bar chairs, wheels, and spacers require bi-annual testing to demostrate suitablity to prevent excessive deformation under loads.
5fdfe15a-0ad3-5e2c-a8e9-214197e7675e | note | ○ Concrete aspros require annual compressive strength and soluble salt testing is required.
eee4bcdc-2147-56af-aaaa-56be5db89ee4 | note | ○ Relevant test reports demonstrating compliance to this clause shall be submitted for review to the Nominated Authority.
3604a3bf-a97b-5758-b174-22c255b078b7 | textbox | Enter: Teambinder Material Approval number
9f683a2b-8e53-5da5-94e4-5c6572d28648 | note | Method - Document Review
e2b89865-3779-5394-a21c-0b4d6707313f | note | Frequency - Once for each supplier, 14 days prior to placement of reinforcement
0ac64c6a-884c-5366-bd0f-4f2adc010eb2 | note | Category - HP
20e11a95-77f6-5511-841e-720e16bb11b9 | note | Responsibility - Nominated Authority
ff1f8104-e7ee-5f68-a4ec-cd1c2aec6da7 | note | Verifying Documents - This ITP
0919a2ec-05ed-5d35-94c0-14a76c819bab | date | Date Completed:
cd5f3b9e-8baa-4d59-b90c-ffba955dd782 | signoff | AUTHORITY HOLDPOINT
9b830049-b5d8-411d-ab2c-7675d728dba0 | section | 3. Preliminaries - Procedures & Documentation
8e4182d7-f983-4627-84ce-d8ad9c7889cc | checkpoint | 3.1 - Working Platform certification
a66da80c-29b4-5caf-adc2-478bd5bba03c | note | Reference -
49a80c46-9a49-569d-9aa8-f85dc92e8393 | note | Acceptance Criteria - Satisfies minimum plant bearing pressures requirement
ee0017dc-7e4a-5ff3-98de-81919d9e34b9 | note | Method - Document Review
ff66b974-3598-5426-bb33-73f35e34f88a | note | Frequency - Prior to works commencing & after rain event which there is >10mm in a 24hr period.
f119b2e9-a447-5e18-9631-b561afe536cd | note | Category - HP
759055c6-2f6c-55c9-a7f0-19a370c83e6e | note | Responsibility - Piling Contractor/Geotechnical Engineer/Fulton Hogan Engineer
63e68586-f066-562c-b6f3-a62db81bdbe1 | note | Verifying Documents - This ITP
6f19b44a-36b7-5b8c-88c6-2f885b62f2a6 | date | Date Completed:
7c7c2524-b41b-4d7c-a5b3-54c88396b33c | signoff | AUTHORITY HOLDPOINT
9d2a70d4-e1ca-4e8c-a21e-a092a112b089 | checkpoint | 3.2 - Piling Operations Work Procedure
736bbbd9-39b9-50fe-b738-5445b2e0b492 | note | Reference - 606.03 (a)
04032ec6-53da-5a41-9ba2-ac551802b993 | note | Acceptance Criteria - Piling operations work procedure to be submitted for review to the Nominated Authority.
7615bfc5-1b98-5ffd-a749-7c8959c4200e | textbox | Enter: Teambinder Approval number
9b29d4d5-3774-519f-ab55-9e509a7c3887 | note | Method - Document Review
491b2b21-15df-5827-9d46-6c8a10cebff4 | note | Frequency - Once, 4 weeks prior to the commencement of piling
d84fffb4-0ff9-5936-8066-f09c7ad587d6 | note | Category - HP
2a7f8ee4-921d-57b9-b9c4-ac97f5c2a19f | note | Responsibility - Nominated Authority
0d3ead46-fd0d-5336-a7a2-caea67c760be | note | Verifying Documents - ConQA Hold Point Release
2dabe553-76aa-52c0-92b8-4198fac9af87 | date | Date Completed:
d07523ba-be0d-4aba-8ca9-1ab6252e038e | signoff | AUTHORITY HOLDPOINT
a24d1ba0-61f8-49a5-9d26-b655a2c6e01c | checkpoint | 3.3 - Temporary Steel Casings
d8a369de-1b9c-52e4-9262-d62e0a561558 | note | Reference - 606.03 (b)
be167445-9b87-5890-8352-23f86c273f2c | note | Acceptance Criteria - Temporary steel casings shall be free from holes and distortion with a smooth internal surface without any projections.
91b40255-37c6-546e-b797-ace57a10f9c7 | note | ○ Any splices in the casings shall be able to withstand any stresses induced during installation & removal.
ca8041bd-70c8-5a39-8f55-80f955ed9fd8 | note | ○ The casing shall be proof engineered by a proof engineer who is pre-qualified with VicRoads.
cfc165f2-b301-5a5e-905a-73c679d9e179 | textbox | Enter: Teambinder Approval number
feb200dc-8727-5aa1-804a-18f96c88fc61 | note | Method - Document Review
e7387389-7135-5b5b-9ad7-9d3b3fdf4986 | note | Frequency - Where applicable, once, prior to use
c6d02372-ce7a-5d8e-b0b8-e3e308ca021d | note | Category - HP
c2974f8e-74cf-5209-b6e2-1b1aef7117cf | note | Responsibility - Nominated Authority
8841c5c7-4c38-5ee2-8c7f-730fd2a9eaa7 | note | Verifying Documents - This ITP
ef2f7e8a-779a-53a0-8663-f920f2f4ca19 | date | Date Completed:
75e34917-de73-4090-8312-36629ee53668 | signoff | AUTHORITY HOLDPOINT
41de8ac2-ca61-4b6a-8de2-cc298e34651f | checkpoint | 3.4 - Casting Under Water Procedure
f3d85c1b-86a7-5914-b497-0d3306fd6f54 | note | Reference - 606.06 (a)
ac47c3cf-25c0-53f1-b4dc-2e53efe5f789 | note | Acceptance Criteria - Casting under water procedure and methodology for removing mud, loose rock and other debris to be submitted for review to the Nominated Authority.
9614f0b7-4490-5ed8-b1fe-d4cb9010eaf7 | textbox | Enter: Teambinder Approval number
fd085706-8bae-5464-b276-a28a5a037742 | note | Note: Piling Operations Work Procedure may cover this requirement - if so, use the same Teambinder Approval Number if this is the case.
85717341-0e23-5292-99a6-4670f426ccc8 | note | Method - Document Review
d6600efc-a881-5e4b-8186-0bfd6fd904c2 | note | Frequency - Where applicable, once, prior to placement of concrete
4a933432-80bd-5122-8b8d-d148d4332ca5 | note | Category - HP
d029afc2-a8c0-5706-bf7f-fc9ce9066594 | note | Responsibility - Nominated Authority
93c09432-63f2-5a4d-8614-8d40ab755c5d | note | Verifying Documents - This ITP
2c326999-f0ea-51a6-8de3-56d63cb91f3d | date | Date Completed:
b36bacd0-fe28-46f8-ac13-894e97217dbe | signoff | AUTHORITY HOLDPOINT
9a337fdb-21a2-4054-b236-65ba0fe88fad | checkpoint | 3.5 - Boring With Bentonite or Polymer Fluids
937a9486-c363-5f50-b3b0-b4e2df9f8f36 | note | Reference - 606.03 ( c)
0af15a57-c7c5-5d20-919d-bd9cd0472c70 | note | Acceptance Criteria - Boring conditions under bentonite or polymer fluids alone or in combination with temporary casings to be submitted for approval to the Nominated Authority.
22116def-b873-52ca-9f42-6db38411f069 | textbox | Enter: Teambinder Approval number
c0bf4b79-4a7e-5c1f-a0df-0e91fcb1f500 | note | ○ Note: Piling Operations Work Procedure may cover this requirement - if so, use the same Teambinder Approval Number if this is the case.
cff970ba-d619-5557-888f-c59fc0aad309 | note | Method - Document Review
ba8e4a10-ea5e-5abe-8b59-fbb17914dc3f | note | Frequency - Where applicable, once, prior to commencement of boring
4682146e-d64d-5f6a-9935-c1cb8701581c | note | Category - HP
cd7bc474-65d2-580b-af86-248bb0bcc585 | note | Responsibility - Nominated Authority
7696f0a3-b363-5595-b39c-de5798326a1b | note | Verifying Documents - This ITP
c6e88247-27ac-59c7-920e-150db3948124 | date | Date Completed:
75a273ea-7563-416c-a47e-e7889439903d | signoff | AUTHORITY HOLDPOINT
d8f87053-1767-4f2f-a2bc-42d6c53b9b98 | checkpoint | 3.6 - Pre-qualified Pile Testing Consultant
8b89c9e1-062a-5121-9610-41df91d6f183 | note | Reference - 606.07
46547f3d-cdc6-5132-b587-82f9b4ec804c | note | Acceptance Criteria - All testing shall be undertaken by a Vicroads pre-qualified consultant who is independent of the piling contractor.
f23c394d-4c42-594f-b835-b448a5f6169d | note | Details of the consultant to be submitted for review to the Nominated Authority.
96296240-1c87-593e-a17e-ec645e1ab4cc | textbox | Enter: Teambinder Approval number
69c823f3-753f-5e5b-8bc9-f4dd04afee7e | note | Method - Document Review
8fea6b00-be8d-5a85-a73e-d4a4eb5d69fa | note | Frequency - Once, two weeks prior to testing
838725de-c063-50e8-8874-b632b4bc2fd9 | note | Category - HP
49e1b6ce-dfda-5d67-95bd-6b7e6a726524 | note | Responsibility - Nominated Authority
e2beaefc-07ec-5a3c-87fc-9f40ba3e1379 | note | Verifying Documents - ConQA Hold Point Release
d45af45b-bb55-5848-86f1-4aa31c42e995 | date | Date Completed:
66295409-0a94-42ba-9d6a-7f2bf4755e80 | signoff | AUTHORITY HOLDPOINT
49d37486-f78f-46f0-816a-1e9145df091c | checkpoint | 3.7 - Reinforcement Welding Specifications & Qualifications
4a900991-a40a-53f5-9568-c2189bca2683 | note | Reference - 611.13 (a), AS/NZS1554.3, Clauses 3.3.2 & 3.3.3, 611.14 (b)
b8b1ef15-1210-5049-af8e-3d862023c9db | note | Acceptance Criteria - Welding of splices in steel reinforcement, including to other steelwork and to continuity bar reinforcement, shall not commence until the welding specification & qualifications (including macro inspection) have been approved by Nominated Authority.
9996f364-231f-54b0-ae09-79905fc2f57f | textbox | Enter: Teambinder Approval number
05bd11e1-db90-5b86-a3aa-7046d7649024 | note | Method - Document Review
9e5b7135-63a1-5baa-b51f-42c65dc9e5a4 | note | Frequency - Where applicable, once, prior to welding
d395f592-09c0-5fbc-9975-f9dc601da9d1 | note | Category - HP
45937685-e189-51be-a29e-448c4211eba9 | note | Responsibility - Nominated Authority
a33eb8cb-0dec-5914-b7cf-481cb34ca8fa | note | Verifying Documents - ConQA Hold Point Release
ad0e2c06-fc97-5b27-a7b7-0cb307b29c6b | date | Date Completed:
cdad8677-e274-4813-8f22-4780484635a4 | signoff | AUTHORITY HOLDPOINT
86205bad-7e3f-4396-8ce2-e1063be01385 | section | 4. Pre-construction Activities
da9670ee-4661-4718-94a4-1bfaff6c7fae | checkpoint | 4.1 - IFC Drawings
de01ce04-42a8-544f-924a-36b26e385d03 | note | Reference - MRPA Quality Management Plan
1f940b19-46c5-5a3d-b104-a107bdc78ba7 | note | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
cac2f321-3070-592e-9318-e284375125fa | note | Method - Document Review
347bd1a2-0423-51a7-881c-1183f8bcc6b6 | note | Frequency - Prior to starting Works and at regular intervals
c2e94653-51d3-57b0-ad6d-a8173b09aca4 | note | Category - HP*
0e202cb4-9199-5cb8-8430-64f5f61819ae | note | Responsibility - All
5c6d5810-6472-54d0-b3f6-ffefae7fc461 | note | Verifying Documents - This ITP
1c57a517-db65-540d-a1e0-a99a5a141701 | date | Date Completed:
0f0a7f06-e2b6-4820-8145-cf5277301c05 | checkpoint | 4.2 - Survey Set-out
00f77a93-6b68-5215-a85c-22472f25fec5 | note | Reference - IFC Drawings 606.08 (a - c)
7bd702b8-ec24-56a4-8783-b004ecdd6817 | note | Acceptance Criteria - Survey activities undertaken to ensure and validate that all Works meet location requirements of ±75mm.
a8c745fe-efd3-5bc6-9800-f0e8bf33c8d6 | note | ○ Attach: Lot Map, Marked drawing to indicate the location of piles in the Lot
f96e980e-70d6-5268-874c-d96052917ef0 | note | Method - Measure, Visual
09a224ee-0d8e-5073-9215-bc840668df2a | note | Frequency - Each pile
7418bdd2-8a2a-516d-8eb3-3803d3feffaf | note | Category - IP
748bc76c-bd9e-54f9-815b-880259ce42fd | note | Responsibility - Surveyor, SE
492e3266-4bc2-531d-83a7-e20a8ed596dd | note | Verifying Documents - This ITP
cb45ea88-6090-5a68-8ac5-2c860180c3f6 | date | Date Completed:
f81c28cd-4159-494b-a6d9-7a3323d59694 | checkpoint | 4.3 - Protection of Adjacent Piles
a2dc802a-4246-5f7a-8980-aaf54d459ecc | note | Reference - 606.04 IFC Drawings
eeccaaa2-df21-597f-aed2-be88fb063fc8 | note | Acceptance Criteria - Pile construction shall not:
fe8d7e3a-0f62-5521-a3ae-4d46e2e6a226 | note | i. result in damage to adjacent newly cast piles due to ground vibration.
a16f3928-e369-5394-b5d5-51afafe97024 | note | ii. commence within 3 piles diameter or 2.5m clear distace(Whichever is greater) from newly cast piles if that pile concrete strength <15MPa
70d7b24b-9eb4-589c-87a2-54a294f0fba5 | note | iii. involve driving or create significant vibration within 9m until that pile strength ≥15MPa and set for a minimum of 24 hours
9ec6f0d3-5417-5d77-9b46-f822b236316c | note | Method - Measure, Visual
e458b3c9-0937-5bb9-9388-d712f1412e0c | note | Frequency - Each pile
c6092f0a-d41d-5841-9040-588a6ecc1048 | note | Category - HP*
7c67d166-a8f3-5764-b810-f0f5827ef222 | note | Responsibility - SPE/PE
0ead32a8-bb98-504e-bdfe-299028d11ff9 | note | Verifying Documents - This ITP
379785fd-4827-5ebc-8ef0-e06acb44a49d | date | Date Completed:
97ffe4ee-2c04-46f4-b0b1-5a0ddaf1e7c3 | section | 5. Construction Activities
31b740c6-bd28-4d8d-aa90-c38082ce7403 | checkpoint | 5.1 - Boring Operations
cf601e3f-7fbc-59d7-97f9-e7f90fdc71ef | note | Reference - IFC Drawings 606.03 (a)
448f39e8-a6eb-5e41-bd6c-822647a95b9f | note | Acceptance Criteria - Boring performed to the required diameter and depths shown on the IFC Drawings under the instruction of an experienced geotechnical engineer.
fd380a33-22ba-5f07-bd63-fea6ca5f600a | note | ○ Where piles are founded on rock, they shall extend a minimum of 2 x pile diameter into the rock shown on the IFC Drawings.
4ab8d814-110f-55a4-93c9-1f42db82238e | note | ○ Excavation clean and de-watered (where applicable) for inspection.
3bc4d9dd-76bf-5d0d-8dea-c3eec2f7e28a | note | ○ Excavation made safe by appropriate means and to be protected from site run-off and loose materials falling in.
5cae9cde-6cc3-5663-8440-ce2a21f4b896 | note | ○ Excavated material to be disposed of as appropriate to maintain a clean site.
d7e8fd78-e5de-5846-b205-493c6025439b | note | Method - Measure, Visual
56578fbe-648f-5e47-9894-292406c36352 | note | Frequency - Each pile
1eded23d-34a4-51b0-911c-5c5b2b2a58ac | note | Category - IP
c25c1312-78e7-5c4c-aa91-f52d57015da7 | note | Responsibility - Surveyor, SE/PE/SPE
727838cf-5f88-58a5-a92b-d51ce550d8d5 | note | Verifying Documents - This ITP
564b996c-e104-5783-a830-9228d47c2fae | date | Date Completed:
7ee3a710-426b-425f-be07-0f9033543fe0 | checkpoint | 5.2 - Formwork Extension
eaa0d347-0d6f-58b5-bdbe-7f8759e22cd3 | note | Reference - IFC Drawings
b1b145cf-6512-59fb-a04a-ed2d89801c64 | note | Acceptance Criteria - Where applicable, formwork shall be used to ensure the top of the pile is at the required RL.
6ec18138-a40d-5d58-bdc4-b4f32cf33eeb | note | Method - Measure, Visual
084e53b9-b4ab-5db4-a26b-26092ea91c13 | note | Frequency - Where applicable, each pile
428a2419-a09b-5260-a465-1669bf6b94c9 | note | Category - IP
296b6235-31f1-5406-881f-e9c62768a412 | note | Responsibility - Surveyor, SE/PE/SPE
bb12407a-d813-55fd-b4f7-2070dd0ee89a | note | Verifying Documents - This ITP
2b4f714b-39e2-525c-9e7b-c33affb16b1a | date | Date Completed:
3da965da-7a87-40a9-845f-8650f2ec330c | checkpoint | 5.3 - Inspection of Pile Excavation
8655c553-d512-5758-ac70-a92cb4cbd731 | note | Reference - 606.05
43492aef-8f12-56a2-9119-da5941c78b75 | note | Acceptance Criteria - Pile walls and base to be inspected by the geotechnical engineer to confirm that the geotechnical strength of the materials in the pile wall base have satisfied the design assumptions.
2abf8bea-f908-5937-ac1a-e85d5f8b002d | note | ○ Attach: Geotechnical Field Sheet or Report
4ce9aef7-ef62-5ba2-89b8-01b41125cfde | note | Method - Measure, Visual
10052d39-07d6-57de-afe2-85d1934028f6 | note | Frequency - Each pile
bb83df46-c790-506c-a3e3-a4c8ce87fc97 | note | Category - HP
407d41c9-acc2-5376-9739-98ef2de920d4 | note | Responsibility - Geotechnical Engineer
1b9b7ab8-cfeb-5abd-9090-21e5b0ccaad7 | note | Verifying Documents - ConQA Hold Point Release
da52fc49-472a-541a-a9a8-a3b853c4e27e | date | Date Completed:
b65e29f5-fcae-4cae-a1ae-45f18a394c12 | signoff | AUTHORITY HOLDPOINT
5f16a1fd-9944-44e1-ab79-f6d0996fb8c5 | checkpoint | 5.4 - Reinforcement - Placement
3df7c6d0-e8df-5828-b148-a8b2837b1346 | note | Reference - IFC Drawings
240f6e78-150f-58c0-8392-e59eb7e0acf4 | note | ○ 611.06
3e603fb2-fe56-5e86-af88-e69856c3ea5a | note | ○ 611.09
44584f58-4b58-55df-a194-0eb2d7332d0f | note | ○ 611.10
93a9e784-12d2-52b3-9f44-2d6fe455c3ed | note | ○ 611.11
45b3cad9-8353-5e4d-acd4-926b4212164d | note | ○ 611.12
f73689c1-0886-5509-8b23-64d62fd33fb0 | note | ○ 606.06 (a)
f270846c-794a-517a-8b79-523c099faf9e | note | Acceptance Criteria - The correct reinforcement grade, quantity, size, orientation, location and spacing as shown on the structural drawings.
27d91a52-8973-5164-8158-9681263fd491 | note | ○ Projecting reinforcement is the correct length and location.
a5241058-4118-59bd-a91a-d95da26e6d80 | note | ○ Splice lengths achieve the minimum length and are in contact for this length.
2c8a1562-9317-539d-803a-33b265597440 | note | ○ The reinforcement surface condition is free from dirt, debris and damage.
7ab758ee-13be-5c72-8604-a6ed2494914b | note | ○ The resulting cage securely held with sufficient ties to limit displacement or deformation during the concrete pour.
c0592fe4-f1a8-5a2b-a8a8-54551cb5c625 | note | ○ Bar chairs or wheels used at no greater than 2m centres so that the minimum cover as shown on the structural drawings all around and has been achieved (including tie wire locations).
1f58aac7-9e73-5657-ac25-bde097187565 | note | Method - Measure, Visual
8b70cd99-c576-57e7-ae74-5608a743cfb3 | note | Frequency - Each pile
ff4cb4d2-ccde-59cb-92ba-7a64f6d0f06e | note | Category - IP
9ff643b6-f697-5f66-bbc3-4dab086cbad0 | note | Responsibility - Foreman, SE/PE/SPE
444bd8d7-65f5-51cb-a97b-cb1f42e7262f | note | Verifying Documents - This ITP
b5fad0c8-aa93-5c9c-8afb-e800c77ec9d8 | date | Date Completed:
8f915a52-493c-4d9a-ab9b-6835932bbf89 | checkpoint | 5.5 - Reinforcement - Electrical Continuity
6bd055c8-06e6-5b6e-969e-7ae2932aa0af | note | Reference - IFC Drawings 610.29 (d), 610.43
cc31aa60-6d77-55bb-ba44-9ba2d2df17e1 | note | Acceptance Criteria - Pile reinforcement cage to be made electrically continuous by:
ec7d90b4-c0a0-5303-8691-015655bd1d59 | note | i. tack welding 4 no. min. longitudinal bars to all intersections of the helix at 2.0m centres max. (at every intersection is preferable)
020c47b4-ddd6-576f-8928-d30ee7dc39af | note | ii. tack welding the selected longitudinal bars at all splices (2 tacks minimum per bar)
2ba5fd23-d7dd-542a-a922-c4ab99a61024 | note | iii. tack welding or fastening the grounding clamps to the longitudinal reinforcement
0a6bfe65-6c38-5be2-a457-b5296a5ef94d | note | ○ Evidence that the resistance across the cage has a maximum value of 0.01Ω / 10,000µΩ is required.
ed472cb1-cd8c-5923-8948-b5e0a515e362 | note | ○ Photograph or attach: Ohmmeter reading across the splice or end to end of the reinforcement cage
154f187d-726d-56e5-a6f5-8ddaa40f25a8 | note | Method - Measure, Visual
8b5023aa-f312-5041-a74d-ac261765c9b3 | note | Frequency - Where applicable, each pile
05a23330-5213-5f2e-9f1d-2462b3dac297 | note | Category - IP
0bdacff7-f021-5769-87fb-aaa6d9b69487 | note | Responsibility - Earthing Engineer, SE/PE/SPE
682c0ff2-ed60-5cd1-8805-9215d8b86fa9 | note | Verifying Documents - This ITP
b4c00c44-9291-530e-b2b8-78ebc3ed0e4c | date | Date Completed:
f26cf190-1c23-4900-877b-d9ca7aacf037 | checkpoint | 5.6 - Cast-in Items
6793f706-6aec-57c1-bbb5-6ee8398a9083 | note | Reference - IFC Drawings
aa566d05-d6c1-5425-9a3f-ada8d0fc334f | note | ○ 610.46 (a), Table 610.462
087512f0-27c9-5507-95da-f960543c0d7e | note | ○ 610.47 (a), Table 610.472
fc57cff4-a705-52ed-80d3-141b0db0eb15 | note | ○ AS3810.1 Table 3.3.6.2
a86b4fea-0091-519e-a56c-3f167d1f35ed | note | Acceptance Criteria - All cast-in items are the correct type, grade, quantity, size, orientation and location as shown on the structural drawings and are securely fastened or restrained to withstand impact and pressure during the concreting operations to prevent dislodgement.
8ce7dca0-c5e5-5f44-8949-1c05f4950adb | note | ○ Any exposed threads, conduits, ducts or voids shall be protected by suitable means to prevent concrete or grout ingress.
83378066-76a2-5d5c-af66-867cd195a588 | note | ○ Tack welding of any cast-in items shall be performed by someone pre-qualified to do so.
6f4a4f18-f449-52b9-a308-1efe448b1a5d | note | ○ Grout tubes shall be fastened at regular intervals to prevent kinking.
d7dc5338-10fe-5029-8287-960b3e1f6e4d | note | ○ Placement tolerances to comply with the IFC drawings, if not specified, use the following:
143d949c-ca56-5517-b1c7-1cd67244e733 | note | i. Bolts, ferrules, projecting bars & couplers = ±3mm
7ef598b4-1891-5e7c-a460-828e874ad2ad | note | ii. Running dimensions of a group of the above = ±6mm
3703e411-f23b-5084-bfd0-f7c549c75c44 | note | iii. Ducts and conduit location = ±12mm
3714e5b3-61fe-5351-a2d1-77588b29442e | note | iv. Diameter of ducts and conduits = ±3mm
57ca043e-d479-57a8-aff4-954f2f2b7427 | note | Method - Measure, Visual
f84f7e94-8bcf-5340-848e-2676ab81c311 | note | Frequency - Where applicable, each pile
e0ba0695-3a57-541c-9d38-5758ba003415 | note | Category - IP
04871bd4-377e-5032-83cf-e41824b88603 | note | Responsibility - Foreman, SE/PE/SPE
d2f1abc1-1e5e-5a57-b423-ce7048a5db53 | note | Verifying Documents - This ITP
49c95465-b10b-5dfc-90f8-e05548bd9fec | date | Date Completed:
1a73816f-b9c1-4ab9-87e2-368cd978df0c | checkpoint | 5.7 - Pre-pour Inspection
a069a7e8-b190-5235-bbfc-8921bb7839fe | note | Reference - IFC Drawings 610.18 (a) (ii) & (iii)
e521c152-91c1-556c-bda7-df5723d9e201 | note | Acceptance Criteria - Evidence that the forms, reinforcement, electrical continuity and other cast-in items conforming to the requirements of this specification and the drawings has been reviewed by the Nominated Authority
3fb337ce-9d98-59d0-8caa-0cd91a3964a5 | note | ○ All foreign material has been completely removed from the excavation.
96619803-3fae-53c4-87a2-09352eaa9fb3 | note | Method - Measure, Visual
e3a9cbbf-240a-5a8d-a948-0f14d0cc235b | note | Frequency - Each pile
2b86f63b-fa45-52a2-b59d-6da2e96db568 | note | Category - HP
5a786186-eece-55b6-87c3-f411e439bae1 | note | Responsibility - Nominated Authority
d901510b-d250-5cd6-9f53-8624e9cd3cd6 | note | Verifying Documents - ConQA Hold Point Release
79607aa0-61d7-5765-a66a-e56bf357c97b | date | Date Completed:
cbf10c46-496c-482b-8604-1f4eb344c8a2 | signoff | AUTHORITY HOLDPOINT
7cf356c3-26a9-4de2-8e4b-2bf762fa926e | checkpoint | 5.8 - Weather Conditions & Evaporation Limits
f6cabc12-fd48-51d1-b549-2baab20bb752 | note | Reference - Hot and/or Cold Weather Concreting Procedure 610.17, 610.17 (a) & (e) Table 610.171
2adcc700-806a-5357-910b-7362a5d1472c | note | Acceptance Criteria - All freshly finished concrete surfaces shall be protected where required from the sun, wind or rain, until curing is implemented.
e99dae1c-51f7-5de2-8333-06e0c99749b8 | note | ○ The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C.
ebaeb804-98f2-5523-b553-2cddaa514f33 | note | ○ The air temperature, relative humidity, concrete temperature and wind velocity are measured to determine the evaporation rate of water from the concrete.
f6a47176-766e-5a9d-886a-582d0682288d | note | ○ When the evaporation rate exceeds 0.50 kg/m²/hr apply evaporation retardant at the rates specified on the manufacturer’s TDS.
6cefd5a6-6e39-52a8-9397-4f8d3b0af615 | note | ○ Record: Required information on the Concrete Pour Record.
cf701195-e00e-577e-baa7-91bde4c12645 | note | Method - Measure, Visual
f3b55245-db85-5779-9393-e178eef4444e | note | Frequency - Each pile
da72fe93-4b0a-5ac1-b178-b9344705ae77 | note | Category - IP
fe3f2652-edd9-5303-8bfb-e799df5e5243 | note | Responsibility - Foreman, SE/PE/SPE
700c6b15-3f08-5d43-a53b-5e925b1cda5f | note | Verifying Documents - This ITP
28079ee0-2f84-54b2-8afe-87f82641f78b | date | Date Completed:
240b3711-8707-424a-b19e-55d02a449caa | checkpoint | 5.9 - Concrete Testing - Sampling Frequency
03d146dd-892e-599c-923b-1e9d4d85c509 | note | Reference - Site Sampling & Testing Procedure 610.16 (b) Table 610.161
54e68843-b40a-5322-ac90-228068a46f96 | note | Acceptance Criteria - Concrete cast in one continuous operation to be tested at a frequency as shown below:
969c5847-3adc-576b-910d-127b468e5963 | note | 0m³ to 10m³ = 1 sample
bf3600d1-8433-5909-a86f-f1062ca154a9 | note | 10m³ to 25m³ = 2 samples
086eb638-d9b1-5b67-b56c-9dc953e0d261 | note | 25m³ to 50m³ = 3 samples
a6c71201-848d-57f0-bff9-c691e8573224 | note | 50m³ to 100m³ = 4 samples + 2 no. VPV cylinders.
98658eb8-00f3-5fca-a04c-70595f5496e4 | note | ○ For each additional 50m³ and additional sample shall be taken.
5cff1a1c-d8ee-5761-a66f-be85561e8746 | note | ○ Where the time interval between the end of discharge of one truckload of concrete and the beginning of discharge of the next truckload exceeds 45 minutes, the minimum number of test samples shall be one (1) per truckload of concrete
f2c5ff91-f9ec-5ec4-8272-84b158b2be21 | note | ○ Each sample shall consist of 1 no. slump or spread test and 3 no. compressive strength cylinders minimum.
500ec26e-6f5a-5eab-8040-321af51c8cf0 | note | ○ Compressive strength cylinders = 1 no. 7 day strength, 2 no. 28 day strength.
09fca4e2-0040-5bc9-82d8-ba0f54169729 | note | ○ Note: Additional cylinders may be required for other purposes such as early strength determination of adjacent piles.
5ecb0b98-8031-584f-b78c-d57377872e4d | note | ○ Record: Required information on the Concrete Pour Record.
f7fea7fa-8b50-54bb-a450-a9ee67ce76be | note | Method - Test
fc3255ca-d15f-58bd-a88f-16514b02a595 | note | Frequency - Each pile
dc03f66f-e606-57cd-b729-b8f7f537016a | note | Category - IP
c446be2f-5ad0-5536-8210-6faedea58ab4 | note | Responsibility - Concrete Tester, Foreman, SE/PE/SPE
203c1994-b319-5d7b-a6a8-cfaf5bf5e11f | note | Verifying Documents - This ITP
cd385d6c-75f9-5157-9cb0-3d93ffeacba4 | date | Date Completed:
fd1e3cc6-20ff-407e-a3c7-ad82567f29b6 | checkpoint | 5.10 - Concrete Testing - Spread, Passability & Viscosity
5524f8b1-38cc-5675-bd3a-a791fa4de460 | note | Reference - 610.13 (b)
215406b1-f7d7-56e5-b9c0-754ae3e0d336 | note | Acceptance Criteria - Spread range = 550mm to 750mm
7ed59319-4518-59d8-a1ed-f66bb769233b | note | ○ T500 = 2 seconds to 5 seconds (to reach a spread of 500mm)
f51d0bfc-ebb6-5efa-8237-90b1bdd21fea | note | ○ Passability = ≤10mm (aggregate height differential)
60493dba-bad7-5f20-ae12-cd148719f6b7 | note | ○ Record: Required information on the Concrete Pour Record.
fa3cabe9-5cfd-5c80-b50d-9c8ce1493311 | note | Method - Test
99e6363c-8316-5d3a-b8e9-4c9c2a7211c3 | note | Frequency - Each sample of Self-compacting Concrete
cf5a218e-7227-5730-b610-7d9d0ab849c8 | note | Category - IP
56860af7-c455-5763-9767-70dc42e5b468 | note | Responsibility - Concrete Tester
550ee5fa-00a3-51c3-b848-04e679a02c2a | note | Verifying Documents - This ITP
e144cd3d-3107-5bf7-849b-68844901a45b | date | Date Completed:
d00e400d-a928-4bce-85ad-b6dc3840abd0 | checkpoint | 5.11 - Concrete Testing - Compressive Strength Cylinders
d7e11a5d-3560-5451-9625-1b40df201582 | note | Reference - Site Sampling & Testing Procedure 610.16
35a01607-9fbb-5908-a473-1a864dd9760c | note | Acceptance Criteria - Correct quantity of cylinders manufactured per sample.
a63dbd7f-dc11-5f10-b44f-3f0966a5ab75 | note | ○ Record: Required information on the Concrete Pour Record.
fe211f06-c32c-5e31-80d0-3380ab7578e5 | note | Method - Test
73716692-0aca-5e67-aadb-d7d59577c64d | note | Frequency - Each sample
3d7d0da6-d90f-50e1-97c9-ec8535abf68c | note | Category - IP
0e3cb82a-c0e5-578f-96b2-e18f39fb7db7 | note | Responsibility - Concrete Tester
e457119d-e912-5784-a380-4932a2f45290 | note | Verifying Documents - This ITP
c9648c6c-468c-5511-9d21-ca979ff81298 | date | Date Completed:
10803547-0fca-49ae-a436-27061b698fd7 | checkpoint | 5.12 - Placement & Compaction (Dry or Wet Excavation Conditions)
3154ec1c-1398-58f8-9616-7c68f599ddfd | note | Reference - Piling Quality Procedure 610.18 (a) & (b), 610.18 (d) (i), 606.06 (a & b)
3017fa97-5f52-55dc-9a0f-5d62b549203e | note | Acceptance Criteria - Concrete shall be placed within 24 hours of excavation - where this has not been achieved, the internal wall & base of the excavation shall be cleaned to an additional depth of 25mm.
a373b48e-9b43-59e3-bdbf-9e738753355b | note | ○ All concrete batches are traceable.
c8305b36-ecfd-5875-87fb-0b4c3c634284 | note | ○ Concrete shall be placed through either a tremie pipe or concrete pump and not dropped freely from a height exceeding 2m.
e498aea1-7d04-5e0e-91be-d848d484f5bd | note | ○ The initial discharge is pumped to waste until a consistent workable mix is discharged.
6351775c-23c5-5768-9c2c-8fe341c27cc0 | note | ○ The ends of the discharge pipe shall not be lifted off the base of the excavation until a 2m head is created, which shall be maintained until the completion of the pour.
7772b4fa-7549-5065-897e-a165cb3ccf05 | note | ○ Where a casing is used, it shall be withdrawn with care and at a rate to ensure that the free surface of the concrete is at least 1.5m above the bottom of the casing.
439388e7-9c48-5630-a04c-97c96e17c10d | note | ○ Pile height is to be 300mm above the cut-off level (or 400mm in wet piles) to allow for breaking back of sound concrete.
279b2c91-653b-5ac5-a2d0-c21ace1ba519 | note | ○ Record: Required information on the Concrete Pour Record.
72e0632a-6910-52dc-9919-a40fe31e51d2 | note | ○ Attach: Concrete Pour Record
774a5f60-512d-57df-8dd9-85c4ff6b0c91 | note | ○ Attach: Concrete Dockets
fb63ac46-f922-5f6f-9cae-ee331bfe9e64 | note | Method - Visual
97cfefe5-925d-52c7-a4ff-82b7ec865cdc | note | Frequency - Each load
088e80df-ccea-5b02-9912-829dabcfdd2d | note | Category - SP
aa932dc8-0f7c-514c-a653-09167d5906ae | note | Responsibility - Foreman, SE/PE/SPE
c672982b-3637-5554-a757-32c346c3b79b | note | Verifying Documents -
4e173637-0de0-5837-9e59-ed1fc99b09cc | date | Date Completed:
b2a75235-2de1-4331-b289-b5afa49c90a0 | checkpoint | 5.13 - Surface Finishes
882d567f-ae38-57f4-a7b0-ee3f7c34806c | note | Reference - IFC Drawings 610.31, 610.20
8534dc77-c7b8-5e94-b157-4d2dd1f83b0a | note | Acceptance Criteria - Surface finish as per IFC drawings.
9ebbc812-135d-5ff4-9d2c-52c26c464d57 | note | ○ Where surface finish is not detailed, the VicRoads class finishes will apply as per 610.31.
878bd62f-e664-520f-8f0a-7a8812990f01 | note | ○ Construction joints shall be roughened in locations shown on the drawings - any proposed changes to construction joints shall be subject to approval from the Nominated Authority.
be04166b-b426-5a93-b010-91d94489350f | note | Method - Visual
76968ea8-6c99-5b95-913e-fe98def2d482 | note | Frequency - Each pile
b03aedd2-7ed3-52a5-9ffe-ff53fc5cc8f1 | note | Category - IP
c8dff89c-9755-5e4a-a0d9-05f9b9593115 | note | Responsibility - Foreman, SE/PE/SPE
4271c52c-7a9f-58d1-8582-0b89dfd7d22e | note | Verifying Documents - This ITP
ac9fe326-ffcf-52e8-a44a-2aee6f796231 | date | Date Completed:
080f32fe-57b0-4108-b6ac-66a7ffed6837 | section | 6. Post-construction Activities
06c707fe-32d1-47ce-96b2-3dfee5874d39 | checkpoint | 6.1 - Pile Trimming
912ab390-9e0d-5baa-9be9-d3e6864d07ce | note | Reference - IFC Drawings AS2159 Clause 7.2.2 - 3, 606.06 (a & b)
eee9bca5-1566-5b16-9d5f-e2e32846f58b | note | Acceptance Criteria - Piles shall not be broken back until a minimum of 24 hours after completion of the placement of concrete.
3d4e5568-1541-52ed-8565-156c8e7adf01 | note | ○ Care shall be taken to ensure that the full cross-sectional area of the pile is at the required RL without any cracking or damage.
be34a95f-a8b7-57a3-8af7-434d79ac855b | note | ○ Any weak or damaged concrete shall be removed back to sound concrete.
c629983e-d1b0-5267-b825-9140ae2c6850 | note | Method - Measure, Visual
8bc9e02a-91c1-507e-a71f-166ca5e11310 | note | Frequency - Where applicable, each pile
d018ee46-ea70-5eb4-acce-85b2596485c3 | note | Category - IP
310427fe-697b-5625-9926-a004b7c0d433 | note | Responsibility - SE/PE/SPE
94328a38-fffe-5b29-8e3e-2d9590a27726 | note | Verifying Documents - This ITP
5ae42398-7948-52a9-9f17-4895c3448816 | date | Date Completed:
28ee0aa6-2494-4047-b76f-e3ef8eb3c633 | checkpoint | 6.2 - Compressive Strength Test Results
ebad6b28-af22-512e-911a-c247b149956a | note | Reference - IFC Drawings Table 610.05.051, 610.16 (g)
ed28f54f-e193-5c0f-9699-4506696f91bd | note | Acceptance Criteria - 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly.
1fd790b3-9e70-56bd-bbff-1148ff922679 | note | ○ 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
250cc22b-091d-588e-8516-2c1a26430271 | note | ○ Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength.
154147bb-979b-52d5-80e2-ec519797cbdd | note | ○ Attach: Compressive Strength Test Results
65a56a88-6460-5c83-bdef-7c02b6f1cbf0 | note | Method - Document Review
09f86e99-ef79-5b02-b76e-adb6a09dd05a | note | Frequency - Each cylinder
7cbf7635-c975-54ce-9f65-063fe92a853c | note | Category - IP
58cd5ab7-1cdc-59e9-a7e2-19a33b0b84a9 | note | Responsibility - SE/PE/SPE
3e22dd16-cd81-530c-9ca5-f60c49335349 | note | Verifying Documents - This ITP
cf31b475-27b2-5e8a-927f-21ef67175962 | date | Date Completed:
4f15791d-d961-4e1c-84ee-b08cd69a43aa | checkpoint | 6.3 - Pile Integrity Testing
23e4cf74-79c3-5b86-a7b3-7a38e39fd2b3 | note | Reference - 606.07 (a, d & e) AS2159 Clause 8.8
01f36b79-d604-5a31-815c-ce9807ddfec2 | note | Acceptance Criteria - Pile integrity testing shall be conducted after the concrete strength has reached 25MPa but not less than 7 days from casting.
f8df3cbf-5d2a-5afa-bbb0-ff952ccbc986 | note | ○ Cross-sectional area = ≥95%
11144b85-2a76-54d2-8b7d-6039840a7eee | note | ○ If any test fails, all piles shall be tested.
7191b589-d60b-5987-8b7b-8fc1718a1498 | note | ○ Attach: Pile Integrity Test Report
b325d18e-427b-5aec-8755-c9b8ce49cbfc | note | Method - Document Review
1b2fcac8-68e4-55df-aaed-2d92dddc4fc1 | note | Frequency - Piles #1 - #6. Reduced to 1 test per 3 piles if the first 6 tests pass.
a64c66ca-c9dc-5715-b813-98f52698e0c7 | note | Category - IP
dbaf942d-1569-5269-b72e-a6207828c3d0 | note | Responsibility - Testing Consultant, SE/PE/SPE
54c4d3e8-c7e1-53d5-9783-78f00e105db6 | note | Verifying Documents - This ITP
d20c7483-e18a-552a-93fd-548351a79044 | date | Date Completed:
d177dc8e-e7a5-4638-8a84-bce2534ebd71 | checkpoint | 6.4 - As-built Survey
c1857083-3a34-5d40-86c5-ea3aa6097f55 | note | Reference - IFC Drawings 606.08 (a - c) AS2159 Clause 7.2.2
b46e2e53-235d-59df-bc62-54a61e918c4f | note | Acceptance Criteria - The following tolerances apply to piles:
d2a4dc1d-9e93-579f-b1c6-3bda641a4460 | note | i. Pile head plan location = ±75mm
24f76a9f-caa6-58de-8b18-9ede28794067 | note | ii. Variance from vertical or rake = 1:100
0df62281-47f4-5ed9-ad7c-878142a85e1e | note | iii. Irregularities in straightness = 1:100
3ad5c9a5-7261-5a12-898b-358a0aeb36b6 | note | iv. RL = ±25mm
14a08fb5-a4e8-58f6-8b9a-e3e10bd6f51e | note | ○ Attach: Survey As-builts / Survey Report
5f8a3744-28d8-5ad8-8367-5795c2d7ab11 | note | Method - Document Review
da00ee21-46d5-559d-b613-2e841a2ac120 | note | Frequency - Each pile
8f2fdc42-17ca-52e1-adb8-65d2955202d2 | note | Category - IP
24b78e61-7596-578a-be05-a81477dbd608 | note | Responsibility - Surveyor, SE/PE/SPE
324f6598-2c1d-5961-9ba1-c557d5549fd2 | note | Verifying Documents - This ITP
f5ff138f-1296-5966-b800-3b5d06671105 | date | Date Completed:
ad9cb318-8639-4df6-a845-ca3b34b6b1dd | checkpoint | 6.5 - Non-conformance Report (NCR) Closure
35635b62-7ca1-5833-8723-098ff4741824 | note | Reference - MRPA Quality Management Plan
110f34b7-94e7-5701-b64b-49823bb2e8cd | note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
57c27e2b-f0ba-50db-9d4f-661ac627ac53 | note | Method - Document Review
71dfb212-7cbd-5903-89be-cd7fe061c554 | note | Frequency - Once, prior to closure of this lot / element / Work area
534c5bfa-3333-5fb2-bf68-e795ef84ff92 | note | Category - HP*
ba6debef-08a3-5b9e-9e94-ea061d4e6c2f | note | Responsibility - SE/PE/SPE
733f9f11-386f-5d79-a2ee-bdd2bdcc6f82 | note | Verifying Documents - This ITP
2a648f33-82ec-529b-94c1-0fcece71c7d9 | date | Date Completed:
dfdeeae3-4094-4f5c-a54d-6615a88b64d2 | checkpoint | Final Inspection
e3ddfcec-bf7e-5f0d-a438-5c8ddee53a42 | note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
2e06820d-8873-59b5-9730-83d0461c4823 | textbox | Name:
bf6baf3a-0eb5-54a6-ae8a-01fc8edb282f | textbox | Position:
350b3e42-34dc-5237-9f6f-8b6d5e97ff00 | textbox | Date Completed:
38e90cd7-8541-4a20-b2e2-3d4eb96dd29e | signoff | Sign ITP
aed06526-4315-44b2-9b13-a6334788e82c | checklist | ITP-308-STR-MSS-Structural concrete Rev 0 | itp | ITP-308-STR-MSS-Structural concrete
ba5e384e-f50f-4186-a0bd-7db7d3506544 | section | 1. Referenced Documentation
7d8d1419-bf1e-4836-8535-d3de3a11f7e9 | checkpoint-no-value | Referenced Documentation
6a01a600-02f2-58f3-8a42-19af04b1f97d | note | Document Title: ITP-308-STR-MSS-Structural Concrete
96c43a37-4812-542f-b531-4e4e2a1638e3 | note | ITP Description: MSS-Structural Concrete
c7a0ec28-1bea-5854-8445-d18519b0beee | note | Discipline (e.g. CIV/STR/RAIL): 308-STR
4157e4a0-438e-599e-b4a5-259918d090a7 | note | Revision Number: 0
02ff18b6-821e-5394-a8ce-5c38f274dc80 | note | Revision Date: 28/08/2025
35d107eb-230a-5d8c-935b-f0a2f58a23bf | note | ITP created by: Andrew Carlini
644d2554-1085-53d1-b4b4-af235b1e1792 | note | ITP approved for use by: Romualdo Magpantay
f62df3ca-f172-5949-82fc-9644245e7b47 | note | 1.1 - Non Dependent
ced9daf0-bb6a-526e-b51c-e9a2f709194b | note | Reference - DTP Section 602 October 2007
f2e7b065-b9e7-5cb7-a095-a1127f2ed797 | note | 1.2 - Non Dependent
f9dd9ebd-8693-5051-98e9-d659a5fc726a | note | Reference - DTP Section 610 February 2020
e852c330-c575-580c-81d9-c5ef7e9db4f1 | note | 1.3 - Non Dependent
2f10058c-1e72-5940-9f33-2173d1a76e75 | note | Reference - DTP Section 611 November 2018
9a972fd7-21ee-5da6-be45-7476e2d62511 | note | 1.4 - Non Dependent
89a431ee-affe-58d6-9a78-8c0ea694d081 | note | Reference - DTP Section 614 June 2017
2f62b773-9348-567a-bce8-e33a89e2edb2 | note | 1.5 - Non Dependent
a00839cd-f283-5c10-9a36-a983db1066c5 | note | Reference - AS3810.1 2018
5b4436dc-6842-4790-8eee-b07a3289da85 | section | 2. Preliminaries - Materials
4997429c-6788-4573-9797-b3db8460b99f | checkpoint | 2.1 - Concrete Mix
252b6b3b-aad9-5a42-9db3-b99559282e40 | note | Reference - 610.07, Table 610.071 IFC Drawings
166e0978-b18c-504a-b23f-3ca7110427ba | note | Acceptance Criteria - Concrete Mix is Registered with VicRoads.
06517b76-63eb-5899-9d1e-312c9bfba58c | note | ○ Concrete mix meets strength, grade, and maximum aggregate size as detailed on drawings.
c4d45773-a492-52c8-afef-0a7e2765de78 | textbox | Enter: Teambinder Material Approval number
5932a7ec-3af6-5cf4-b7e8-3b31c5f2ee0c | note | Method - Document Review
00ddadfe-b9c4-54a3-bd78-fe18d6bf050e | note | Frequency - Once, for each mix design, 4 weeks prior to placement of concrete
f4a636fe-3776-59a4-a146-60e3f84632ce | note | Category - HP
e610835e-9038-5504-8083-8cb217501943 | note | Responsibility - Nominated Authority
2a261822-6105-5bb4-9a80-afb6471999da | note | Verifying Documents - ConQA Hold Point Release
fbc93af7-9a52-5e78-9c20-eb214154a066 | date | Date Completed:
d1bf7f10-e0c3-4e7f-94da-5201ee48cbcb | signoff | AUTHORITY HOLDPOINT
d9b10eeb-75dd-457e-820a-a02840df66f0 | checkpoint | 2.2 - ACRS Certification (for Reinforcement) Bar Chairs/Aspros Certification
0c5a7944-6ee4-58bd-a693-42f2bf1012cb | note | Reference - 611.05 (a), 610.26 (a)
d5b4c103-b701-5403-a78c-01ee1491b2aa | note | Acceptance Criteria - Current ACRS certification for materials and for bar processing.
b16d0b49-22a7-5b76-bb21-b117fa39c4a5 | note | ○ Note: ACRS certificate may cover both aspects or be for each separate portion (e.g 1 for the material supplier and another for the bar processor (bending, cropping and delivery)
549e0a55-8908-58ce-b4d6-5fb80ff0aaed | note | ○ Plastic bar chairs, wheels, and spacers require bi-annual testing to demonstrate suitability to prevent excessive deformation under loads.
0f79d101-1477-573f-a038-c721124a35b9 | note | ○ Concrete aspros require annual compressive strength and soluble salt testing is required.
594d7626-0c94-5a28-8e1c-021386e0bb30 | note | ○ Relevant test reports demonstrating compliance to this clause shall be submitted for review to the Nominated Authority.
26ab8119-2dff-5a09-8a31-df1297689032 | textbox | Enter: Teambinder Material Approval number
383bfd6d-2309-54c0-99db-cc0342795df8 | note | Method - Document Review
31026620-be6a-53e8-b247-162b239d97c2 | note | Frequency - Once for each supplier, 14 days of award of contract
cdf581be-f305-5521-a5de-5572b5560fe4 | note | Category - HP
f05e6804-bf7f-5a12-b6ae-d335b5a1ca7d | note | Responsibility - Nominated Authority
239715d0-08fc-5436-98fc-a546a4160eb2 | note | Verifying Documents - This ITP
1a846a4c-aa36-5ae0-980f-3690fbb49cc9 | date | Date Completed:
9d647a2b-7ed9-4278-9e2d-4b84178c512c | signoff | AUTHORITY HOLDPOINT
eb95680f-4384-4375-b63f-47e19708f469 | checkpoint | 2.3 - Evaporative Retardant Curing Compound
8c8a887c-0b74-5aa1-bdea-5952e318fda3 | note | Reference - 610.17 (f), 610.23 (d)
7c016d77-762d-5f23-aaec-6d9c3798a92c | note | Acceptance Criteria - Details of evaporative retardant, application procedure (including application rates) to be submitted for review to the Nominated Authority.
4c6912f8-5a22-52ad-ba3e-ece8c254243a | note | ○ Details of curing compound and NATA test certificate stating compliance with AS3799 no more than 3 years from issue, to be submitted for review to the Nominated Authority.
52a2cd95-cdb3-50be-ae5e-4b2bd2edadbf | textbox | Enter: Teambinder Material Approval number
7d6cbe10-cd10-5770-9fe0-3c74c1f13129 | note | Method - Document Review
ad74046e-e3be-576e-b53b-8663e61be743 | note | Frequency - Once, for each product, 4 weeks prior to placement of concrete
c92009f1-4c5e-5c5c-8b37-e5db13fcb23f | note | Category - HP
87bbb4b8-1b1d-55c6-bbae-15736b91514b | note | Responsibility - Nominated Authority
6fc43390-e8e2-5ee4-8149-a1f00e64876a | note | Verifying Documents - This ITP
b135331a-62ef-578f-95d8-00b13ccb5e1b | date | Date Completed:
5cbccac3-cc61-4dbd-9eef-00b3ffdfc0c8 | signoff | AUTHORITY HOLDPOINT
7c4a361a-71b5-4ae1-b6b8-a5cfc8b48549 | section | 3. Preliminaries - Procedures & Documentation
daa61d96-fe39-4d3c-84f2-a8591f6024a6 | checkpoint | 3.1 - Concrete Placement and Compaction Work Method Statements (Concrete Sampling and Testing Procedure, Concrete Placement and Compaction Toolbox Meeting, Hot and/or Cold Weather Concreting Procedure, Curing Methodology (for Concrete and Grout)
07a69928-c5bb-5e39-866a-57748542bc3b | note | Reference - 610.18 (a) (i)
aaeb0272-9e5b-5986-8b53-aa759c4f865e | note | ○ 610.18 (a) (v)
a75479fe-7f77-5dc9-a4d7-5b1b780ee6c4 | note | ○ 610.18 (a) (iv)
7beffa2e-75eb-529d-a082-8e6db2935daf | note | ○ 610.17 (a)
b668a2b8-4ce3-5005-bca8-661e76402f53 | note | ○ 610.23 (a)
acdf5a5e-70d0-5222-844d-7e42922f022a | note | Acceptance Criteria - Concrete placement and compaction WMS to be submitted for review to the Nominated Authority.
fc2f9bec-bb55-5773-ba21-1286460cee6f | note | ○ Concrete sampling and testing procedure to be submitted for review to the Nominated Authority.
b815955f-28d6-5e10-afc3-fe760a927ae0 | note | ○ Concrete placement and compaction toolbox meeting held to discuss the quality requirements.
2d6b02c4-a305-581c-8d02-1d49360194eb | note | ○ Minutes of this meeting to be submitted to the Nominated Authority.
5989bf46-a02e-58cc-98c9-8cd4f89964cd | note | ○ Hot and/or cold weather concreting procedure to be submitted for review to the Nominated Authority.
27a4c556-edad-5256-91e7-d115d31ca01e | note | ○ Curing methodology/procedure to be submitted for review to the Nominated Authority.
fa4847bd-1e1c-51cc-82c2-db0948a51c6c | textbox | Enter: Teambinder Approval number
bf104d4c-a836-5a89-8d6a-64f20545b151 | note | Method - Document Review
c3d966d2-12cc-5f4a-bc37-24019c97c9a6 | note | Frequency - Once, 4 weeks prior to placement of concrete
f50dde51-8c27-5af5-ab15-8264d02ee54f | note | Category - HP
2391a935-80fd-53cc-864e-9b433e8e6a8f | note | Responsibility - Nominated Authority
8c77a8c2-8fb8-5589-abd6-6ab5e0cd2690 | note | Verifying Documents - ConQA Hold Point Release
b366e728-8260-51ef-9e6e-45ca12790914 | date | Date Completed:
37bbdb3f-61d3-4fe4-a169-c53ba9b6c499 | signoff | AUTHORITY HOLDPOINT
008fddf3-1e33-4a38-b0ae-d5feae0637e2 | checkpoint | 3.2 - Concrete Drilling Procedure
301f5cc3-7838-5d46-bb69-0a1fc68c2f55 | note | Reference - 610.46
bc5eb14e-423c-5841-ac5b-c2b48b7575b2 | note | Acceptance Criteria - Where holes are to be drilled into existing (new or old) concrete members, the locations shall positioned to avoid striking any existing reinforcing bars, tendons and services.
96e94444-8c4c-59f5-a37c-13263b262dbb | note | ○ The planned locations and drilling procedure shall be submitted for review to the Nominated Authority.
8424c855-8604-54fc-a2ba-72590b1f0965 | textbox | Enter: Teambinder Approval number
c20cb787-1463-5434-b11d-3208f2ae9a50 | note | Method - Document Review
6c554df6-a4df-5cf8-8416-6a54491843ae | note | Frequency - Where applicable, once, 2 days prior to drilling
fab38f77-b47c-554d-87ab-1a2c4814505f | note | Category - HP
6c79a7b3-3122-50d0-ba9b-ed82a8a33b65 | note | Responsibility - Nominated Authority
5d3d7c8c-0cfc-51e4-9c92-799ade9f6823 | note | Verifying Documents - ConQA Hold Point Release
2943a7e5-0620-545c-80d9-c1f968c899af | date | Date Completed:
2be75e82-6009-473c-826b-8e8861d64c1c | signoff | AUTHORITY HOLDPOINT
13e6b12c-c270-4d57-bae3-aee77ec7c18b | checkpoint | 3.3 - Temprature difference measuring-Calibration
b4d82dc9-1df3-5f00-a75e-0c9ab214daea | note | Reference - MRPA Quality Management Plan
03578302-237e-5478-80f4-49374104d628 | note | Acceptance Criteria - Calibration records are valid and up to date.
183e04f3-b85d-5b9d-a19a-69474f3fc1dc | note | ○ Attach: Calibration certificate
ae4a5f3e-b3dc-5b29-af71-1e69bfdf4711 | note | Method - Document review
904fd11c-6422-5c84-8f7c-4f2669422db6 | note | Frequency - Where applicable
eaf23428-4bcb-5a23-8c5f-f9c99d44c705 | note | Category - HP*
f1330f6c-544c-5fec-9830-3e38cccc583b | note | Responsibility - PE
17f9e6c6-67f4-56cb-86da-92ce6a59baad | note | Verifying Documents - This ITP, Attached calibration certificate
3d5dbc2d-c698-58c9-9558-afd81b594c8d | date | Date Completed:
bc674644-986d-443e-ac71-9742f97a6bc5 | section | 4. Pre-construction Activities
de66459f-28d7-4a55-990c-7d673126f85a | checkpoint | 4.1 - IFC Drawings
284f6524-b7e5-599f-a7d9-93502f796041 | note | Reference - MRPA Quality Management Plan
29f310cf-1183-54ef-8a44-1fdeffc77b70 | note | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
064f1232-df56-53cb-9a80-e5fcc7773c47 | note | Method - Document Review
0af80382-0640-54c2-8d08-caac2d9a1e1c | note | Frequency - Prior to starting Works and at regular intervals
71ac3837-86b1-5e08-aab5-26ca3ec3b979 | note | Category - HP*
b3258a69-944f-56c3-b9d3-7cde23a7f4ee | note | Responsibility - All
bc0ddcfb-5263-53b7-bcf8-2732251dcf37 | note | Verifying Documents - This ITP
3c1d6bfb-4707-5ef9-893c-9fe5d7573f54 | date | Date Completed:
15269fdc-2cbf-4f63-8fc1-6ff6e7309ce2 | checkpoint | 4.2 - Survey Set-out
b760c67c-b522-5f7c-a0bd-a0c151ff3a3b | note | Reference - IFC Drawings 610.47 (a) Table 610.472
7e225052-8107-5643-83fb-e1055ce126c2 | note | Acceptance Criteria - Survey activities undertaken to ensure and validate that all Works meet level and location requirements within the tolerances as per the table 610.462 as applicable to the element.
7fbd085e-6e52-5a11-bf12-5dbac37f1f49 | note | ○ Attach: Lot Map, Marked up drawing which shows the Lot Location and extent
00ab5fd3-6abc-5c6e-9295-6ff0261d9997 | note | Method - Measure, Visual
4a4c7582-b514-5555-b43d-6da0e11cc26c | note | Frequency - Each element
bb9d619a-58ad-5dbf-9a66-820e2f8edf16 | note | Category - IP
c37e34ed-2f45-56ed-8cbf-4fefc23f72d8 | note | Responsibility - Surveyor, SE/PE
92ae5716-2f6c-5c73-a6dd-4b30522f8a31 | note | Verifying Documents - This ITP
0655d2b7-946d-5ca4-999f-7bc778b812eb | date | Date Completed:
005032a5-b78e-417b-a44e-395d843791dc | checkpoint | 4.3 - Excavation support
86fc8a4c-826c-5408-862c-dc63d5a3dffc | note | Reference - 602.02
7d997a1d-090a-53c0-93e5-3dddeb4a90c4 | note | Acceptance Criteria - For excavations adjacent to railway property, alongside roadways, in or alongside waterways, and excavations deeper than 1.5 m, the Contractor shall submit to the Nominated Authority for review detailed drawings of bracing and/or sheeting proposals, including design calculations and methods of construction and removal.
e70af64a-842c-5e68-abae-85fd153d624f | textbox | Enter: Teambinder Approval number
41acbc9c-771f-5365-985c-7fb19a3391c9 | note | Method - Document Review
cf804bba-587c-56f9-9d6e-fef8ca5a797e | note | Frequency - Where applicable, not less than 10 business days prior to excavation
7c20b604-842a-5ac3-b097-f924e76cb500 | note | Category - WP
76f779c8-79f4-54c2-9ff2-77e8d66c391d | note | Responsibility - SE/PE/SPE
62f7244d-7118-5422-9a5e-a1985df397ae | note | Verifying Documents - ConQA Hold Point Release
c02a19a0-5db7-5347-ad54-312de5a19f5b | date | Date Completed:
529aecce-1a75-4d6a-9b05-6e57e8bf90d2 | checkpoint | 4.4 - Excavation Inspection
b384176f-43ce-5e50-9fe6-ea71e355ca31 | note | Reference - 602.03
a523be06-3452-5439-8f49-e599b29f1c1b | note | Acceptance Criteria - Blinding concrete shall not be placed until the bottom of the excavation has been reviewed by the Nominated Authority.
aac61a22-2688-581c-88ff-166ccb0b5b7a | note | Method - Visual
13bc6c62-37c3-51e4-ab91-56f7d17e0ad8 | note | Frequency - Where applicable, prior to placing blinding concrete
b2a307a7-db91-5359-b45b-7f3bd1f22b07 | note | Category - HP
c1b06c4a-5360-5794-8fce-e42e2730e7ec | note | Responsibility - Nominated Authority
2ea2bd09-bdd1-5c3f-91b4-6c2e3046c921 | note | Verifying Documents - ConQA Hold Point Release
469b77e4-3bb1-544c-a312-67be8e96f069 | date | Date Completed:
5bb5b8fb-f1cc-4b39-95ce-665a2656d123 | signoff | AUTHORITY HOLDPOINT
3cb359c4-b273-45f9-90ac-5004747976aa | section | 5. Construction Activities
f954c9aa-7a6d-4d32-97f6-b0ec4d8a6246 | checkpoint | 5.1 - Formwork Design and Construction
438d62f3-e88b-5293-ae4f-ac448c510e7c | note | Reference - IFC Drawings 614.04, 614.05, 614.06
328857d4-e403-5f5b-a0a8-4622cdf49fff | note | Acceptance Criteria - Designed and constructed in such a manner so it can be removed without damage to the concrete.
e3d5b61c-af2a-5d4b-beb2-477243058152 | note | ○ Formwork to be rigid, watertight, braced, tied together & selected to achieve the required surface finish.
9caea330-1b88-533b-9b3d-7331affd68ba | note | ○ Formwork shall not be placed where steel & fixtures cannot be inspected.
2cfb7629-52fc-5baa-ae82-4cecc972ea64 | note | Method - Document Review, Visual, Measure
fad202fa-32ee-54a4-afe2-09c60443ad8c | note | Frequency - Each type of element
74c882d2-6be6-5531-9578-9e8e20c61cfc | note | Category - IP
3be996d7-b0e8-59c8-a38b-d2027528a9f2 | note | Responsibility - Temporary Works Designer, Proof Engineer, SE/PE/SPE
d3b65393-412d-5fc7-ad7a-e3bb09912c2e | note | Verifying Documents - This ITP
58420856-fec7-599d-97fc-4a5479667fad | date | Date Completed:
0fb00d7a-85cb-4b8c-a147-7e65a36cc8fc | checkpoint | 5.2 - Formwork Certification - Formwork Inspection (Members Greater than 2m)
2766b93d-918e-5c5c-89ec-d40e16021d29 | note | Reference - 614.08
e591d00e-325e-53e3-9309-1a7a23251b2c | note | Acceptance Criteria - The application of any load shall not proceed until the Certificate of Compliance - Formwork Inspection of the constructed formwork has been reviewed by the Nominated Authority
afa03d7a-5237-59fa-a1c0-5bdd3bf16f3d | note | ○ Walls with heights greater than 2.0 metres
7560fbb0-bb3b-55a4-a68f-47758e51bc0f | note | ○ Any member for which self-compacting concrete is proposed.
49be003b-9228-5cdb-9b0d-aa935faac49b | note | ○ Attach: Attachment A
5a79cfef-090d-51de-acd4-d8ce2fdb3c2c | note | ○ Attach: Attachment B
89a2e64c-7595-547b-b70f-3f45d7b3cb14 | note | Method - Document Review, Visual, Measure
539e7648-ad70-5aa1-b212-f05f0eddd980 | note | Frequency - Each element (where greater than 2m)
b73f9524-c96b-5dac-b767-98d46ac140d6 | note | Category - HP
bb001db5-1a62-57e8-8fdf-52edba5a29c6 | note | Responsibility - Temporary Works Designer, Proof Engineer
5bd852ed-18ec-5035-84f0-5458c083b4d1 | note | Verifying Documents - ConQA Hold Point Release
97451bc3-2ec4-5f5c-8e25-9e5150c7c6a6 | date | Date Completed:
d88880dd-e71a-48c3-b0ad-76fd8c5c0e17 | signoff | AUTHORITY HOLDPOINT
6cd73211-ee7c-4641-bfec-742bd28be2af | checkpoint | 5.3 - Formwork Certification - Formwork Inspection (Members Less than or Equal to 2m)
da59e2ef-9173-52ca-92a5-69c618e147d4 | note | Reference - 614.08
87f5e10b-298f-5b56-a21d-d273948ad7fe | note | Acceptance Criteria - The application of any load shall not proceed until the Certificate of Compliance - Formwork Inspection of the constructed formwork has been reviewed by the Nominated Authority
e7531e4d-5baf-5732-96ed-32ed3f329694 | note | ○ Walls with heights less than 2.0 metres
c8230c85-4dbc-54e8-9c7a-cf0bddb08f1e | note | ○ Attach: Attachment C
ae6fc42b-22dd-5bed-a640-6c2bcdd57c65 | note | Method - Document Review, Visual, Measure
6188c21a-c38c-530d-bc74-8a95a6252d6b | note | Frequency - Each element (where 2m or less)
6b8975e6-67eb-5f6b-95a6-97cd3abfcc71 | note | Category - HP
420992f2-b6a4-5c9d-8781-573f17580e5e | note | Responsibility - Temporary Works Designer, Proof Engineer
4c76597c-f817-510d-947a-2e2a2cfbfef6 | note | Verifying Documents - ConQA Hold Point Release
e6bc89a9-a4cd-5987-925b-bb7df2f31e55 | date | Date Completed:
2bf2c576-24d8-4f57-a2a7-7947c9e9a3ba | signoff | AUTHORITY HOLDPOINT
a745ed40-384a-41d1-a4f5-ec91ae68a605 | checkpoint | 5.4 - Pre-pour Survey
4e39af5e-5e9e-5ad1-91af-8ea2aca37537 | note | Reference - 610.47 (a), Table 610.472
1663ca13-6135-5bdb-b57c-e669a5b0aaf2 | note | Acceptance Criteria - A pre-pour survey carried out by a surveyor.
712e5983-dc78-54da-b87e-1b0608ae1913 | note | ○ Erected formwork within the tolerances as per the table 610.462 as applicable to the element.
6510f15f-4289-543f-8a48-dbe55ba01bb1 | note | Method - Measure, Visual
5d37694e-d582-5304-9d1e-eaea05c8de5e | note | Frequency - Each element
af25b2f5-50d7-5d67-b824-936be57cde9d | note | Category - HP*
ff9c0654-7037-5635-9da0-4afd7403335a | note | Responsibility - Surveyor, SE/PE/SPE
f165c2e2-0de9-5266-9b30-6bf562f36ab0 | note | Verifying Documents - This ITP
28c6daf0-ca8f-5072-8b5b-3a72b5e86311 | date | Date Completed:
a4be2861-e2d1-404e-89ad-4b18436734e7 | checkpoint | 5.5 - Reinforcement Placement
3f9e19a0-74e7-533d-8a94-c4710b0e11a5 | note | Reference - IFC Drawings
ece7add2-0326-55f1-9d77-c4a1cf0486b7 | note | ○ 611.06
6175cf15-7e2c-5f95-8860-53710ee9885a | note | ○ 611.09
3fca57e0-a344-51a9-a8a5-ce470a126728 | note | ○ 611.10
1da0b7c3-d802-59f0-8f47-f8d361aa2c8c | note | ○ 611.11
fa6b1b74-a968-5625-a249-301530ff5ffb | note | ○ 611.12
51eceb4a-cb55-53cb-8e7d-77fb1fb21061 | note | Acceptance Criteria - The correct reinforcement grade, quantity, size, orientation, location and spacing as shown on the structural drawings.
db04fc5d-88c3-51e7-ba70-ca5dd20062e2 | note | ○ Projecting reinforcement is the correct length and location.
06549a0e-f505-5603-8596-385bbbaf8dca | note | ○ Splice lengths achieve the minimum length and are in contact for this length.
d6332bc6-3533-5b90-8a80-794bd80053f1 | note | ○ The reinforcement surface condition is free from dirt, debris and damage.
d9dfe9cc-83cd-5bcd-bf46-df16977f2e99 | note | ○ The resulting cage securely held with sufficient ties to limit displacement or deformation during the concrete pour.
9fb6245a-cca4-57cd-9c4a-78d9a10c0500 | note | ○ Minimum cover as shown on the structural drawings for each face has been achieved (including tie wire locations).
3c4fece5-4b64-5878-8d7b-1673e74db84e | note | Method - Measure, Visual
b50d39dd-be12-5161-8b56-5e85acd99d67 | note | Frequency - Each element
6b39ddc8-47a6-5eee-9256-2f365c32fdca | note | Category - IP
67a158af-233d-5438-803f-5a192a6522b2 | note | Responsibility - Foreman, SE/PE/SPE
79a95081-46c3-54c0-87d7-171889384b52 | note | Verifying Documents - This ITP
8585ff0c-7239-59c6-8a45-8478b6baa6a0 | date | Date Completed:
8af6fd82-5c8c-49a1-93f2-1a4c4dd838d4 | checkpoint | 5.6 - Cast-in Items
31a78ea2-6d70-589a-8c14-849561a55e9f | note | Reference - IFC Drawings
5d8fde4c-fa07-5c5b-bd41-15c04bda7241 | note | ○ 610.47 (a), Table 610.472
438b1268-c0c4-5ee9-b4c1-cdb4c919ec43 | note | ○ AS3810.1 Table 3.3.6.2
653cfcdd-4458-57bc-b697-4157787f7031 | note | Acceptance Criteria - All cast-in items are the correct type, grade, quantity, size, orientation and location as shown on the structural drawings and are securely fastened or restrained to withstand impact and pressure during the concreting operations to prevent dislodgement.
a46a93e0-021f-50b6-ba32-1bc6b11b957c | note | ○ Any exposed threads, conduits, ducts or voids shall be protected by suitable means to prevent concrete or grout ingress.
719b5a0d-82b2-55b9-a670-3b332c9bc06f | note | ○ Tack welding of any cast-in items shall be performed by someone pre-qualified to do so.
e3eaf736-f743-5089-8ae1-4d4bc26b7da5 | note | ○ Grout tubes shall be fastened at regular intervals to prevent kinking.
fff554b8-bbbd-590a-8fdb-83862bd381cc | note | ○ Placement tolerances to comply with the IFC drawings, if not specified, use the following:
8d7573ab-e7f8-5d44-9520-370b9430a050 | note | i. Bolts, ferrules, projecting bars & couplers = ±3mm
9e767203-016d-571c-82aa-71f92c3d3724 | note | ii. Running dimensions of a group of the above = ±6mm
7ea8b8ec-8c2d-5c33-b218-3e494e4e5750 | note | iii. Ducts and conduit location = ±12mm
294be9b2-25fa-5ef8-b3fa-d959455c87ab | note | iv. Diameter of ducts and conduits = ±3mm
28bb7e4e-f67e-5cb6-9f94-d69cb038ee53 | note | Method - Measure, Visual
2fee6dcd-bf80-5eca-9426-80df7fef9788 | note | Frequency - Where applicable, each element
823f8e36-0eb2-5d02-baa4-ef2d166aeef9 | note | Category - IP
ddaeb365-321d-5f11-93d1-1e3879c5721b | note | Responsibility - Foreman, SE/PE/SPE
4ce5e71a-0574-514c-b8b0-3cbded8fea6a | note | Verifying Documents - This ITP
36613d1b-2d34-5199-8afb-670b213de9db | date | Date Completed:
5fbfc6d2-e686-4c09-9105-6331b201f3ae | checkpoint | 5.7 - Thermal Differential Monitoring
c28881f7-03c1-5898-9765-d10139d219f9 | note | Reference - 610.22
e48c55a1-4710-5e12-a737-fdb034089194 | note | Acceptance Criteria - Thermal differential monitoring thermocouples installed.
bc332509-7395-59c6-aed3-2fc661df3096 | note | ○ Only applicable if the element has:
48f06a41-d569-58f5-894f-9c7aecf16493 | note | i. the smallest sectional dimension exceeding 500mm
985badf5-41e1-5182-8c03-b3d888ed8cfa | note | ii. one or more faces being restrained by previously hardened concrete or other external constraints
fc517e3f-e0c0-5f2f-b5e9-377375124acd | note | Method - Measure
ceb21219-9f8a-5578-987d-b50a8fac1ef8 | note | Frequency - Where applicable, each element
ad0ca0ba-dd3c-547e-85fb-ee9facd464a9 | note | Category - IP
3a896d27-86bb-5881-a969-c84fe78cad5b | note | Responsibility - Foreman, SE/PE/SPE
a445c097-8966-5d5c-b3eb-293bdc381c73 | note | Verifying Documents - This ITP
ea4dab84-8a59-5d6e-808a-0b820590d1f0 | date | Date Completed:
f3fa17e2-b8af-4873-8978-8aeb4a2f408f | checkpoint | 5.8 - Pre-pour Inspection
0692cdb7-6180-50e9-a864-2f6286a97211 | note | Reference - IFC Drawings 610.18 (a) (ii) & (iii)
baca361d-8b15-50f0-ae8f-477a9012f9ff | note | Acceptance Criteria - Evidence that the forms, reinforcement, electrical continuity and other cast-in items conforming to the requirements of this specification and the drawings has been reviewed by the Nominated Authority
6f600ecf-1ed3-56ab-bffa-7fb6280c0b16 | note | ○ All foreign material has been completely removed from the forms.
40bc5ba8-6874-5c0b-80e9-4ebbe7b7c846 | note | ○ ATTACH: Pre-Pour Checklist
5114c417-ec42-5362-a1f9-9a6750cc5d08 | note | Method - Measure, Visual
6fdf9d30-27cb-55d5-a8ba-42e2e44e6ec0 | note | Frequency - Each element
f06ecd02-facf-5a82-9134-d2c85a033b30 | note | Category - HP
36258b2f-637b-5c09-81fa-83f4ff2181c9 | note | Responsibility - Nominated Authority
16023bf5-96aa-56db-92b1-bc40706eb5cd | note | Verifying Documents - ConQA Hold Point Release Pre-pour checklist
61c38359-8134-5f1f-a4af-ebaf39a2e95d | date | Date Completed:
32c1471e-d943-4610-9f25-62a6166abd03 | signoff | AUTHORITY HOLDPOINT
721f173f-4cc0-4743-9c6b-d4494143a559 | checkpoint | 5.9 - Weather Conditions & Evaporation Limits
34800ac4-fefe-5ddc-bb62-1ec66a4d83fd | note | Reference - Hot and/or Cold Weather Concreting Procedure 610.17, 610.17 (a) & (e) Table 610.171
59a80fb2-defc-5432-9f06-2639b6b2e8df | note | Acceptance Criteria - All freshly finished concrete surfaces shall be protected where required from the sun, wind or rain, until curing is implemented.
d936d77c-c4fe-5117-b849-48642950fef8 | note | ○ The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C.
dfc297f5-98d6-5839-85d5-41695877c4d3 | note | ○ The air temperature, relative humidity, concrete temperature and wind velocity are measured to determine the evaporation rate of water from the concrete.
517ef9b2-6478-50d6-b79f-fa9fc9a8d90d | note | ○ When the evaporation rate exceeds 0.50 kg/m²/hr apply evaporation retardant at the rates specified on the manufacturer’s TDS.
7b75461f-dc4c-565e-9671-fbd01a5738e5 | note | ○ Record: Required information on the Concrete Pour Record.
e8585149-6c5c-5168-bfa5-609e1c3e7ac9 | note | Method - Measure, Visual
5d982d7d-4dec-53cd-93f0-1131a45c31cf | note | Frequency - Each element
b7ef3a4d-2a19-5727-b20e-3f5781c6a9d9 | note | Category - IP
976c686b-f36a-5c39-b422-fa57e5142168 | note | Responsibility - Foreman, SE/PE/SPE
02be46d6-9ee8-508e-90d7-857e6bacdc5c | note | Verifying Documents - This ITP, Concrete Pour Record
6edf328a-696e-5a0f-8dad-02c588a4e81c | date | Date Completed:
bb7abe0f-7ff8-4c54-a0fb-d36b5555740d | checkpoint | 5.10 - Concrete Testing - Sampling Frequency
c04f953a-3b2c-5f8f-9604-2d1968c9a9a7 | note | Reference - Site Sampling & Testing Procedure 610.16 (b)
c9be9b1a-6e4a-581a-94ee-3db1d9f8bb98 | note | Acceptance Criteria - Concrete cast in one continuous operation to be tested at a frequency as shown below:
a488043a-2d37-5f63-9b6f-d025bc5d0e80 | note | 0m³ to 10m³ = 1 sample
39933e3a-2615-50c4-b6d3-8056a7cc01ce | note | 10m³ to 25m³ = 2 samples
8d3d1f72-6e19-5196-8d95-d11373804a80 | note | 25m³ to 50m³ = 3 samples
0d76567b-b714-5074-a8e8-418bee8d16ef | note | 50m³ to 100m³ = 4 samples + 2 no. VPV cylinders.
8aac9d1b-5042-5370-9332-70bd0bb74efd | note | ○ For each additional 50m³ and additional sample shall be taken.
74204d9f-e3ea-5def-b4d3-42545fec471f | note | ○ Where IFC nominates minimum strength development, ensure strength is verified by additional cylinder or other approved method (such as maturity testing).
33b63dd9-7b96-5e0c-b7d1-5e9f2109c3c8 | note | ○ Each sample shall consist of 1 no. slump or spread test and 3 no. compressive strength cylinders minimum.
55d1ad91-3036-5da0-8c7d-361c119d8185 | note | ○ Compressive strength cylinders = 1 no. 7 day strength, 2 no. 28 day strength.
29126b71-0e24-58c7-abcb-52a336312028 | note | ○ Note: Additional cylinders may be required for other purposes such as early trafficking or removal of formwork.
dcbf40c2-a5aa-5e06-8e4b-32fa67a54c69 | note | ○ Record: Required information on the Concrete Pour Record.
b35645fc-e6d0-5ccc-bbdf-86086204d907 | note | Method - Test
2b41a383-d98f-580c-8fce-1742b64bc621 | note | Frequency - Each element
a42bfce1-5013-51a5-a3ee-e477b6e9b8da | note | Category - IP
1d2f62fc-7cb4-5053-b2c5-aa44b0e655a4 | note | Responsibility - Concrete Tester, Foreman, SE/PE/SPE
1bb6efa1-7924-598d-ab09-859ecb2890b9 | note | Verifying Documents - This ITP, Concrete Pour Record
4d0dbfe7-97a2-573b-a145-01b483469533 | date | Date Completed:
9559e10e-b276-4015-847d-da7873d70e61 | checkpoint | 5.11 - Concrete Testing - Slump
b46f4c60-4b4d-585e-b1ec-4f80257c7096 | note | Reference - 610.16 (c)
8e6824dc-2a92-5eab-938d-c9f57906e4b8 | note | Acceptance Criteria - Slump testing tolerances =
f66d58e3-bd99-5dde-8df7-bd61f0debbf8 | note | <60mm = ±10mm
ba16149e-d075-5f35-a8c2-f06485b46b13 | note | ≥60mm to ≤80mm = ±15mm
2cbfa670-7b83-58a8-839d-e2b453a53464 | note | >80mm to ≤110mm = ±20mm
1eaa2a05-7eb9-5669-aae7-ac288054b88f | note | >110mm to ≤150mm = ±30mm
e25fdbb9-6a48-505d-8d8a-45c34b2ea59a | note | >150mm = ±40mm
c236f296-2b44-56d9-8086-146386ea4ee5 | note | ○ Record: Required information on the Concrete Pour Record.
cfadf853-c5f7-5084-95ef-e0636839fad9 | note | Method - Test
68199877-9d85-58b0-89a8-4aad2b73c59c | note | Frequency - Each sample of Standard or Superplasticised Concrete
9fd65426-deea-5fd4-bcec-85b86b49f450 | note | Category - IP
dc45a41c-eb65-5636-851d-179ea56c5b3d | note | Responsibility - Concrete Tester
979b8b0b-33bb-5724-ac45-52bdf02e8a5a | note | Verifying Documents - This ITP, Concrete Pour Record
d411c1ed-81d3-5452-b4c9-496915b0e285 | date | Date Completed:
6da39d2c-9ec7-442b-b5e9-463ae995f5c6 | checkpoint | 5.12 - Concrete Testing - Spread, Passability & Viscosity
e77d90e3-5915-5991-ae78-cbc944a2128d | note | Reference - 610.13 (b)
78bb568a-2e61-535d-8257-29b980edaefd | note | Acceptance Criteria - Spread range = 550mm to 750mm
b457c5e0-e04e-5ddc-b021-127f4ba46e78 | note | ○ T500 = 2 seconds to 5 seconds (to reach a spread of 500mm)
6e72e782-f175-525c-9e4f-c81368200c4c | note | ○ Passability = ≤10mm (aggregate height differential)
394fee64-1661-5bb7-8ce0-0cc5e5ec3d24 | note | ○ Record: Required information on the Concrete Pour Record.
4c0e2c93-997c-52ab-b23c-5926c9226e35 | note | Method - Test
ae4902e5-09ce-56bd-b785-aae8ecdf76d1 | note | Frequency - Each sample of Self-compacting Concrete
d2cc3575-3aac-5492-acf3-92558b8d0a37 | note | Category - IP
c9bbe73b-dce3-513b-b6cf-b8876789c4ae | note | Responsibility - Concrete Tester
60de4fbb-6cf2-58c6-a272-0889a907a8d8 | note | Verifying Documents - This ITP, Concrete Pour Record
a01d5bad-cbc8-5d22-adfc-99efe65b3af6 | date | Date Completed:
c0b0ba98-9be1-458b-8306-5f87458a4813 | checkpoint | 5.13 - Concrete Testing - Compressive Strength Cylinders
5094753c-2bd7-54cc-b229-33144bfefaa8 | note | Reference - Site Sampling & Testing Procedure
37429e4b-f3bb-5907-a1e9-80eee92b585a | note | Acceptance Criteria - Correct quantity of cylinders manufactured per sample.
04c96c7e-b135-5e8c-9161-72d3872f2ef8 | note | ○ Record: Required information on the Concrete Pour Record.
5e0d3ee4-fc27-5fad-ab72-d07b6349129f | note | Method - Test
b92cf832-398f-5e5e-a70c-ec56e39ad783 | note | Frequency - Each sample
668c55a7-01c7-54aa-a0bc-29b96554d0f8 | note | Category - IP
b41fce5f-2da5-5b2a-9d85-5bd1f217bfeb | note | Responsibility - Concrete Tester
db68f3f2-bc01-5e6f-9cb8-ac932a4b2036 | note | Verifying Documents - This ITP
844bc600-dfa4-5e53-b4cb-29004f99477c | date | Date Completed:
2fbc01dd-e104-41f2-a64e-8d13dfe24ff1 | checkpoint | 5.14 - Supply & Discharge Rates
3852c263-71d9-5225-a6b3-4bd9768ad723 | note | Reference - 610.13 (a) & (f)
3d0287a3-7627-5067-9358-82d4e0458c69 | note | Acceptance Criteria - Concrete is supplied at an adequate rate to ensure no cold joints are formed.
11355979-e9d5-56cc-8df1-488ed01742b6 | note | ○ No water is to be added once discharge commences.
cc8c997e-6589-5b5a-b81e-5b1fc10916d0 | note | ○ Maximum time between batching trucks is 25 minutes.
cba0dca8-0b5e-598f-8be2-0515b41a6155 | note | ○ Maximum elapsed time for discharge (including compaction) is 60 minutes from batching unless the mix design has an extension using set retardants.
3708679f-9bd8-5824-b67b-65d170f656ee | note | ○ Concrete that stiffens or is showing signs of stiffening shall not be used.
85927518-c4f0-5e86-8fa2-d776e62273b6 | note | ○ Record: Required information on the Concrete Pour Record.
fa3997f3-f5dd-5dbf-b38b-b601c8f82727 | note | Method - Measure, Visual
da8dec8e-9396-5ac0-8527-0898e10b9d31 | note | Frequency - Each load
22d3d728-7d5a-55b4-b351-da142f57d946 | note | Category - IP
a16a4b9b-3f10-504c-a640-6011a2fa7bd9 | note | Responsibility - Foreman, SE/PE/SPE
4c05bca6-3df7-52b3-9cb4-5c7610253d60 | note | Verifying Documents - This ITP, Concrete Pour Record
72a4c8fe-382d-5319-89ee-aaeaf0c70399 | date | Date Completed:
a44587c9-63ba-42bb-81cb-d052af888678 | checkpoint | 5.15 - Placement & Compaction
8e170c90-0c0b-5e39-ad15-ce70fb6ae809 | note | Reference - Placement & Compaction Work Procedure 610.18 (a) & (b), 610.18 (d) (i)
8172a223-bb05-5821-9077-f4e4fcdee132 | note | Acceptance Criteria - All concrete batches are traceable.
ddf759fc-5904-5839-9309-8574e5fa0dad | note | ○ Where concrete pumps are used, the initial discharge is pumped to waste until a consistent workable mix is discharged.
04e42bdc-e27b-54e3-8ee0-0ef5a11421a9 | note | ○ Concrete is not dropped freely from a height exceeding 2m.
d6278100-e3eb-57a2-bf76-cb4e5246cc50 | note | ○ Concrete is not moved horizontally by use of vibrators.
1762b2f1-fb48-554f-8d7e-a376931dc79d | note | ○ Adequate compaction is ensured
edac2ff5-2e26-5de9-a173-8186b9afbc39 | note | ○ Care has been taken to fill every part of the form and force concrete under and around reinforcement and embedments.
ba47821b-9ba4-519a-8bfb-3e41ab181c56 | note | ○ Concrete layers are not more than 350mm
3e45272d-50c3-5190-8c6a-2cbcca0c8715 | note | ○ Internal vibrators are inserted at spacing not exceeding the manufacturer's zone of influence.
d679ecd2-918b-51c4-8ecf-754e8efbd31f | note | ○ Vibration continued at each point until air bubbles cease to emerge from the concrete.
69e9182d-6063-58d2-8521-9eccb4b800fb | note | ○ Record: Required information on the Concrete Pour Record.
556cb067-c8e4-5d22-b881-c44b382db878 | note | ○ Attach: Concrete Pour Record
5cf3c8ef-89f8-5ede-8129-a6be6268073d | note | ○ Attach: Concrete Dockets
50e2c511-e07e-5e5b-930b-60b487121ada | note | Method - Visual
6cf0d68b-2864-5538-9352-4d84a688f7b2 | note | Frequency - Each load
8200626e-fea4-527d-b1f3-9459416e90a1 | note | Category - SP
b44fa808-bf59-5786-813f-d43c68c31ce2 | note | Responsibility - Foreman, SE/PE/SPE
b449eb35-36e1-57db-bffd-38258f2d445d | note | Verifying Documents - This ITP, Concrete Pour Record
813173f5-55bf-5834-960e-e9479b4919c0 | date | Date Completed:
d5832b38-e2b4-4cfa-b26a-eb939dcab40e | checkpoint | 5.16 - Surface Finishes
d4ed880a-2234-5eac-84b8-d1076c0fb5ef | note | Reference - IFC Drawings 610.31, 610.20
59bdef61-0bc1-51c2-bbf0-1225d7c2c960 | note | Acceptance Criteria - Surface finish as per IFC drawings.
084f865e-f092-532f-a8a5-0f933c2d0816 | note | ○ Where surface finish is not detailed, the VicRoads class finishes will apply as per 610.31.
14736c09-7fe1-518f-8c32-4184ae2017a0 | note | ○ Construction joints shall be roughened in locations shown on the drawings - any proposed changes to construction joints shall be subject to approval from the Nominated Authority.
30d7c1bb-18e3-5be2-adbc-2e4da3c9ee01 | note | Method - Visual
d14ec8d8-16fd-584f-a4d3-3d042a741848 | note | Frequency - Each element
d95a3535-2817-505e-9cda-a5aa036844d7 | note | Category - IP
e57a0f71-93d0-5546-b296-d1767ae00396 | note | Responsibility - Foreman, SE/PE/SPE
69d89c36-561d-5767-82e7-f8cdf1ff3430 | note | Verifying Documents - This ITP
bf5f2b16-7b37-50df-b907-f9d5e7dbd2f7 | date | Date Completed:
4ba0ffbd-5f9f-4441-99c1-5063544de380 | checkpoint | 5.17 - Curing-Top Surface
7f309a94-d297-5a2b-8bcd-a0ee71440a0d | note | Reference - IFC Drawings
1ff55efb-27b1-534a-a31e-581e90ae7534 | note | Acceptance Criteria - Top surface of the pier and abutment walls shall be water ponded for at least 72 hours following initial set. Alternatively the top surface of the pier and abutment walls may be covered with thermal blankets for at least 72 hours and then treated with a curing compound.
15f77de9-1019-5c56-8d6e-dfc79e3df348 | note | Method - Visual
3385b4be-f468-5a0d-bc9d-8b52d6e8efa2 | note | Frequency - Each element
0f3221c7-b73a-593f-8980-77164c4fe554 | note | Category - IP
f3860a49-13e7-5627-ad11-9152497ea0d9 | note | Responsibility - Foreman, SE/PE/SPE
2a737e81-14a0-5bb3-b152-25177b416377 | note | Verifying Documents - This ITP
5eeb84c3-1b73-597e-9049-861f0baea448 | date | Date Completed:
d97fd515-4462-4157-abad-2878600e62bd | checkpoint | 5.18 - Curing after formwork removal
5c479828-d853-5eec-8dac-1d50f2b8e8d1 | note | Reference - IFC Drawings
8f1b0721-32bf-573e-91f8-c15f589a8f54 | note | Acceptance Criteria - After formwork removal, seal curing shall be applied to all exposed concrete surfaces to achieve overall of 7 days equivalent wet curing
dddb9c0f-c28e-565f-8cc2-a1d22fc7d2d2 | note | Method - Visual
81288d08-f284-5c62-8daa-bb3d1fad1251 | note | Frequency - Each element
28209dba-01df-5b2e-be28-88e98b52d9a1 | note | Category - IP
14f93049-fbe4-5635-9302-3f25be208305 | note | Responsibility - SE
8fecfe20-17c9-545b-a416-ee66a2d396d4 | note | Verifying Documents - Thip ITP
742e1670-cadb-5987-8a8d-912b2bc8ed67 | date | Date Completed:
e6bd0030-d2f8-4820-86bb-e27a65728328 | section | 6. Post-construction Activities
8f98ed3e-5745-47da-ae65-7b0b746721b0 | checkpoint | 6.1 - Thermal Differential Monitoring
1d9f3d8a-f6f6-57dd-9e37-20983a7d01d9 | note | Reference - 610.22
5ba73444-f00c-5e5c-8449-c75a3981ad2b | note | Acceptance Criteria - Maximum thermal differential between the core and exposed surface not to exceed 20°C.
2259d541-311d-539d-8a1e-05a1dd1e49e2 | note | ○ Only applicable if the element has:
7beef71d-12ac-546f-99fa-65717a165a9b | note | i. the smallest sectional dimension exceeding 500mm
697444f3-660e-5dfe-a008-a2218c0723f1 | note | ii. one or more faces being restrained by previously hardened concrete or other external constraints.
390e52d2-a74f-5cde-9e5d-9eeed22d50b3 | note | ○ Attach: Thermal Monitoring Report
41eda216-b2c1-5e74-a161-b16977d14850 | note | Method - Document Review
15873c77-0e42-578e-a158-898177a4b737 | note | Frequency - Where applicable, each element
0acfd335-d864-58f8-a0db-47993fa18595 | note | Category - IP
f356d62d-f879-559a-bf96-89777ba04430 | note | Responsibility - Foreman, SE/PE/SPE
426686e2-5f75-5b33-b903-853634974734 | note | Verifying Documents - This ITP
02c9099f-df72-53ea-9ff3-476e1ce5eb34 | date | Date Completed:
8c60db46-cc98-4334-ae4e-c97ba157f582 | checkpoint | 6.2 - Early Age Compressive Strength Test Results - Removal of Formwork
81e99f2e-7730-5574-a19e-40dc5689f1d5 | note | Reference - IFC Drawings
c3ecaf6d-c9d6-5fd1-8f48-20b8088d3749 | note | Acceptance Criteria - Formwork shall be removed not earlier than 72 hours. Formwork shall not be removed when the ambient temprature is less than 10 degrees
b11057af-e6a5-5467-8081-f69ecb965fa2 | note | ○ Where IFC nominates minimum strength development, ensure strength is verified by additional cylinder or other approved method (such as maturity testing).
7bc47686-676c-5eac-a93c-36c0ecfc5922 | note | Method - Document Review
fdad2ae4-9c0d-5916-a312-0307dfe2e308 | note | Frequency - Where applicable, each element
4af9be77-f5e1-5625-83b7-e501218586bc | note | Category - IP
12404fd5-fbe3-5ff6-af84-a64d89f633fc | note | Responsibility - Foreman, SE/PE/SPE
932724c3-8f28-5ec1-86fa-96f1dd2a92c8 | note | Verifying Documents - This ITP
92c8de18-f82e-5695-9087-c1d531d6af06 | date | Date Completed:
0e26af55-5e8d-4f9d-a1c9-7c0626602878 | checkpoint | 6.3 - Surface Inspection - Cracks
e815b952-7fea-5d81-a4e4-49a8dfd573e3 | note | Reference - 610.24
a3bee56f-2f8c-5ff4-8eb9-850e70ac1d29 | note | Acceptance Criteria - No cracks greater than 0.2mm (exposure classification B1)
5477e511-0470-5a7b-b9bf-ac6865ce25ec | note | ○ If cracking is observed follow Structural Concrete Crack Repair ITP for investigation and repair.
b36ca01e-e945-5041-8246-363c21d8f685 | note | Method - Visual, Measure
c3abb3b5-b5e8-5755-86da-95ab159679ec | note | Frequency - Each element
ca6be0ce-2d98-5ed1-b49a-a2a0bc8b8ab2 | note | Category - IP
2ed54390-f218-5839-b06e-ae1ac07bd2a7 | note | Responsibility - SE/PE/SPE
d0f1698c-1128-59c2-b464-8050ab9ac85a | note | Verifying Documents - This ITP
e46087bf-1fc2-51fe-8735-dd6080d58b85 | date | Date Completed:
8bcaa524-652e-4718-9dda-7135e2116d24 | checkpoint | 6.4 - Surface Inspection - Surface Finish
34242976-1788-50c1-8daa-d8ae112bba5b | note | Reference - IFC Drawings 610.31 (a) - (n), 610.32
3ed39506-2737-5df6-ae22-846b30e5130a | note | Acceptance Criteria - Comply with the IFC drawings and specifications.
ad5fa12c-5561-5ad5-8f99-258a1fbae25f | note | ○ Where surface finishes are non-conforming follow Structural Concrete Patch Repair ITP for investigation and repair.
2bea37d1-2153-591c-b6ec-ef4a7acf65a1 | note | Method - Visual
267f17e9-ebf4-5743-8970-39d19d21fffb | note | Frequency - Each element
30361bfb-550f-585c-a4ca-dc81a14bded4 | note | Category - IP
03d9db34-42b5-57ca-9ed9-6ce11ea85448 | note | Responsibility - SE/PE/SPE
c2bf484a-bd24-57d5-8fa5-152d7c3febfe | note | Verifying Documents - This ITP
181f5a90-9ed1-5c40-972a-3e89293dbf7b | date | Date Completed:
4c2f83c8-ac7e-4158-829d-4f4058229ed5 | checkpoint | 6.5 - Measurement of Concrete Cover
02213efb-099d-54c5-893c-fefe1e27cfd3 | note | Reference - 610.34
1633f8d0-e0f3-5aee-9df1-4948666730b3 | note | Acceptance Criteria - Concrete covermeter check one 3m² test area for every 25m² exterior surface area.
aedd8b8f-08b0-5f9d-a743-b3bcf14fc4e3 | note | ○ Minimum 10 no. measurements recorded in each area.
9cc27299-ddad-53d5-88f9-ea8c9aef7866 | note | ○ Where low cover is identified, an assessment to evaluate the influence on durability of the structure is submitted to the Nominated Authority.
d0234b76-3d84-540b-906b-2f4f50cc34c3 | note | ○ Attach: Covermeter Check Record
b59ee70b-4f64-5f59-a4fd-a9ff2a62b8a5 | note | Method - Measure
e6c22414-c8a2-5441-8ae9-3ea1feb58f73 | note | Frequency - Each element
0f33c597-83a6-5556-968f-3e9010f6fa37 | note | Category - IP
dc898187-edd7-5df9-a0cd-c12a7861bc7c | note | Responsibility - SE/PE/SPE
2e084dfc-6d95-5c7a-9f5c-38bbba55df2d | note | Verifying Documents - This ITP
a253a706-797f-5391-a367-22925a5b11cc | date | Date Completed:
a8dfaab1-ba8c-4671-a0cf-c5bc1296a7f6 | checkpoint | 6.6 - Early Age Compressive Strength Results - Placement of Fill Against Concrete
71912b10-06e5-5e92-aa91-60ff25e45d6e | note | Reference - Early Loading and Trafficking of Decks and Approach Slab Procedure 610.35
ba10c67e-6442-59c5-8f6c-4c35bf63e91b | note | Acceptance Criteria - Fill is not placed against concrete within 14 days of pour.
afb7f9f3-ab42-5e66-937a-dbc163c7c2d0 | note | ○ Proposed placement of fill prior to 14 days - follow the Early Loading and Trafficking of Decks and Approach Slabs Procedure.
5d5832e6-fe7e-58ea-a4ed-2a7ffd7a8f4a | note | ○ Attach: Concrete Test Results or Maturity Test Results
da27c7d9-0eb7-5336-8f3a-b0b9d66cd2cf | note | Method - Document Review
a20a29d9-e7c7-5dc5-bd87-6a679eaf3f10 | note | Frequency - Where applicable, each substructure element
801f12bf-25cf-5a74-a6c0-51447633de86 | note | Category - SP
66d8784c-0d95-576f-a95b-12ea36bacbd3 | note | Responsibility - Foreman, SE/PE/SPE
349f3f4f-4c7c-5de6-a55a-76f9e3259e37 | note | Verifying Documents - This ITP
ca0cdcfd-52d7-5689-a3d1-fdbdf242e82f | date | Date Completed:
92aa32c2-3b68-4989-ae2a-5c0dee1e3d0d | checkpoint | 6.7 - Compressive Strength Test Results
1a22bdd6-e623-5869-b42f-7cf5b0b311a7 | note | Reference - IFC Drawings Table 610.05.051, 610.16 (g)
51bdf8ad-7f06-5eb7-9b09-09eb9fb57d5b | note | Acceptance Criteria - 7 day compressive strength to comply with table 610.051 for early indication that the strength is tracking correctly.
321cbd41-5f7a-5ff0-9464-5650f855814d | note | ○ 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
c609fc5b-af67-55b7-b32e-042f79e38032 | note | ○ Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength.
99d064a6-3320-5adb-9d85-6b841ea1be41 | note | ○ Attach: Compressive Strength Test Results
0eb26967-c9a9-5b21-aa22-2a975d13c0d5 | note | Method - Document Review
7c9edcbd-6572-53b3-b872-1a3376092ce2 | note | Frequency - Each cylinder
08c6464b-1ea9-58f0-b4c3-939a70cff449 | note | Category - IP
64af92c9-331c-5a39-aa34-f68a1b9d90ad | note | Responsibility - SE/PE/SPE
cab1de28-f875-58d8-ab13-4aad7497d218 | note | Verifying Documents - This ITP
73867b47-26c5-5afb-881d-b02780446e85 | date | Date Completed:
a73f4d96-f294-492d-bd79-e364fdf66dd1 | checkpoint | 6.8 - As-built Survey
53fad8a5-4e6e-57a9-8a32-69ad3a9116e8 | note | Reference - IFC Drawings 610.47 Table 610.472
b3347fda-371a-542f-b891-34f5729ec34e | note | Acceptance Criteria - Provide record of dimensional measurements to demonstrate concrete members comply with tolerances as per the table 610.462 as applicable to the element.
5ac6ba29-171f-5116-a83a-a4622db97c79 | note | ○ Attach: Survey As-builts / Survey Report
930f977c-67dc-5819-b82e-eb41cf97f618 | note | Method - Document Review
d38d9863-f77e-5de4-bf69-82eeda551f24 | note | Frequency - Each element
2d7148f1-06f6-5bde-b3e1-7265a24447c7 | note | Category - IP
8be5947a-6f3e-57da-a173-80aa1866c76e | note | Responsibility - Surveyor, SE/PE/SPE
c71ec465-e7b3-55d6-a6e1-745f57d02685 | note | Verifying Documents - This ITP
fd08d09c-8fa0-53d0-96bf-9138d04c843d | date | Date Completed:
a2bb5c8c-bab4-4dc5-bf08-a4557623635a | checkpoint | 6.9 - Non-conformance Report (NCR) Closure
d779c4a0-622e-56f5-b189-d06dae6adf76 | note | Reference - MRPA Quality Management Plan
407b7acb-5057-58b0-ab6a-b93bcab622e5 | note | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
cadc2708-1327-5ca8-8f56-3ff5d90cef21 | note | Method - Document Review
c5636885-21a8-5599-a60f-31f1e65d26c7 | note | Frequency - Once, prior to closure of this lot / element / Work area
5ab2ac75-64e6-5cbf-bb4a-bea0a87447ab | note | Category - HP*
c2eda6d8-7d9a-5ab3-8e6f-c3c39ac2d8a9 | note | Responsibility - SE/PE/SPE
87e520ec-acc7-5b18-8028-018efeef1af5 | note | Verifying Documents - This ITP
b120c6b5-424a-58e9-ba30-0fb4550c0479 | date | Date Completed:
884e7b6a-6584-45c9-8432-1b9533b855c5 | checkpoint | Final Inspection
e71f5bcc-2316-5fc2-86a2-2552a9134b3e | note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed above have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
9a846e71-b567-5108-947b-82e7c84184fd | textbox | Name:
2c9bbd1a-dc59-5acc-bd5b-33ac9b2ecaff | textbox | Position:
20f9c857-221e-54e1-abb9-39fd31a9dcf2 | textbox | Date Completed:
a1efeb6a-0470-41d6-8690-f498fe263185 | signoff | Sign ITP