## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Wall Closure Checklist 2 Rough In [P] | [5 empty] | Wall Closure Checklist 2 Rough In [P]
section | Wall Closure Checklist 2 Rough In
checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule?
checkpoint | FCU installed at right height with 5% slope towards the drain point?
checkpoint | Thermostat control and zone control cabling has been installed and location is correct?
checkpoint | Drains have been run to Tundish and does not protrude wall framing?
checkpoint | Drains tested and witnessed by Boad Air?
checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
checkpoint | Refrigeration insulation is not damaged?
checkpoint | Pipe projecting the wall cavities in balconies have been sealed?
checkpoint | Refrigeration pipes run through cavity without being kinked or damaged?
checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
checklist | Ceiling Closure Checklist 2 Rough In [Q] | [5 empty] | Ceiling Closure Checklist 2 Rough In [Q]
section | Air Conditioning:
checkpoint | Air Conditioning
textbox | Inspection Date:
checkpoint | FCU’s are installed and other services are not impeding access to fan coil?
checkpoint | Wiring connected to indoor unit electrical box?
checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
checkpoint | All FCU flexible ducts connections to air terminals and spigots have been air tight by using duct tape?
checkpoint | All FCU flexible ducts installed and supported by intact load spreader?
checkpoint | All FCU flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties
checkpoint | Are the zone controllers installed correctly and easily accessible?
checkpoint | Are the zone motors wired correctly back to the zone controllers?
checkpoint | Zone motors are installed and connected with junction boxes?
checkpoint | Zone motors is side face?
checkpoint | Supply boxes are installed and supported at correct location in the middle of bulkhead height?
section | Ventilation:
checkpoint | Ventilation
textbox | Inspection Date:
checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
checkpoint | All ventilation flexible ducts connections to air terminals and spigots have been air tight by using duct tape?
checkpoint | All ventilation flexible ducts connections to air terminals and spigots have been secured by using fixing ties/cables ties?
checkpoint | All flex are installed and supported by intact load spreaders?
checkpoint | Flexible ducts on the right location and not jammed?
checkpoint | Butterfly dampers are installed and they are in a fully opened position and air tight sealed?
checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
section | Access Panel:
checkpoint | Access Panel
textbox | Inspection Date:
checkpoint | Access Panel location has been marked on floor as per RCP and has been checked?
checkpoint | All other other services do not impede access?
checklist | Duct Installation Checklist [C] | [5 empty] | Duct Installation Checklist [C]
section | Duct Installation Checklist
checkpoint | Are drawings on site the latest issue
checkpoint | Are plant and equipment location correct
checkpoint | Fan in the duct run has been installed
checkpoint | Model of the fan is correct as per latest Fan Schedule
checkpoint | Duct size and location correct
checkpoint | Material and gauge correct
checkpoint | Is correct support method being used - Risers are supported at each level.
checkpoint | Is correct jointing method being used
checkpoint | Are joints completed and cleated installed on flanges
checkpoint | Is correct joint sealant being used
checkpoint | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
checkpoint | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
checkpoint | Is adequate distance between attenuator and fans been maintained?
checkpoint | Are the attenuator splitters in the plane of the bend ?
checkpoint | Are transitions close to attenuators gradual?
checkpoint | Is a settling duct between volume control dampers and attenuators allowed?
checkpoint | Are fire dampers installed and break away joint complete
checkpoint | Are flexible ducts installed, supported and connected to spigot by approved mthod using duct tape on internal core and cable tie on outer core
checkpoint | Is ductwork insulation as per drawings
checkpoint | Is ductwork fire rating complete
checkpoint | Are all spigots installed and dampers fully open
checkpoint | Are all access panels for fire damper access installed and closed
checkpoint | Is ductwork installation complete
checklist | Wall Closure Checklist 1 Rough In [A] | [5 empty] | Wall Closure Checklist 1 Rough In [A]
section | Wall Closure Checklist 1 Rough In
checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule?
checkpoint | FCU installed at right height to ensure grille is centred into the bulkhead?
checkpoint | Thermostat control cabling has been installed?
checkpoint | Thermostat location is correct as per RCP?
checkpoint | Drains have been run to Tundish and does not protrude wall framing?
checkpoint | Drains tested and witnessed by Boad Air?
checkpoint | All wiring including interconection wiring and power from isolator to the condensers are roughed without defect?
checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height?
checkpoint | Refrigeration pipes run through cavity without being kinked or damaged?
checkpoint | Pipe projecting the wall cavities in balconies have been sealed?
checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed?
checklist | Ceiling Closure Checklist 1 Rough In [B] | [5 empty] | Ceiling Closure Checklist 1 Rough In [B]
section | Air Conditioning:
checkpoint | Air Conditioning
textbox | Inspection Date:
checkpoint | FCUs are installed and other services are not impeding access to fan coil?
checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access?
checkpoint | Wiring connected to indoor unit electrical box?
checkpoint | Condensate line has 2% fail towards the tundish and has support every 1m-1.5m?
checkpoint | Refrigeration lines supported by pipe clamps to avoid damage the insulation?
section | Ventilation:
checkpoint | Ventilation
textbox | Inspection Date:
checkpoint | Vent fans are installed with rubber isolation in the correct location as per drawing?
checkpoint | All flex are installed and supported by intact load spreaders?
checkpoint | All flexible ducts inner core and outer core have been mechanically secured & taped to spigots and air terminals by using duct tape & fixing ties?
checkpoint | Butterfly dampers are installed and they are in a fully opened position and air tight sealed?
checkpoint | PVC ducts have been hung at correct height and supported by hanging straps?
section | Access Panel:
checkpoint | Access Panel
textbox | Inspection Date:
checkpoint | Access Panel location has been marked on floor as per RCP and has been checked
checkpoint | All other other services do not impede access