## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-183-CIV-SSB-Conduits and Pits-MTM Carpark lighting
ITP Description: |  | Conduit and Pits- MTM Car Park Lighting
Discipline (e.g. CIV/STR/RAIL: |  | CIV
Revision Number: |  | 0
Revision Date: |  | 2023-11-13
ITP created by: |  | Romualdo Magpantay
ITP approved for use by: |  | Victor Mira
Special Notes to ConQA Team : |  | ITP for Station Street, Beaconsfield
Inspection & Test Plan - Conduit and Pit (Supply and Install) - MTM Car Park Lighting
[9 empty] | Revision: | 0
[9 empty] | Date: | 2024-07-16
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | L1-CHE-STD-035 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
1.3 | Non Dependent | AS /NZS 3000 | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A
2 | Preliminaries
2.1 | Obtain and review manufacturer documentations for the supply of materials ● LV + HV Conduits ● Communication Conduits ● Fixing and Supporting Materials ● Pits | IFC Drawing Supplier Specification AS /NZS 3000 | • Materials comply with relevant specifications. • Obtain conformance certificates and submit to the Nominated Authority prior inclusion into the works. | Visual | Once | HP | Nominated Authority | ConQA Hold Point Release
2.2 | Inspect supplied items upon delivery | IFC Drawing Supplier Specification AS /NZS 3000 | Supplied items are to correct spec, class, size and undamaged | Testing | Once | IP | Eelctricians Site /Project Engineer | This ITP
3 | Construction / Installation Activities
3.1 | Excavation of Conduit Trenches & Pits | AS/NZS 3000 clause 3.9 IFC Drawings | ● Install the conduits after earthworks have been completed to subgrade level. ● Installation of the conduits must be in accordance in the design dwgs. ● Where the conduits run beneath a road, provide a minimum cover of 500 mm from the top of the conduits to the underside of the pavement; in all other areas, provide a cover of 500 mm to finished surface level. | Inspection | Once | IP | Supervisor /PE/SPE | This ITP
3.2 | Sand bedding, laying and backfilling | AS/NZS 3000 clause 3.11.4.5 IFC Drawings | ●Use a min. 50mm compacted sand for bedding if not shown on the design drawings. ● Lay the conduit on a straight grade and line ●Compact backfill over the conduits to 100% relative compaction or depend on IFC drawing & pavement design requirements. | Inspection | Once | IP | Supervisor /PE/SPE | This ITP
3.3 | Install conduits according to manufacturer’s instructions, relevant drawings and Standards | AS/NZS 3000 clause 3.9 IFC Drawings | ● The works are constructed in accordance with AS/NZS 3000 Wiring Rules and Services and the installation Rules of AS 2067. ● Conduits are joined together with solvent cement, generally in accordance with clause 4.2 of AS/NZS 2032 and all joints are water tight and free of foreign matter ●Conduits are inline & positioned evenly ● Location of each conduit is as per Design Drawings | Inspection | Once | IP | Supervisor /PE/SPE | This ITP
3.4 | Installation of Electrical and Communication Pits | IFC Drawings L1-CHE-STD-035 section 12.6 | Compliance to IFC Drawings, Schedules & relevant specification: • Correct pit as per the IFC drawings • Soil underneath pit bedding is to be firmly packed prior to install • Bedding according to IFC drawings to be placed • Pit orientation is correct • Lids & covers to comply with technical specification | Inspection | Once | IP | Supervisor /PE/SPE | This ITP
3.5 | Marker Tapes | AS/NZS 3000 clause 3.11.4.5 IFC Drawings | Wiring systems installed underground shall be identified by an orange marker tape complying AS/NZS 2648.1. Positioned at approximately 50% of depth cover above wiring system or any additional mechanical protection provided that system. | Inspection | Once | IP | Supervisor /PE/SPE | This ITP
3.6 | Install draw-in rope to all electrical conduits(if applicable) | IFC Drawings QA & Work method of statement | Polypropylene draw-in rope consisting of one continuous length of not less than 4mm dia. in all electrical conduits or specify in methodolody | Inspection | Once, | IP | Supervisor /PE/SPE | This ITP
4 | Post Construction Activies
4.1 | As-built Survey (if required) | As Built Drawings Asset Change form | Survey activities undertaken to validate correct construction Attach: Surevy Report, Engineering Asset From | Survey Document Review | Per lot | IP | Supervisor /PE/SPE | This ITP
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /