## Calculations
Pressure Rebound Test Air Volume Assessment Calculations | [9 empty] | Paste Data in green cells below
[5 empty] | Report Headings |  |  |  |  | Serial Number | 809976
| Enter information in green cells |  |  |  | Date |  |  |  |  | Model | 30BARXP2I
| Blue cells calculate automatically |  |  |  | Contract |  |  |  |  | Units | kPa
[5 empty] | Location |  |  |  |  | Firmware Version | R0324 | Message Store | ------------
[5 empty] | Drain Layer |  |  |  |  | Run Index | 5
[5 empty] | Qualifications |  |  |  |  | Logging Type | Actual
[5 empty] | Site Engineer |  |  |  |  | Logging Interval | 10
[5 empty] | Client Rep |  |  |  |  | Start Time | 2022-06-15 11:53
Nominal Size (mm) |  |  |  |  | Ambient Air Temperature |  |  |  |  | Stop Time | 2022-06-15 15:09
Mean Bore (mm) |  |  |  |  | Water Temperature |  |  |  |  | Time | Reading
Tested Length (m) |  |  |  |  | Pressure Applied (kPa) |  |  |  | 0 | 0 | 527.8
V (L) | 0 | [7 empty] | 0.16667 | 10 | 527.8
e(m) | 0 | [7 empty] | 0.33333 | 20 | 527.8
Ew (kPax103) | [8 empty] | 0.5 | 30 | 524
Er (kPax103) |  | Water Meter Readings | [6 empty] | 0.66667 | 40 | 544.5
ΔP (kPa) |  | Before (m3) | [6 empty] | 0.83333 | 50 | 566.8
ΔVmax allowable (L) | #DIV/0! | After (m3) | [6 empty] | 1 | 60 | 574.2
ΔV (L) | 0 | ΔV (L) | 0 | [5 empty] | 1.1667 | 70 | 589.8
Acceptance | #DIV/0! | [7 empty] | 1.3333 | 80 | 628.1
[9 empty] | 1.5 | 90 | 645.1
[9 empty] | 1.6667 | 100 | 656.2
[9 empty] | 1.8333 | 110 | 676.1
[9 empty] | 2 | 120 | 695.3
EW - Bulk Modulus Water |  | ER - Pipe Material Modulus for PE 80B and PE 100 | [6 empty] | 2.1667 | 130 | 724.2
Temperature (°C) | Bulk Modulus (kPax103) | Temperature (°C) | PE 80B - E Modulus (kPax103) |  |  | PE 100 - E Modulus (kPax103) |  |  | 2.3333 | 140 | 747.4
5 | 2080 |  | 1h | 2h | 3h | 1h | 2h | 3h | 2.5 | 150 | 763.7
10 | 2110 | 5 | 740 | 700 | 680 | 990 | 930 | 900 | 2.6667 | 160 | 782.8
15 | 2140 | 10 | 670 | 630 | 610 | 900 | 850 | 820 | 2.8333 | 170 | 812.4
20 | 2170 | 15 | 600 | 570 | 550 | 820 | 780 | 750 | 3 | 180 | 832.8
25 | 2210 | 20 | 550 | 520 | 510 | 750 | 710 | 680 | 3.1667 | 190 | 860.8
30 | 2230 | 25 | 510 | 490 | 470 | 690 | 650 | 630 | 3.3333 | 200 | 885.9
|  | 30 | 470 | 450 | 430 | 640 | 610 | 600 | 3.5 | 210 | 916.7
[9 empty] | 3.6667 | 220 | 948.1
[9 empty] | 3.8333 | 230 | 973.3
[9 empty] | 4 | 240 | 1007.4
[9 empty] | 4.1667 | 250 | 1043.9
[9 empty] | 4.3333 | 260 | 1067.9
[9 empty] | 4.5 | 270 | 1104.1
[9 empty] | 4.6667 | 280 | 1140.1
[9 empty] | 4.8333 | 290 | 1170.3
[9 empty] | 5 | 300 | 1208.7
[9 empty] | 5.1667 | 310 | 1252.7
[9 empty] | 5.3333 | 320 | 1242.3
[9 empty] | 5.5 | 330 | 1231.4
[9 empty] | 5.6667 | 340 | 1223.7
[9 empty] | 5.8333 | 350 | 1217.7
[9 empty] | 6 | 360 | 1212.6
[9 empty] | 6.1667 | 370 | 1208.2
[9 empty] | 6.3333 | 380 | 1204.4
[9 empty] | 6.5 | 390 | 1201
[9 empty] | 6.6667 | 400 | 1197.8
[9 empty] | 6.8333 | 410 | 1194.9
[9 empty] | 7 | 420 | 1192.2
[9 empty] | 7.1667 | 430 | 1189.8
[9 empty] | 7.3333 | 440 | 1187.5
[9 empty] | 7.5 | 450 | 1185.3
[9 empty] | 7.6667 | 460 | 1183.2
[9 empty] | 7.8333 | 470 | 1181.2
[9 empty] | 8 | 480 | 1179.2
[9 empty] | 8.1667 | 490 | 1177.5
[9 empty] | 8.3333 | 500 | 1175.8
[9 empty] | 8.5 | 510 | 1173.5
[9 empty] | 8.6667 | 520 | 1172.3
[9 empty] | 8.8333 | 530 | 1170.1
[9 empty] | 9 | 540 | 1168
[9 empty] | 9.1667 | 550 | 1167.3
[9 empty] | 9.3333 | 560 | 1166.1
[9 empty] | 9.5 | 570 | 1164.8
[9 empty] | 9.6667 | 580 | 1163.3
[9 empty] | 9.8333 | 590 | 1161.9
[9 empty] | 10 | 600 | 1160.7
[9 empty] | 10.1667 | 610 | 1159.5
[9 empty] | 10.3333 | 620 | 1158.3
[9 empty] | 10.5 | 630 | 1157
[9 empty] | 10.6667 | 640 | 1155.8
[9 empty] | 10.8333 | 650 | 1154.6
[9 empty] | 11 | 660 | 1153.4
[9 empty] | 11.1667 | 670 | 1152.3
[9 empty] | 11.3333 | 680 | 1151.1
[9 empty] | 11.5 | 690 | 1149.9
[9 empty] | 11.6667 | 700 | 1148.8
[9 empty] | 11.8333 | 710 | 1147.6
[9 empty] | 12 | 720 | 1146.5
[9 empty] | 12.1667 | 730 | 1145.4
[9 empty] | 12.3333 | 740 | 1144.3
[9 empty] | 12.5 | 750 | 1143.2
[9 empty] | 12.6667 | 760 | 1142.2
[9 empty] | 12.8333 | 770 | 1141.2
[9 empty] | 13 | 780 | 1140.3
[9 empty] | 13.1667 | 790 | 1139.4
[9 empty] | 13.3333 | 800 | 1138.5
[9 empty] | 13.5 | 810 | 1137.5
[9 empty] | 13.6667 | 820 | 1136.7
[9 empty] | 13.8333 | 830 | 1135.9
[9 empty] | 14 | 840 | 1135.2
[9 empty] | 14.1667 | 850 | 1134.4
[9 empty] | 14.3333 | 860 | 1133.5
[9 empty] | 14.5 | 870 | 1132.8
[9 empty] | 14.6667 | 880 | 1132.1
[9 empty] | 14.8333 | 890 | 1131.3
[9 empty] | 15 | 900 | 1130.7
[9 empty] | 15.1667 | 910 | 1130.1
[9 empty] | 15.3333 | 920 | 1156.1
[9 empty] | 15.5 | 930 | 1167.3
[9 empty] | 15.6667 | 940 | 1218.5
[9 empty] | 15.8333 | 950 | 1247.2
[9 empty] | 16 | 960 | 1240.3
[9 empty] | 16.1667 | 970 | 1235.7
[9 empty] | 16.3333 | 980 | 1232.3
[9 empty] | 16.5 | 990 | 1229.5
[9 empty] | 16.6667 | 1000 | 1227
[9 empty] | 16.8333 | 1010 | 1224.9
[9 empty] | 17 | 1020 | 1223
[9 empty] | 17.1667 | 1030 | 1221.3
[9 empty] | 17.3333 | 1040 | 1219.7
[9 empty] | 17.5 | 1050 | 1218.3
[9 empty] | 17.6667 | 1060 | 1216.9
[9 empty] | 17.8333 | 1070 | 1215.6
[9 empty] | 18 | 1080 | 1214.4
[9 empty] | 18.1667 | 1090 | 1213.2
[9 empty] | 18.3333 | 1100 | 1212
[9 empty] | 18.5 | 1110 | 1210.9
[9 empty] | 18.6667 | 1120 | 1209.8
[9 empty] | 18.8333 | 1130 | 1208.7
[9 empty] | 19 | 1140 | 1207.7
[9 empty] | 19.1667 | 1150 | 1206.6
[9 empty] | 19.3333 | 1160 | 1205.6
[9 empty] | 19.5 | 1170 | 1204.6
[9 empty] | 19.6667 | 1180 | 1203.6
[9 empty] | 19.8333 | 1190 | 1202.7
[9 empty] | 20 | 1200 | 1201.8
[9 empty] | 20.1667 | 1210 | 1200.9
[9 empty] | 20.3333 | 1220 | 1200.1
[9 empty] | 20.5 | 1230 | 1199.2
[9 empty] | 20.6667 | 1240 | 1198.6
[9 empty] | 20.8333 | 1250 | 1197.8
[9 empty] | 21 | 1260 | 1197
[9 empty] | 21.1667 | 1270 | 1196.2
[9 empty] | 21.3333 | 1280 | 1195.6
[9 empty] | 21.5 | 1290 | 1194.9
[9 empty] | 21.6667 | 1300 | 1194.3
[9 empty] | 21.8333 | 1310 | 1193.6
[9 empty] | 22 | 1320 | 1193
[9 empty] | 22.1667 | 1330 | 1192.4
[9 empty] | 22.3333 | 1340 | 1191.8
[9 empty] | 22.5 | 1350 | 1191.2
[9 empty] | 22.6667 | 1360 | 1190.6
[9 empty] | 22.8333 | 1370 | 1190
[9 empty] | 23 | 1380 | 1189.4
[9 empty] | 23.1667 | 1390 | 1188.8
[9 empty] | 23.3333 | 1400 | 1188.3
[9 empty] | 23.5 | 1410 | 1187.7
[9 empty] | 23.6667 | 1420 | 1187.1
[9 empty] | 23.8333 | 1430 | 1186.5
[9 empty] | 24 | 1440 | 1186
[9 empty] | 24.1667 | 1450 | 1185.4
[9 empty] | 24.3333 | 1460 | 1184.9
[9 empty] | 24.5 | 1470 | 1184.3
[9 empty] | 24.6667 | 1480 | 1191.3
[9 empty] | 24.8333 | 1490 | 1253.2
[9 empty] | 25 | 1500 | 1256.5
[9 empty] | 25.1667 | 1510 | 1251.6
[9 empty] | 25.3333 | 1520 | 1248.3
[9 empty] | 25.5 | 1530 | 1245.8
[9 empty] | 25.6667 | 1540 | 1243.7
[9 empty] | 25.8333 | 1550 | 1241.8
[9 empty] | 26 | 1560 | 1240.2
[9 empty] | 26.1667 | 1570 | 1238.8
[9 empty] | 26.3333 | 1580 | 1237.5
[9 empty] | 26.5 | 1590 | 1236.3
[9 empty] | 26.6667 | 1600 | 1235.2
[9 empty] | 26.8333 | 1610 | 1234.1
[9 empty] | 27 | 1620 | 1233.1
[9 empty] | 27.1667 | 1630 | 1232.2
[9 empty] | 27.3333 | 1640 | 1231.3
[9 empty] | 27.5 | 1650 | 1230.5
[9 empty] | 27.6667 | 1660 | 1229.6
[9 empty] | 27.8333 | 1670 | 1228.8
[9 empty] | 28 | 1680 | 1228
[9 empty] | 28.1667 | 1690 | 1227.3
[9 empty] | 28.3333 | 1700 | 1226.5
[9 empty] | 28.5 | 1710 | 1225.8
[9 empty] | 28.6667 | 1720 | 1225
[9 empty] | 28.8333 | 1730 | 1224.3
[9 empty] | 29 | 1740 | 1223.7
[9 empty] | 29.1667 | 1750 | 1223.1
[9 empty] | 29.3333 | 1760 | 1222.4
[9 empty] | 29.5 | 1770 | 1221.7
[9 empty] | 29.6667 | 1780 | 1221.1
[9 empty] | 29.8333 | 1790 | 1220.4
[9 empty] | 30 | 1800 | 1219.8
[9 empty] | 30.1667 | 1810 | 1219.2
[9 empty] | 30.3333 | 1820 | 1218.6
[9 empty] | 30.5 | 1830 | 1218
[9 empty] | 30.6667 | 1840 | 1217.4
[9 empty] | 30.8333 | 1850 | 1216.8
[9 empty] | 31 | 1860 | 1216.2
[9 empty] | 31.1667 | 1870 | 1215.6
[9 empty] | 31.3333 | 1880 | 1215
[9 empty] | 31.5 | 1890 | 1214.4
[9 empty] | 31.6667 | 1900 | 1213.8
[9 empty] | 31.8333 | 1910 | 1213.1
[9 empty] | 32 | 1920 | 1212.5
[9 empty] | 32.1667 | 1930 | 1211.9
[9 empty] | 32.3333 | 1940 | 1211.3
[9 empty] | 32.5 | 1950 | 1210.7
[9 empty] | 32.6667 | 1960 | 1210.1
[9 empty] | 32.8333 | 1970 | 1209.5
[9 empty] | 33 | 1980 | 1208.9
[9 empty] | 33.1667 | 1990 | 1208.3
[9 empty] | 33.3333 | 2000 | 1207.7
[9 empty] | 33.5 | 2010 | 1207.1
[9 empty] | 33.6667 | 2020 | 1206.6
[9 empty] | 33.8333 | 2030 | 1206
[9 empty] | 34 | 2040 | 1205.4
[9 empty] | 34.1667 | 2050 | 1204.9
[9 empty] | 34.3333 | 2060 | 1204.3
[9 empty] | 34.5 | 2070 | 1225.8
[9 empty] | 34.6667 | 2080 | 1250.8
[9 empty] | 34.8333 | 2090 | 1246.8
[9 empty] | 35 | 2100 | 1244.3
[9 empty] | 35.1667 | 2110 | 1242.5
[9 empty] | 35.3333 | 2120 | 1241
[9 empty] | 35.5 | 2130 | 1239.7
[9 empty] | 35.6667 | 2140 | 1238.5
[9 empty] | 35.8333 | 2150 | 1237.5
[9 empty] | 36 | 2160 | 1236.7
[9 empty] | 36.1667 | 2170 | 1235.7
[9 empty] | 36.3333 | 2180 | 1234.9
[9 empty] | 36.5 | 2190 | 1234.1
[9 empty] | 36.6667 | 2200 | 1233.3
[9 empty] | 36.8333 | 2210 | 1232.6
[9 empty] | 37 | 2220 | 1231.8
[9 empty] | 37.1667 | 2230 | 1231.1
[9 empty] | 37.3333 | 2240 | 1230.5
[9 empty] | 37.5 | 2250 | 1229.8
[9 empty] | 37.6667 | 2260 | 1229.2
[9 empty] | 37.8333 | 2270 | 1228.6
[9 empty] | 38 | 2280 | 1228
[9 empty] | 38.1667 | 2290 | 1227.4
[9 empty] | 38.3333 | 2300 | 1226.8
[9 empty] | 38.5 | 2310 | 1226.3
[9 empty] | 38.6667 | 2320 | 1225.7
[9 empty] | 38.8333 | 2330 | 1225.1
[9 empty] | 39 | 2340 | 1224.5
[9 empty] | 39.1667 | 2350 | 1223.9
[9 empty] | 39.3333 | 2360 | 1223.4
[9 empty] | 39.5 | 2370 | 1222.8
[9 empty] | 39.6667 | 2380 | 1222.1
[9 empty] | 39.8333 | 2390 | 1221.5
[9 empty] | 40 | 2400 | 1220.9
[9 empty] | 40.1667 | 2410 | 1220.3
[9 empty] | 40.3333 | 2420 | 1219.7
[9 empty] | 40.5 | 2430 | 1219.1
[9 empty] | 40.6667 | 2440 | 1218.5
[9 empty] | 40.8333 | 2450 | 1217.9
[9 empty] | 41 | 2460 | 1217.2
[9 empty] | 41.1667 | 2470 | 1216.6
[9 empty] | 41.3333 | 2480 | 1216
[9 empty] | 41.5 | 2490 | 1215.4
[9 empty] | 41.6667 | 2500 | 1214.8
[9 empty] | 41.8333 | 2510 | 1214.2
[9 empty] | 42 | 2520 | 1213.6
[9 empty] | 42.1667 | 2530 | 1213.1
[9 empty] | 42.3333 | 2540 | 1212.5
[9 empty] | 42.5 | 2550 | 1211.9
[9 empty] | 42.6667 | 2560 | 1211.3
[9 empty] | 42.8333 | 2570 | 1210.7
[9 empty] | 43 | 2580 | 1210.2
[9 empty] | 43.1667 | 2590 | 1209.6
[9 empty] | 43.3333 | 2600 | 1209
[9 empty] | 43.5 | 2610 | 1208.5
[9 empty] | 43.6667 | 2620 | 1207.9
[9 empty] | 43.8333 | 2630 | 1207.3
[9 empty] | 44 | 2640 | 1206.9
[9 empty] | 44.1667 | 2650 | 1206.3
[9 empty] | 44.3333 | 2660 | 1205.7
[9 empty] | 44.5 | 2670 | 1205.2
[9 empty] | 44.6667 | 2680 | 1204.7
[9 empty] | 44.8333 | 2690 | 1204.1
[9 empty] | 45 | 2700 | 1203.6
[9 empty] | 45.1667 | 2710 | 1203.1
[9 empty] | 45.3333 | 2720 | 1202.6
[9 empty] | 45.5 | 2730 | 1202.1
[9 empty] | 45.6667 | 2740 | 1201.6
[9 empty] | 45.8333 | 2750 | 1201.1
[9 empty] | 46 | 2760 | 1200.6
[9 empty] | 46.1667 | 2770 | 1200.1
[9 empty] | 46.3333 | 2780 | 1199.6
[9 empty] | 46.5 | 2790 | 1199.2
[9 empty] | 46.6667 | 2800 | 1198.8
[9 empty] | 46.8333 | 2810 | 1198.3
[9 empty] | 47 | 2820 | 1197.9
[9 empty] | 47.1667 | 2830 | 1197.5
[9 empty] | 47.3333 | 2840 | 1197.1
[9 empty] | 47.5 | 2850 | 1196.7
[9 empty] | 47.6667 | 2860 | 1196.4
[9 empty] | 47.8333 | 2870 | 1196.1
[9 empty] | 48 | 2880 | 1195.8
[9 empty] | 48.1667 | 2890 | 1195.5
[9 empty] | 48.3333 | 2900 | 1195.2
[9 empty] | 48.5 | 2910 | 1194.9
[9 empty] | 48.6667 | 2920 | 1194.6
[9 empty] | 48.8333 | 2930 | 1194.3
[9 empty] | 49 | 2940 | 1194
[9 empty] | 49.1667 | 2950 | 1193.7
[9 empty] | 49.3333 | 2960 | 1193.4
[9 empty] | 49.5 | 2970 | 1193
[9 empty] | 49.6667 | 2980 | 1192.8
[9 empty] | 49.8333 | 2990 | 1192.4
[9 empty] | 50 | 3000 | 1192.1
[9 empty] | 50.1667 | 3010 | 1191.8
[9 empty] | 50.3333 | 3020 | 1191.5
[9 empty] | 50.5 | 3030 | 1191.2
[9 empty] | 50.6667 | 3040 | 1190.9
[9 empty] | 50.8333 | 3050 | 1190.7
[9 empty] | 51 | 3060 | 1190.5
[9 empty] | 51.1667 | 3070 | 1190.3
[9 empty] | 51.3333 | 3080 | 1190.1
[9 empty] | 51.5 | 3090 | 1189.9
[9 empty] | 51.6667 | 3100 | 1189.7
[9 empty] | 51.8333 | 3110 | 1189.5
[9 empty] | 52 | 3120 | 1189.3
[9 empty] | 52.1667 | 3130 | 1189.2
[9 empty] | 52.3333 | 3140 | 1189
[9 empty] | 52.5 | 3150 | 1188.8
[9 empty] | 52.6667 | 3160 | 1188.6
[9 empty] | 52.8333 | 3170 | 1188.4
[9 empty] | 53 | 3180 | 1188.2
[9 empty] | 53.1667 | 3190 | 1188
[9 empty] | 53.3333 | 3200 | 1187.8
[9 empty] | 53.5 | 3210 | 1187.6
[9 empty] | 53.6667 | 3220 | 1187.4
[9 empty] | 53.8333 | 3230 | 1187.1
[9 empty] | 54 | 3240 | 1186.9
[9 empty] | 54.1667 | 3250 | 1186.6
[9 empty] | 54.3333 | 3260 | 1186.3
[9 empty] | 54.5 | 3270 | 1186
[9 empty] | 54.6667 | 3280 | 1185.8
[9 empty] | 54.8333 | 3290 | 1185.6
[9 empty] | 55 | 3300 | 1185.2
[9 empty] | 55.1667 | 3310 | 1184.9
[9 empty] | 55.3333 | 3320 | 1184.6
[9 empty] | 55.5 | 3330 | 1184.2
[9 empty] | 55.6667 | 3340 | 1183.9
[9 empty] | 55.8333 | 3350 | 1183.6
[9 empty] | 56 | 3360 | 1183.2
[9 empty] | 56.1667 | 3370 | 1182.8
[9 empty] | 56.3333 | 3380 | 1182.3
[9 empty] | 56.5 | 3390 | 1181.9
[9 empty] | 56.6667 | 3400 | 1181.5
[9 empty] | 56.8333 | 3410 | 1181.1
[9 empty] | 57 | 3420 | 1180.7
[9 empty] | 57.1667 | 3430 | 1180.3
[9 empty] | 57.3333 | 3440 | 1179.9
[9 empty] | 57.5 | 3450 | 1179.4
[9 empty] | 57.6667 | 3460 | 1179.1
[9 empty] | 57.8333 | 3470 | 1178.7
[9 empty] | 58 | 3480 | 1178.3
[9 empty] | 58.1667 | 3490 | 1178
[9 empty] | 58.3333 | 3500 | 1177.6
[9 empty] | 58.5 | 3510 | 1177.3
[9 empty] | 58.6667 | 3520 | 1177
[9 empty] | 58.8333 | 3530 | 1176.7
[9 empty] | 59 | 3540 | 1176.4
[9 empty] | 59.1667 | 3550 | 1176.1
[9 empty] | 59.3333 | 3560 | 1175.8
[9 empty] | 59.5 | 3570 | 1175.5
[9 empty] | 59.6667 | 3580 | 1175.3
[9 empty] | 59.8333 | 3590 | 1175
[9 empty] | 60 | 3600 | 1174.7
[9 empty] | 60.1667 | 3610 | 1174.5
[9 empty] | 60.3333 | 3620 | 1174.2
[9 empty] | 60.5 | 3630 | 1173.9
[9 empty] | 60.6667 | 3640 | 1173.7
[9 empty] | 60.8333 | 3650 | 1173.4
[9 empty] | 61 | 3660 | 1173.2
[9 empty] | 61.1667 | 3670 | 1172.9
[9 empty] | 61.3333 | 3680 | 1172.7
[9 empty] | 61.5 | 3690 | 1172.4
[9 empty] | 61.6667 | 3700 | 1172.1
[9 empty] | 61.8333 | 3710 | 1171.8
[9 empty] | 62 | 3720 | 1171.5
[9 empty] | 62.1667 | 3730 | 1171.2
[9 empty] | 62.3333 | 3740 | 1170.9
[9 empty] | 62.5 | 3750 | 1170.6
[9 empty] | 62.6667 | 3760 | 1170.3
[9 empty] | 62.8333 | 3770 | 1170
[9 empty] | 63 | 3780 | 1169.7
[9 empty] | 63.1667 | 3790 | 1169.4
[9 empty] | 63.3333 | 3800 | 1169.1
[9 empty] | 63.5 | 3810 | 1168.7
[9 empty] | 63.6667 | 3820 | 1168.3
[9 empty] | 63.8333 | 3830 | 1168
[9 empty] | 64 | 3840 | 1167.6
[9 empty] | 64.1667 | 3850 | 1167.3
[9 empty] | 64.3333 | 3860 | 1166.9
[9 empty] | 64.5 | 3870 | 1166.6
[9 empty] | 64.6667 | 3880 | 1166.2
[9 empty] | 64.8333 | 3890 | 1165.9
[9 empty] | 65 | 3900 | 1165.5
[9 empty] | 65.1667 | 3910 | 1165.1
[9 empty] | 65.3333 | 3920 | 1164.8
[9 empty] | 65.5 | 3930 | 1164.4
[9 empty] | 65.6667 | 3940 | 1164.1
[9 empty] | 65.8333 | 3950 | 1163.7
[9 empty] | 66 | 3960 | 1163.4
[9 empty] | 66.1667 | 3970 | 1163.1
[9 empty] | 66.3333 | 3980 | 1162.8
[9 empty] | 66.5 | 3990 | 1162.4
[9 empty] | 66.6667 | 4000 | 1162.1
[9 empty] | 66.8333 | 4010 | 1161.8
[9 empty] | 67 | 4020 | 1161.5
[9 empty] | 67.1667 | 4030 | 1161.3
[9 empty] | 67.3333 | 4040 | 1161
[9 empty] | 67.5 | 4050 | 1160.7
[9 empty] | 67.6667 | 4060 | 1160.5
[9 empty] | 67.8333 | 4070 | 1160.3
[9 empty] | 68 | 4080 | 1160
[9 empty] | 68.1667 | 4090 | 1159.8
[9 empty] | 68.3333 | 4100 | 1159.6
[9 empty] | 68.5 | 4110 | 1159.3
[9 empty] | 68.6667 | 4120 | 1159
[9 empty] | 68.8333 | 4130 | 1158.8
[9 empty] | 69 | 4140 | 1158.6
[9 empty] | 69.1667 | 4150 | 1158.3
[9 empty] | 69.3333 | 4160 | 1158.1
[9 empty] | 69.5 | 4170 | 1157.8
[9 empty] | 69.6667 | 4180 | 1157.6
[9 empty] | 69.8333 | 4190 | 1157.4
[9 empty] | 70 | 4200 | 1157.2
[9 empty] | 70.1667 | 4210 | 1156.9
[9 empty] | 70.3333 | 4220 | 1156.7
[9 empty] | 70.5 | 4230 | 1156.5
[9 empty] | 70.6667 | 4240 | 1156.2
[9 empty] | 70.8333 | 4250 | 1156
[9 empty] | 71 | 4260 | 1155.8
[9 empty] | 71.1667 | 4270 | 1155.6
[9 empty] | 71.3333 | 4280 | 1155.4
[9 empty] | 71.5 | 4290 | 1155.2
[9 empty] | 71.6667 | 4300 | 1155
[9 empty] | 71.8333 | 4310 | 1154.8
[9 empty] | 72 | 4320 | 1154.6
[9 empty] | 72.1667 | 4330 | 1154.5
[9 empty] | 72.3333 | 4340 | 1154.3
[9 empty] | 72.5 | 4350 | 1154.2
[9 empty] | 72.6667 | 4360 | 1154
[9 empty] | 72.8333 | 4370 | 1153.9
[9 empty] | 73 | 4380 | 1153.7
[9 empty] | 73.1667 | 4390 | 1153.6
[9 empty] | 73.3333 | 4400 | 1153.5
[9 empty] | 73.5 | 4410 | 1153.4
[9 empty] | 73.6667 | 4420 | 1153.3
[9 empty] | 73.8333 | 4430 | 1153.2
[9 empty] | 74 | 4440 | 1153
[9 empty] | 74.1667 | 4450 | 1152.9
[9 empty] | 74.3333 | 4460 | 1152.8
[9 empty] | 74.5 | 4470 | 1152.7
[9 empty] | 74.6667 | 4480 | 1152.5
[9 empty] | 74.8333 | 4490 | 1152.4
[9 empty] | 75 | 4500 | 1152.2
[9 empty] | 75.1667 | 4510 | 1152.1
[9 empty] | 75.3333 | 4520 | 1152
[9 empty] | 75.5 | 4530 | 1151.8
[9 empty] | 75.6667 | 4540 | 1151.7
[9 empty] | 75.8333 | 4550 | 1151.6
[9 empty] | 76 | 4560 | 1151.4
[9 empty] | 76.1667 | 4570 | 1151.3
[9 empty] | 76.3333 | 4580 | 1151.1
[9 empty] | 76.5 | 4590 | 1150.9
[9 empty] | 76.6667 | 4600 | 1150.8
[9 empty] | 76.8333 | 4610 | 1150.7
[9 empty] | 77 | 4620 | 1150.5
[9 empty] | 77.1667 | 4630 | 1150.3
[9 empty] | 77.3333 | 4640 | 1150.2
[9 empty] | 77.5 | 4650 | 1150
[9 empty] | 77.6667 | 4660 | 1149.8
[9 empty] | 77.8333 | 4670 | 1149.7
[9 empty] | 78 | 4680 | 1149.5
[9 empty] | 78.1667 | 4690 | 1149.3
[9 empty] | 78.3333 | 4700 | 1149.1
[9 empty] | 78.5 | 4710 | 1149
[9 empty] | 78.6667 | 4720 | 1148.7
[9 empty] | 78.8333 | 4730 | 1148.6
[9 empty] | 79 | 4740 | 1148.4
[9 empty] | 79.1667 | 4750 | 1148.2
[9 empty] | 79.3333 | 4760 | 1148
[9 empty] | 79.5 | 4770 | 1147.9
[9 empty] | 79.6667 | 4780 | 1147.7
[9 empty] | 79.8333 | 4790 | 1147.5
[9 empty] | 80 | 4800 | 1147.3
[9 empty] | 80.1667 | 4810 | 1147.1
[9 empty] | 80.3333 | 4820 | 1146.9
[9 empty] | 80.5 | 4830 | 1146.7
[9 empty] | 80.6667 | 4840 | 1146.5
[9 empty] | 80.8333 | 4850 | 1146.3
[9 empty] | 81 | 4860 | 1146.1
[9 empty] | 81.1667 | 4870 | 1145.9
[9 empty] | 81.3333 | 4880 | 1145.7
[9 empty] | 81.5 | 4890 | 1145.4
[9 empty] | 81.6667 | 4900 | 1145.2
[9 empty] | 81.8333 | 4910 | 1145
[9 empty] | 82 | 4920 | 1144.7
[9 empty] | 82.1667 | 4930 | 1144.5
[9 empty] | 82.3333 | 4940 | 1144.2
[9 empty] | 82.5 | 4950 | 1144
[9 empty] | 82.6667 | 4960 | 1143.7
[9 empty] | 82.8333 | 4970 | 1143.5
[9 empty] | 83 | 4980 | 1143.2
[9 empty] | 83.1667 | 4990 | 1143
[9 empty] | 83.3333 | 5000 | 1142.8
[9 empty] | 83.5 | 5010 | 1142.6
[9 empty] | 83.6667 | 5020 | 1142.3
[9 empty] | 83.8333 | 5030 | 1142.1
[9 empty] | 84 | 5040 | 1141.9
[9 empty] | 84.1667 | 5050 | 1141.7
[9 empty] | 84.3333 | 5060 | 1141.5
[9 empty] | 84.5 | 5070 | 1141.3
[9 empty] | 84.6667 | 5080 | 1141.1
[9 empty] | 84.8333 | 5090 | 1140.9
[9 empty] | 85 | 5100 | 1140.7
[9 empty] | 85.1667 | 5110 | 1140.5
[9 empty] | 85.3333 | 5120 | 1140.4
[9 empty] | 85.5 | 5130 | 1140.2
[9 empty] | 85.6667 | 5140 | 1140
[9 empty] | 85.8333 | 5150 | 1139.9
[9 empty] | 86 | 5160 | 1139.7
[9 empty] | 86.1667 | 5170 | 1139.6
[9 empty] | 86.3333 | 5180 | 1139.4
[9 empty] | 86.5 | 5190 | 1139.3
[9 empty] | 86.6667 | 5200 | 1139.1
[9 empty] | 86.8333 | 5210 | 1138.9
[9 empty] | 87 | 5220 | 1138.7
[9 empty] | 87.1667 | 5230 | 1138.6
[9 empty] | 87.3333 | 5240 | 1138.4
[9 empty] | 87.5 | 5250 | 1138.2
[9 empty] | 87.6667 | 5260 | 1138
[9 empty] | 87.8333 | 5270 | 1137.8
[9 empty] | 88 | 5280 | 1137.7
[9 empty] | 88.1667 | 5290 | 1137.5
[9 empty] | 88.3333 | 5300 | 1137.4
[9 empty] | 88.5 | 5310 | 1137.2
[9 empty] | 88.6667 | 5320 | 1137
[9 empty] | 88.8333 | 5330 | 1136.8
[9 empty] | 89 | 5340 | 1136.7
[9 empty] | 89.1667 | 5350 | 1136.6
[9 empty] | 89.3333 | 5360 | 1136.4
[9 empty] | 89.5 | 5370 | 1136.3
[9 empty] | 89.6667 | 5380 | 1136.1
[9 empty] | 89.8333 | 5390 | 1136
[9 empty] | 90 | 5400 | 1135.8
[9 empty] | 90.1667 | 5410 | 1135.7
[9 empty] | 90.3333 | 5420 | 1135.5
[9 empty] | 90.5 | 5430 | 1135.3
[9 empty] | 90.6667 | 5440 | 1135.1
[9 empty] | 90.8333 | 5450 | 1134.9
[9 empty] | 91 | 5460 | 1134.7
[9 empty] | 91.1667 | 5470 | 1134.5
[9 empty] | 91.3333 | 5480 | 1134.3
[9 empty] | 91.5 | 5490 | 1134.1
[9 empty] | 91.6667 | 5500 | 1133.9
[9 empty] | 91.8333 | 5510 | 1133.7
[9 empty] | 92 | 5520 | 1133.6
[9 empty] | 92.1667 | 5530 | 1133.3
[9 empty] | 92.3333 | 5540 | 1133.2
[9 empty] | 92.5 | 5550 | 1133
[9 empty] | 92.6667 | 5560 | 1132.8
[9 empty] | 92.8333 | 5570 | 1132.7
[9 empty] | 93 | 5580 | 1132.5
[9 empty] | 93.1667 | 5590 | 1132.3
[9 empty] | 93.3333 | 5600 | 1132.2
[9 empty] | 93.5 | 5610 | 1132
[9 empty] | 93.6667 | 5620 | 1131.8
[9 empty] | 93.8333 | 5630 | 1131.6
[9 empty] | 94 | 5640 | 1131.5
[9 empty] | 94.1667 | 5650 | 1131.3
[9 empty] | 94.3333 | 5660 | 1131.2
[9 empty] | 94.5 | 5670 | 1131
[9 empty] | 94.6667 | 5680 | 1131
[9 empty] | 94.8333 | 5690 | 986.5
[9 empty] | 95 | 5700 | 992.5
[9 empty] | 95.1667 | 5710 | 1007.6
[9 empty] | 95.3333 | 5720 | 1012.8
[9 empty] | 95.5 | 5730 | 1015.8
[9 empty] | 95.6667 | 5740 | 1017.7
[9 empty] | 95.8333 | 5750 | 1019.1
[9 empty] | 96 | 5760 | 1020
[9 empty] | 96.1667 | 5770 | 1020.8
[9 empty] | 96.3333 | 5780 | 1021.4
[9 empty] | 96.5 | 5790 | 1021.9
[9 empty] | 96.6667 | 5800 | 1022.3
[9 empty] | 96.8333 | 5810 | 1022.7
[9 empty] | 97 | 5820 | 1023
[9 empty] | 97.1667 | 5830 | 1023.3
[9 empty] | 97.3333 | 5840 | 1023.5
[9 empty] | 97.5 | 5850 | 1024.1
[9 empty] | 97.6667 | 5860 | 1023.9
[9 empty] | 97.8333 | 5870 | 1024.1
[9 empty] | 98 | 5880 | 1024.3
[9 empty] | 98.1667 | 5890 | 1024.4
[9 empty] | 98.3333 | 5900 | 1024.6
[9 empty] | 98.5 | 5910 | 1024.7
[9 empty] | 98.6667 | 5920 | 1024.8
[9 empty] | 98.8333 | 5930 | 1024.9
[9 empty] | 99 | 5940 | 1025
[9 empty] | 99.1667 | 5950 | 1025.1
[9 empty] | 99.3333 | 5960 | 1025.2
[9 empty] | 99.5 | 5970 | 1025.3
[9 empty] | 99.6667 | 5980 | 1025.4
[9 empty] | 99.8333 | 5990 | 1025.6
[9 empty] | 100 | 6000 | 1025.7
[9 empty] | 100.1667 | 6010 | 1025.7
[9 empty] | 100.3333 | 6020 | 1025.8
[9 empty] | 100.5 | 6030 | 1025.9
[9 empty] | 100.6667 | 6040 | 1026
[9 empty] | 100.8333 | 6050 | 1026
[9 empty] | 101 | 6060 | 1026
[9 empty] | 101.1667 | 6070 | 1026.1
[9 empty] | 101.3333 | 6080 | 1026.1
[9 empty] | 101.5 | 6090 | 1026.1
[9 empty] | 101.6667 | 6100 | 1026.1
[9 empty] | 101.8333 | 6110 | 1026.1
[9 empty] | 102 | 6120 | 1026.1
[9 empty] | 102.1667 | 6130 | 1026.1
[9 empty] | 102.3333 | 6140 | 1026.1
[9 empty] | 102.5 | 6150 | 1026.1
[9 empty] | 102.6667 | 6160 | 1026.1
[9 empty] | 102.8333 | 6170 | 1026
[9 empty] | 103 | 6180 | 1026
[9 empty] | 103.1667 | 6190 | 1026
[9 empty] | 103.3333 | 6200 | 1025.9
[9 empty] | 103.5 | 6210 | 1025.9
[9 empty] | 103.6667 | 6220 | 1025.8
[9 empty] | 103.8333 | 6230 | 1025.8
[9 empty] | 104 | 6240 | 1025.7
[9 empty] | 104.1667 | 6250 | 1025.6
[9 empty] | 104.3333 | 6260 | 1025.6
[9 empty] | 104.5 | 6270 | 1025.5
[9 empty] | 104.6667 | 6280 | 1025.4
[9 empty] | 104.8333 | 6290 | 1025.3
[9 empty] | 105 | 6300 | 1025.2
[9 empty] | 105.1667 | 6310 | 1025.1
[9 empty] | 105.3333 | 6320 | 1025
[9 empty] | 105.5 | 6330 | 1024.9
[9 empty] | 105.6667 | 6340 | 1024.8
[9 empty] | 105.8333 | 6350 | 1024.7
[9 empty] | 106 | 6360 | 1024.5
[9 empty] | 106.1667 | 6370 | 1024.4
[9 empty] | 106.3333 | 6380 | 1024.3
[9 empty] | 106.5 | 6390 | 1024
[9 empty] | 106.6667 | 6400 | 1023.9
[9 empty] | 106.8333 | 6410 | 1023.9
[9 empty] | 107 | 6420 | 1023.7
[9 empty] | 107.1667 | 6430 | 1023.5
[9 empty] | 107.3333 | 6440 | 1023.3
[9 empty] | 107.5 | 6450 | 1023.1
[9 empty] | 107.6667 | 6460 | 1023
[9 empty] | 107.8333 | 6470 | 1022.8
[9 empty] | 108 | 6480 | 1022.7
[9 empty] | 108.1667 | 6490 | 1022.6
[9 empty] | 108.3333 | 6500 | 1022.5
[9 empty] | 108.5 | 6510 | 1022.4
[9 empty] | 108.6667 | 6520 | 1022.3
[9 empty] | 108.8333 | 6530 | 1022.4
[9 empty] | 109 | 6540 | 1022.2
[9 empty] | 109.1667 | 6550 | 1022.2
[9 empty] | 109.3333 | 6560 | 1022.1
[9 empty] | 109.5 | 6570 | 1022.1
[9 empty] | 109.6667 | 6580 | 1022.1
[9 empty] | 109.8333 | 6590 | 1022.1
[9 empty] | 110 | 6600 | 1022.1
[9 empty] | 110.1667 | 6610 | 1022.1
[9 empty] | 110.3333 | 6620 | 1022.2
[9 empty] | 110.5 | 6630 | 1022.1
[9 empty] | 110.6667 | 6640 | 1022.1
[9 empty] | 110.8333 | 6650 | 1022.1
[9 empty] | 111 | 6660 | 1022.1
[9 empty] | 111.1667 | 6670 | 1022.1
[9 empty] | 111.3333 | 6680 | 1022.1
[9 empty] | 111.5 | 6690 | 1022.1
[9 empty] | 111.6667 | 6700 | 1022.1
[9 empty] | 111.8333 | 6710 | 1022.1
[9 empty] | 112 | 6720 | 1022
[9 empty] | 112.1667 | 6730 | 1022
[9 empty] | 112.3333 | 6740 | 1022
[9 empty] | 112.5 | 6750 | 1022
[9 empty] | 112.6667 | 6760 | 1022
[9 empty] | 112.8333 | 6770 | 1022.1
[9 empty] | 113 | 6780 | 1022.1
[9 empty] | 113.1667 | 6790 | 1022.1
[9 empty] | 113.3333 | 6800 | 1022.1
[9 empty] | 113.5 | 6810 | 1022.1
[9 empty] | 113.6667 | 6820 | 1022.1
[9 empty] | 113.8333 | 6830 | 1022
[9 empty] | 114 | 6840 | 1022.1
[9 empty] | 114.1667 | 6850 | 1022
[9 empty] | 114.3333 | 6860 | 1022
[9 empty] | 114.5 | 6870 | 1022
[9 empty] | 114.6667 | 6880 | 1021.9
[9 empty] | 114.8333 | 6890 | 1021.9
[9 empty] | 115 | 6900 | 1021.9
[9 empty] | 115.1667 | 6910 | 1021.8
[9 empty] | 115.3333 | 6920 | 1021.7
[9 empty] | 115.5 | 6930 | 1021.6
[9 empty] | 115.6667 | 6940 | 1021.6
[9 empty] | 115.8333 | 6950 | 1021.5
[9 empty] | 116 | 6960 | 1021.4
[9 empty] | 116.1667 | 6970 | 1021.3
[9 empty] | 116.3333 | 6980 | 1021.2
[9 empty] | 116.5 | 6990 | 1021.2
[9 empty] | 116.6667 | 7000 | 1021.1
[9 empty] | 116.8333 | 7010 | 1021
[9 empty] | 117 | 7020 | 1020.9
[9 empty] | 117.1667 | 7030 | 1020.8
[9 empty] | 117.3333 | 7040 | 1020.7
[9 empty] | 117.5 | 7050 | 1020.7
[9 empty] | 117.6667 | 7060 | 1020.6
[9 empty] | 117.8333 | 7070 | 1020.5
[9 empty] | 118 | 7080 | 1020.5
[9 empty] | 118.1667 | 7090 | 1020.4
[9 empty] | 118.3333 | 7100 | 1020.4
[9 empty] | 118.5 | 7110 | 1020.3
[9 empty] | 118.6667 | 7120 | 1020.3
[9 empty] | 118.8333 | 7130 | 1020.3
[9 empty] | 119 | 7140 | 1020.3
[9 empty] | 119.1667 | 7150 | 1020.3
[9 empty] | 119.3333 | 7160 | 1020.3
[9 empty] | 119.5 | 7170 | 1020.3
[9 empty] | 119.6667 | 7180 | 1020.3
[9 empty] | 119.8333 | 7190 | 1020.3
[9 empty] | 120 | 7200 | 1020.3
[9 empty] | 120.1667 | 7210 | 1020.3
[9 empty] | 120.3333 | 7220 | 1020.3
[9 empty] | 120.5 | 7230 | 1020.4
[9 empty] | 120.6667 | 7240 | 1020.4
[9 empty] | 120.8333 | 7250 | 1020.4
[9 empty] | 121 | 7260 | 1020.4
[9 empty] | 121.1667 | 7270 | 1020.4
[9 empty] | 121.3333 | 7280 | 1020.4
[9 empty] | 121.5 | 7290 | 1020.4
[9 empty] | 121.6667 | 7300 | 1020.4
[9 empty] | 121.8333 | 7310 | 1020.4
[9 empty] | 122 | 7320 | 1020.4
[9 empty] | 122.1667 | 7330 | 1020.3
[9 empty] | 122.3333 | 7340 | 1020.3
[9 empty] | 122.5 | 7350 | 1020.2
[9 empty] | 122.6667 | 7360 | 1020.2
[9 empty] | 122.8333 | 7370 | 1020.1
[9 empty] | 123 | 7380 | 1020
[9 empty] | 123.1667 | 7390 | 1019.9
[9 empty] | 123.3333 | 7400 | 1019.9
[9 empty] | 123.5 | 7410 | 1019.7
[9 empty] | 123.6667 | 7420 | 1019.7
[9 empty] | 123.8333 | 7430 | 1019.5
[9 empty] | 124 | 7440 | 1019.4
[9 empty] | 124.1667 | 7450 | 1019.3
[9 empty] | 124.3333 | 7460 | 1019.2
[9 empty] | 124.5 | 7470 | 1019.1
[9 empty] | 124.6667 | 7480 | 1018.9
[9 empty] | 124.8333 | 7490 | 1018.8
[9 empty] | 125 | 7500 | 1018.6
[9 empty] | 125.1667 | 7510 | 1018.5
[9 empty] | 125.3333 | 7520 | 1018.3
[9 empty] | 125.5 | 7530 | 1018.1
[9 empty] | 125.6667 | 7540 | 1018
[9 empty] | 125.8333 | 7550 | 1017.9
[9 empty] | 126 | 7560 | 1017.7
[9 empty] | 126.1667 | 7570 | 1017.6
[9 empty] | 126.3333 | 7580 | 1017.5
[9 empty] | 126.5 | 7590 | 1017.3
[9 empty] | 126.6667 | 7600 | 1017.2
[9 empty] | 126.8333 | 7610 | 1017.1
[9 empty] | 127 | 7620 | 1017
[9 empty] | 127.1667 | 7630 | 1016.9
[9 empty] | 127.3333 | 7640 | 1016.7
[9 empty] | 127.5 | 7650 | 1016.6
[9 empty] | 127.6667 | 7660 | 1016.6
[9 empty] | 127.8333 | 7670 | 1016.4
[9 empty] | 128 | 7680 | 1016.3
[9 empty] | 128.1667 | 7690 | 1016.3
[9 empty] | 128.3333 | 7700 | 1016.2
[9 empty] | 128.5 | 7710 | 1016.2
[9 empty] | 128.6667 | 7720 | 1016.1
[9 empty] | 128.8333 | 7730 | 1016.1
[9 empty] | 129 | 7740 | 1016.1
[9 empty] | 129.1667 | 7750 | 1016
[9 empty] | 129.3333 | 7760 | 1016
[9 empty] | 129.5 | 7770 | 1016
[9 empty] | 129.6667 | 7780 | 1016
[9 empty] | 129.8333 | 7790 | 1015.9
[9 empty] | 130 | 7800 | 1015.9
[9 empty] | 130.1667 | 7810 | 1015.8
[9 empty] | 130.3333 | 7820 | 1015.8
[9 empty] | 130.5 | 7830 | 1015.8
[9 empty] | 130.6667 | 7840 | 1015.7
[9 empty] | 130.8333 | 7850 | 1015.7
[9 empty] | 131 | 7860 | 1015.6
[9 empty] | 131.1667 | 7870 | 1015.6
[9 empty] | 131.3333 | 7880 | 1015.5
[9 empty] | 131.5 | 7890 | 1015.5
[9 empty] | 131.6667 | 7900 | 1015.4
[9 empty] | 131.8333 | 7910 | 1015.4
[9 empty] | 132 | 7920 | 1015.3
[9 empty] | 132.1667 | 7930 | 1015.3
[9 empty] | 132.3333 | 7940 | 1015.2
[9 empty] | 132.5 | 7950 | 1015.2
[9 empty] | 132.6667 | 7960 | 1015.1
[9 empty] | 132.8333 | 7970 | 1015
[9 empty] | 133 | 7980 | 1014.9
[9 empty] | 133.1667 | 7990 | 1014.8
[9 empty] | 133.3333 | 8000 | 1014.6
[9 empty] | 133.5 | 8010 | 1014.5
[9 empty] | 133.6667 | 8020 | 1014.3
[9 empty] | 133.8333 | 8030 | 1014.1
[9 empty] | 134 | 8040 | 1014
[9 empty] | 134.1667 | 8050 | 1013.8
[9 empty] | 134.3333 | 8060 | 1013.6
[9 empty] | 134.5 | 8070 | 1013.4
[9 empty] | 134.6667 | 8080 | 1013.3
[9 empty] | 134.8333 | 8090 | 1013.1
[9 empty] | 135 | 8100 | 1013
[9 empty] | 135.1667 | 8110 | 1012.9
[9 empty] | 135.3333 | 8120 | 1012.8
[9 empty] | 135.5 | 8130 | 1012.6
[9 empty] | 135.6667 | 8140 | 1012.5
[9 empty] | 135.8333 | 8150 | 1012.5
[9 empty] | 136 | 8160 | 1012.4
[9 empty] | 136.1667 | 8170 | 1012.3
[9 empty] | 136.3333 | 8180 | 1012.2
[9 empty] | 136.5 | 8190 | 1012.2
[9 empty] | 136.6667 | 8200 | 1012.1
[9 empty] | 136.8333 | 8210 | 1012.1
[9 empty] | 137 | 8220 | 1012
[9 empty] | 137.1667 | 8230 | 1012
[9 empty] | 137.3333 | 8240 | 1011.9
[9 empty] | 137.5 | 8250 | 1011.9
[9 empty] | 137.6667 | 8260 | 1011.8
[9 empty] | 137.8333 | 8270 | 1011.8
[9 empty] | 138 | 8280 | 1011.7
[9 empty] | 138.1667 | 8290 | 1011.7
[9 empty] | 138.3333 | 8300 | 1011.6
[9 empty] | 138.5 | 8310 | 1011.6
[9 empty] | 138.6667 | 8320 | 1011.5
[9 empty] | 138.8333 | 8330 | 1011.5
[9 empty] | 139 | 8340 | 1011.4
[9 empty] | 139.1667 | 8350 | 1011.4
[9 empty] | 139.3333 | 8360 | 1011.3
[9 empty] | 139.5 | 8370 | 1011.3
[9 empty] | 139.6667 | 8380 | 1011.3
[9 empty] | 139.8333 | 8390 | 1011.2
[9 empty] | 140 | 8400 | 1011.2
[9 empty] | 140.1667 | 8410 | 1011.1
[9 empty] | 140.3333 | 8420 | 1011.1
[9 empty] | 140.5 | 8430 | 1011.1
[9 empty] | 140.6667 | 8440 | 1011
[9 empty] | 140.8333 | 8450 | 1011
[9 empty] | 141 | 8460 | 1010.9
[9 empty] | 141.1667 | 8470 | 1010.9
[9 empty] | 141.3333 | 8480 | 1010.8
[9 empty] | 141.5 | 8490 | 1010.7
[9 empty] | 141.6667 | 8500 | 1010.7
[9 empty] | 141.8333 | 8510 | 1010.6
[9 empty] | 142 | 8520 | 1010.5
[9 empty] | 142.1667 | 8530 | 1010.4
[9 empty] | 142.3333 | 8540 | 1010.4
[9 empty] | 142.5 | 8550 | 1010.3
[9 empty] | 142.6667 | 8560 | 1010.2
[9 empty] | 142.8333 | 8570 | 1010.1
[9 empty] | 143 | 8580 | 1010
[9 empty] | 143.1667 | 8590 | 1009.9
[9 empty] | 143.3333 | 8600 | 1009.8
[9 empty] | 143.5 | 8610 | 1009.8
[9 empty] | 143.6667 | 8620 | 1009.7
[9 empty] | 143.8333 | 8630 | 1009.6
[9 empty] | 144 | 8640 | 1009.6
[9 empty] | 144.1667 | 8650 | 1009.5
[9 empty] | 144.3333 | 8660 | 1009.5
[9 empty] | 144.5 | 8670 | 1009.5
[9 empty] | 144.6667 | 8680 | 1009.4
[9 empty] | 144.8333 | 8690 | 1009.4
[9 empty] | 145 | 8700 | 1009.4
[9 empty] | 145.1667 | 8710 | 1009.4
[9 empty] | 145.3333 | 8720 | 1009.4
[9 empty] | 145.5 | 8730 | 1009.4
[9 empty] | 145.6667 | 8740 | 1009.3
[9 empty] | 145.8333 | 8750 | 1009.4
[9 empty] | 146 | 8760 | 1009.4
[9 empty] | 146.1667 | 8770 | 1009.3
[9 empty] | 146.3333 | 8780 | 1009.3
[9 empty] | 146.5 | 8790 | 1009.3
[9 empty] | 146.6667 | 8800 | 1009.3
[9 empty] | 146.8333 | 8810 | 1009.4
[9 empty] | 147 | 8820 | 1009.4
[9 empty] | 147.1667 | 8830 | 1009.3
[9 empty] | 147.3333 | 8840 | 1009.4
[9 empty] | 147.5 | 8850 | 1009.3
[9 empty] | 147.6667 | 8860 | 1009.3
[9 empty] | 147.8333 | 8870 | 1009.3
[9 empty] | 148 | 8880 | 1009.3
[9 empty] | 148.1667 | 8890 | 1009.3
[9 empty] | 148.3333 | 8900 | 1009.3
[9 empty] | 148.5 | 8910 | 1009.2
[9 empty] | 148.6667 | 8920 | 1009.3
[9 empty] | 148.8333 | 8930 | 1009.2
[9 empty] | 149 | 8940 | 1009.2
[9 empty] | 149.1667 | 8950 | 1009.2
[9 empty] | 149.3333 | 8960 | 1009.2
[9 empty] | 149.5 | 8970 | 1009.2
[9 empty] | 149.6667 | 8980 | 1009.2
[9 empty] | 149.8333 | 8990 | 1009.2
[9 empty] | 150 | 9000 | 1009.1
[9 empty] | 150.1667 | 9010 | 1009.1
[9 empty] | 150.3333 | 9020 | 1009.1
[9 empty] | 150.5 | 9030 | 1009
[9 empty] | 150.6667 | 9040 | 1009
[9 empty] | 150.8333 | 9050 | 1008.9
[9 empty] | 151 | 9060 | 1008.9
[9 empty] | 151.1667 | 9070 | 1008.9
[9 empty] | 151.3333 | 9080 | 1008.8
[9 empty] | 151.5 | 9090 | 1008.8
[9 empty] | 151.6667 | 9100 | 1008.8
[9 empty] | 151.8333 | 9110 | 1008.7
[9 empty] | 152 | 9120 | 1008.7
[9 empty] | 152.1667 | 9130 | 1008.7
[9 empty] | 152.3333 | 9140 | 1008.7
[9 empty] | 152.5 | 9150 | 1008.7
[9 empty] | 152.6667 | 9160 | 1008.7
[9 empty] | 152.8333 | 9170 | 1008.6
[9 empty] | 153 | 9180 | 1008.6
[9 empty] | 153.1667 | 9190 | 1008.6
[9 empty] | 153.3333 | 9200 | 1008.6
[9 empty] | 153.5 | 9210 | 1008.6
[9 empty] | 153.6667 | 9220 | 1008.6
[9 empty] | 153.8333 | 9230 | 1008.6
[9 empty] | 154 | 9240 | 1008.6
[9 empty] | 154.1667 | 9250 | 1008.6
[9 empty] | 154.3333 | 9260 | 1008.6
[9 empty] | 154.5 | 9270 | 1008.5
[9 empty] | 154.6667 | 9280 | 1008.5
[9 empty] | 154.8333 | 9290 | 1008.5
[9 empty] | 155 | 9300 | 1008.5
[9 empty] | 155.1667 | 9310 | 1008.4
[9 empty] | 155.3333 | 9320 | 1008.4
[9 empty] | 155.5 | 9330 | 1008.4
[9 empty] | 155.6667 | 9340 | 1008.3
[9 empty] | 155.8333 | 9350 | 1008.3
[9 empty] | 156 | 9360 | 1008.2
[9 empty] | 156.1667 | 9370 | 1008.2
[9 empty] | 156.3333 | 9380 | 1008.1
[9 empty] | 156.5 | 9390 | 1008
[9 empty] | 156.6667 | 9400 | 1008
[9 empty] | 156.8333 | 9410 | 1007.9
[9 empty] | 157 | 9420 | 1007.9
[9 empty] | 157.1667 | 9430 | 1007.8
[9 empty] | 157.3333 | 9440 | 1007.7
[9 empty] | 157.5 | 9450 | 1007.7
[9 empty] | 157.6667 | 9460 | 1007.6
[9 empty] | 157.8333 | 9470 | 1007.6
[9 empty] | 158 | 9480 | 1007.5
[9 empty] | 158.1667 | 9490 | 1007.5
[9 empty] | 158.3333 | 9500 | 1007.5
[9 empty] | 158.5 | 9510 | 1007.4
[9 empty] | 158.6667 | 9520 | 1007.3
[9 empty] | 158.8333 | 9530 | 1007.3
[9 empty] | 159 | 9540 | 1007.3
[9 empty] | 159.1667 | 9550 | 1007.2
[9 empty] | 159.3333 | 9560 | 1007.3
[9 empty] | 159.5 | 9570 | 1007.2
[9 empty] | 159.6667 | 9580 | 1007.2
[9 empty] | 159.8333 | 9590 | 1007.1
[9 empty] | 160 | 9600 | 1007.1
[9 empty] | 160.1667 | 9610 | 1007.1
[9 empty] | 160.3333 | 9620 | 1007
[9 empty] | 160.5 | 9630 | 1007
[9 empty] | 160.6667 | 9640 | 1006.9
[9 empty] | 160.8333 | 9650 | 1006.9
[9 empty] | 161 | 9660 | 1006.8
[9 empty] | 161.1667 | 9670 | 1006.8
[9 empty] | 161.3333 | 9680 | 1006.7
[9 empty] | 161.5 | 9690 | 1006.7
[9 empty] | 161.6667 | 9700 | 1006.6
[9 empty] | 161.8333 | 9710 | 1006.5
[9 empty] | 162 | 9720 | 1006.5
[9 empty] | 162.1667 | 9730 | 1006.4
[9 empty] | 162.3333 | 9740 | 1006.3
[9 empty] | 162.5 | 9750 | 1006.3
[9 empty] | 162.6667 | 9760 | 1006.2
[9 empty] | 162.8333 | 9770 | 1006.1
[9 empty] | 163 | 9780 | 1006
[9 empty] | 163.1667 | 9790 | 1005.9
[9 empty] | 163.3333 | 9800 | 1005.9
[9 empty] | 163.5 | 9810 | 1005.8
[9 empty] | 163.6667 | 9820 | 1005.7
[9 empty] | 163.8333 | 9830 | 1005.6
[9 empty] | 164 | 9840 | 1005.5
[9 empty] | 164.1667 | 9850 | 1005.4
[9 empty] | 164.3333 | 9860 | 1005.4
[9 empty] | 164.5 | 9870 | 1005.3
[9 empty] | 164.6667 | 9880 | 1005.3
[9 empty] | 164.8333 | 9890 | 1005.2
[9 empty] | 165 | 9900 | 1005.1
[9 empty] | 165.1667 | 9910 | 1005.1
[9 empty] | 165.3333 | 9920 | 1005
[9 empty] | 165.5 | 9930 | 1005
[9 empty] | 165.6667 | 9940 | 1004.9
[9 empty] | 165.8333 | 9950 | 1004.8
[9 empty] | 166 | 9960 | 1004.8
[9 empty] | 166.1667 | 9970 | 1004.7
[9 empty] | 166.3333 | 9980 | 1004.7
[9 empty] | 166.5 | 9990 | 1004.6
[9 empty] | 166.6667 | 10000 | 1004.6
[9 empty] | 166.8333 | 10010 | 1004.5
[9 empty] | 167 | 10020 | 1004.5
[9 empty] | 167.1667 | 10030 | 1004.4
[9 empty] | 167.3333 | 10040 | 1004.3
[9 empty] | 167.5 | 10050 | 1004.3
[9 empty] | 167.6667 | 10060 | 1004.2
[9 empty] | 167.8333 | 10070 | 1004.2
[9 empty] | 168 | 10080 | 1004.1
[9 empty] | 168.1667 | 10090 | 1004.1
[9 empty] | 168.3333 | 10100 | 1004
[9 empty] | 168.5 | 10110 | 1003.9
[9 empty] | 168.6667 | 10120 | 1003.9
[9 empty] | 168.8333 | 10130 | 1003.9
[9 empty] | 169 | 10140 | 1003.9 |  |  | Tare, 0.0
[9 empty] | 169.1667 | 10150 | 1003.8
[9 empty] | 169.3333 | 10160 | 1003.8
[9 empty] | 169.5 | 10170 | 1003.8
[9 empty] | 169.6667 | 10180 | 1003.8
[9 empty] | 169.8333 | 10190 | 1003.7
[9 empty] | 170 | 10200 | 1003.7
[9 empty] | 170.1667 | 10210 | 1003.7
[9 empty] | 170.3333 | 10220 | 1003.6
[9 empty] | 170.5 | 10230 | 1003.6
[9 empty] | 170.6667 | 10240 | 1003.6
[9 empty] | 170.8333 | 10250 | 1003.6
[9 empty] | 171 | 10260 | 1003.5
[9 empty] | 171.1667 | 10270 | 1003.5
[9 empty] | 171.3333 | 10280 | 1003.5
[9 empty] | 171.5 | 10290 | 1003.5
[9 empty] | 171.6667 | 10300 | 1003.5
[9 empty] | 171.8333 | 10310 | 1003.4
[9 empty] | 172 | 10320 | 1003.4
[9 empty] | 172.1667 | 10330 | 1003.4
[9 empty] | 172.3333 | 10340 | 1003.4
[9 empty] | 172.5 | 10350 | 1003.3
[9 empty] | 172.6667 | 10360 | 1003.3
[9 empty] | 172.8333 | 10370 | 1003.3
[9 empty] | 173 | 10380 | 1003.2
[9 empty] | 173.1667 | 10390 | 1003.2
[9 empty] | 173.3333 | 10400 | 1003.1
[9 empty] | 173.5 | 10410 | 1003.1
[9 empty] | 173.6667 | 10420 | 1003
[9 empty] | 173.8333 | 10430 | 1003
[9 empty] | 174 | 10440 | 1003
[9 empty] | 174.1667 | 10450 | 1003
[9 empty] | 174.3333 | 10460 | 1002.9
[9 empty] | 174.5 | 10470 | 1002.9
[9 empty] | 174.6667 | 10480 | 1002.9
[9 empty] | 174.8333 | 10490 | 1002.9
[9 empty] | 175 | 10500 | 1002.9
[9 empty] | 175.1667 | 10510 | 1002.9
[9 empty] | 175.3333 | 10520 | 1002.9
[9 empty] | 175.5 | 10530 | 1002.9
[9 empty] | 175.6667 | 10540 | 1002.9
[9 empty] | 175.8333 | 10550 | 1002.9
[9 empty] | 176 | 10560 | 1002.8
[9 empty] | 176.1667 | 10570 | 1002.9
[9 empty] | 176.3333 | 10580 | 1002.8
[9 empty] | 176.5 | 10590 | 1002.9
[9 empty] | 176.6667 | 10600 | 1002.9
[9 empty] | 176.8333 | 10610 | 1002.8
[9 empty] | 177 | 10620 | 1002.8
[9 empty] | 177.1667 | 10630 | 1002.7
[9 empty] | 177.3333 | 10640 | 1002.7
[9 empty] | 177.5 | 10650 | 1002.7
[9 empty] | 177.6667 | 10660 | 1002.7
[9 empty] | 177.8333 | 10670 | 1002.7
[9 empty] | 178 | 10680 | 1002.6
[9 empty] | 178.1667 | 10690 | 1002.6
[9 empty] | 178.3333 | 10700 | 1002.5
[9 empty] | 178.5 | 10710 | 1002.4
[9 empty] | 178.6667 | 10720 | 1002.4
[9 empty] | 178.8333 | 10730 | 1002.3
[9 empty] | 179 | 10740 | 1002.2
[9 empty] | 179.1667 | 10750 | 1002.1
[9 empty] | 179.3333 | 10760 | 1002.1
[9 empty] | 179.5 | 10770 | 1002
[9 empty] | 179.6667 | 10780 | 1001.9
[9 empty] | 179.8333 | 10790 | 1001.8
[9 empty] | 180 | 10800 | 1001.6
[9 empty] | 180.1667 | 10810 | 1001.6
[9 empty] | 180.3333 | 10820 | 1001.5
[9 empty] | 180.5 | 10830 | 1001.4
[9 empty] | 180.6667 | 10840 | 1001.2
[9 empty] | 180.8333 | 10850 | 1001
[9 empty] | 181 | 10860 | 1000.9
[9 empty] | 181.1667 | 10870 | 1000.8
[9 empty] | 181.3333 | 10880 | 1000.7
[9 empty] | 181.5 | 10890 | 1000.6
[9 empty] | 181.6667 | 10900 | 1000.5
[9 empty] | 181.8333 | 10910 | 1000.4
[9 empty] | 182 | 10920 | 1000.3
[9 empty] | 182.1667 | 10930 | 1000.2
[9 empty] | 182.3333 | 10940 | 1000
[9 empty] | 182.5 | 10950 | 999.9
[9 empty] | 182.6667 | 10960 | 999.8
[9 empty] | 182.8333 | 10970 | 999.7
[9 empty] | 183 | 10980 | 999.6
[9 empty] | 183.1667 | 10990 | 999.6
[9 empty] | 183.3333 | 11000 | 999.4
[9 empty] | 183.5 | 11010 | 998.9
[9 empty] | 183.6667 | 11020 | 999.4
[9 empty] | 183.8333 | 11030 | 999.2
[9 empty] | 184 | 11040 | 999.1
[9 empty] | 184.1667 | 11050 | 999
[9 empty] | 184.3333 | 11060 | 999
[9 empty] | 184.5 | 11070 | 998.9
[9 empty] | 184.6667 | 11080 | 998.8
[9 empty] | 184.8333 | 11090 | 998.7
[9 empty] | 185 | 11100 | 998.7
[9 empty] | 185.1667 | 11110 | 998.6
[9 empty] | 185.3333 | 11120 | 998.5
[9 empty] | 185.5 | 11130 | 998.5
[9 empty] | 185.6667 | 11140 | 998.4
[9 empty] | 185.8333 | 11150 | 998.5
[9 empty] | 186 | 11160 | 998.4
[9 empty] | 186.1667 | 11170 | 998.4
[9 empty] | 186.3333 | 11180 | 998.3
[9 empty] | 186.5 | 11190 | 998.3
[9 empty] | 186.6667 | 11200 | 998.2
[9 empty] | 186.8333 | 11210 | 998.3
[9 empty] | 187 | 11220 | 998.2
[9 empty] | 187.1667 | 11230 | 998.7
[9 empty] | 187.3333 | 11240 | 998.1
[9 empty] | 187.5 | 11250 | 998.1
[9 empty] | 187.6667 | 11260 | 998.1
[9 empty] | 187.8333 | 11270 | 998.1
[9 empty] | 188 | 11280 | 998.1
[9 empty] | 188.1667 | 11290 | 998.1
[9 empty] | 188.3333 | 11300 | 998
[9 empty] | 188.5 | 11310 | 998
[9 empty] | 188.6667 | 11320 | 998
[9 empty] | 188.8333 | 11330 | 998.1
[9 empty] | 189 | 11340 | 998
[9 empty] | 189.1667 | 11350 | 998
[9 empty] | 189.3333 | 11360 | 998
[9 empty] | 189.5 | 11370 | 998
[9 empty] | 189.6667 | 11380 | 998
[9 empty] | 189.8333 | 11390 | 998
[9 empty] | 190 | 11400 | 997.9
[9 empty] | 190.1667 | 11410 | 998.1
[9 empty] | 190.3333 | 11420 | 998.1
[9 empty] | 190.5 | 11430 | 998.1
[9 empty] | 190.6667 | 11440 | 998
[9 empty] | 190.8333 | 11450 | 998
[9 empty] | 191 | 11460 | 998.1
[9 empty] | 191.1667 | 11470 | 998.1
[9 empty] | 191.3333 | 11480 | 998.1
[9 empty] | 191.5 | 11490 | 998
[9 empty] | 191.6667 | 11500 | 998
[9 empty] | 191.8333 | 11510 | 998
[9 empty] | 192 | 11520 | 998
[9 empty] | 192.1667 | 11530 | 998
[9 empty] | 192.3333 | 11540 | 998
[9 empty] | 192.5 | 11550 | 998
[9 empty] | 192.6667 | 11560 | 997.9
[9 empty] | 192.8333 | 11570 | 997.9
[9 empty] | 193 | 11580 | 997.8
[9 empty] | 193.1667 | 11590 | 997.8
[9 empty] | 193.3333 | 11600 | 997.8
[9 empty] | 193.5 | 11610 | 997.7
[9 empty] | 193.6667 | 11620 | 997.7
[9 empty] | 193.8333 | 11630 | 997.6
[9 empty] | 194 | 11640 | 997.5
[9 empty] | 194.1667 | 11650 | 997.4
[9 empty] | 194.3333 | 11660 | 997.5
[9 empty] | 194.5 | 11670 | 997.4
[9 empty] | 194.6667 | 11680 | 997.3
[9 empty] | 194.8333 | 11690 | 997.3
[9 empty] | 195 | 11700 | 997.2
[9 empty] | 195.1667 | 11710 | 997.2
[9 empty] | 195.3333 | 11720 | 997.1
[9 empty] | 195.5 | 11730 | 997.1
[9 empty] | 195.6667 | 11740 | 997.1
[9 empty] | 195.8333 | 11750 | 997.1
[9 empty] | 196 | 11760 | 997
[9 empty] | 196.1667 | 11770 | 997
[9 empty] | 196.3333 | 11780 | 996.9
[9 empty] | 196.5 | 11790 | 996.9
〖∆𝑉〗_max⁡𝑎𝑙𝑙𝑜𝑤𝑎𝑏𝑙𝑒 =1.2𝑉∆𝑃(1/𝐸_(𝑤 ) +𝐷/(𝑒𝐸_𝑅 ))
x e

## Report
Pressure Testing Record Sheet For Pressure Pipelines Reference: AS/NZS 2566.2, Appendix M, Paragraph M7
Contract: |  |  | Work Area(s):
Sub Work Area(s): |  |  | Lot(s):
Sublot(s): |  |  | Date:
Personnel Conducting Test |  | Drain Layer:
Site Engineer:
CPS Engineer
Pipe Material and Rating | Test Length (m) L |  |  | Pipe Internal Diameter (mm) D |  | Depth of Pipe Below Water Table
0 | 0 |  |  | 0 |  | N.A.
Test Section Sketch (show heights, air valves, gauges and filling points)
Ambient Air Temperature | 0 | °C |  | Water Temperature: |  | 0 | °C
Pressure Rebound Method
Standard Test Pressure |  |  |  | Pressure Applied
[5 empty] | 0 | kPa
Preliminary Phase P60 > 70% STP |  |  |  | Acceptance:
Air Volume Assessment 1.Reduce pressure by 10%-15% STP (ΔP) 2.Measure water volume bled out (ΔV) 3.Calculate ΔVmax allowable Where: Acceptance ΔV < ΔVmax allowable |  |  |  | Air Volume Assessment Parameters
|  |  |  | Nominal Size (mm) |  | 0
|  |  |  | Mean Bore (mm) |  | 0
|  |  |  | Tested Length (m) |  | 0
|  |  |  | V (m3) |  | 0
|  |  |  | e (mm) |  | 0
|  |  |  | Ew (kPax103) |  | 0
|  |  |  | Er (kPax103) |  | 0
|  |  |  | ΔP (kPa) |  | 0
|  |  |  | ΔVmax allowable (L) |  | #DIV/0!
|  |  |  | ΔV (L) |  | 0
|  |  |  | Acceptance |  | #DIV/0!
Main Test Phase Observe and record pressure for 0.5 - 1.5hrs Acceptance 1. No failure of any thrust block, pipe, fitting, joint or other pipeline component present 2.No visible leakage present 3. Pressure rises or remains static for 30min period 4.If doubt exists extend pressure recovery to 90min where pressure drop is to be < 20kPa |  |  |  | Acceptance
Comments:
General Methodology Details
Process for removal of air
Details of water meter
Details of pressure gauge
Details of pump
Water source
Water Disposal
Data Collection
Checked and Signed by Site Engineer |  | Signature: |  |  |  | Date:
Site Photo Records
〖∆𝑉〗_max⁡𝑎𝑙𝑙𝑜𝑤𝑎𝑏𝑙𝑒 =1.2𝑉∆𝑃(1/𝐸_(𝑤 ) +𝐷/(𝑒𝐸_𝑅 ))

## GRAPH
Data Collection Report
Gauge Information |  | Run Info
Serial Number | 809976 | Start Time | 2022-06-15 11:53
Model | 30BARXP2I | Stop Time | 2022-06-15 15:09
Message Store | ------------ | Logging Interval | 10
Units | kPa

## Data for GRAPH
Serial Number | 809976
Model | 30BARXP2I
Units | kPa
Firmware Version | R0324 | Message Store | ------------
Run Index | 5
Logging Type | Actual
Logging Interval | 10
Start Time | 2022-06-15 11:53
Stop Time | 2022-06-15 15:09
Time | Reading
0 | 527.8
10 | 527.8
20 | 527.8
30 | 524
40 | 544.5
50 | 566.8
60 | 574.2
70 | 589.8
80 | 628.1
90 | 645.1
100 | 656.2
110 | 676.1
120 | 695.3
130 | 724.2
140 | 747.4
150 | 763.7
160 | 782.8
170 | 812.4
180 | 832.8
190 | 860.8
200 | 885.9
210 | 916.7
220 | 948.1
230 | 973.3
240 | 1007.4
250 | 1043.9
260 | 1067.9
270 | 1104.1
280 | 1140.1
290 | 1170.3
300 | 1208.7
310 | 1252.7
320 | 1242.3
330 | 1231.4
340 | 1223.7
350 | 1217.7
360 | 1212.6
370 | 1208.2
380 | 1204.4
390 | 1201
400 | 1197.8
410 | 1194.9
420 | 1192.2
430 | 1189.8
440 | 1187.5
450 | 1185.3
460 | 1183.2
470 | 1181.2
480 | 1179.2
490 | 1177.5
500 | 1175.8
510 | 1173.5
520 | 1172.3
530 | 1170.1
540 | 1168
550 | 1167.3
560 | 1166.1
570 | 1164.8
580 | 1163.3
590 | 1161.9
600 | 1160.7
610 | 1159.5
620 | 1158.3
630 | 1157
640 | 1155.8
650 | 1154.6
660 | 1153.4
670 | 1152.3
680 | 1151.1
690 | 1149.9
700 | 1148.8
710 | 1147.6
720 | 1146.5
730 | 1145.4
740 | 1144.3
750 | 1143.2
760 | 1142.2
770 | 1141.2
780 | 1140.3
790 | 1139.4
800 | 1138.5
810 | 1137.5
820 | 1136.7
830 | 1135.9
840 | 1135.2
850 | 1134.4
860 | 1133.5
870 | 1132.8
880 | 1132.1
890 | 1131.3
900 | 1130.7
910 | 1130.1
920 | 1156.1
930 | 1167.3
940 | 1218.5
950 | 1247.2
960 | 1240.3
970 | 1235.7
980 | 1232.3
990 | 1229.5
1000 | 1227
1010 | 1224.9
1020 | 1223
1030 | 1221.3
1040 | 1219.7
1050 | 1218.3
1060 | 1216.9
1070 | 1215.6
1080 | 1214.4
1090 | 1213.2
1100 | 1212
1110 | 1210.9
1120 | 1209.8
1130 | 1208.7
1140 | 1207.7
1150 | 1206.6
1160 | 1205.6
1170 | 1204.6
1180 | 1203.6
1190 | 1202.7
1200 | 1201.8
1210 | 1200.9
1220 | 1200.1
1230 | 1199.2
1240 | 1198.6
1250 | 1197.8
1260 | 1197
1270 | 1196.2
1280 | 1195.6
1290 | 1194.9
1300 | 1194.3
1310 | 1193.6
1320 | 1193
1330 | 1192.4
1340 | 1191.8
1350 | 1191.2
1360 | 1190.6
1370 | 1190
1380 | 1189.4
1390 | 1188.8
1400 | 1188.3
1410 | 1187.7
1420 | 1187.1
1430 | 1186.5
1440 | 1186
1450 | 1185.4
1460 | 1184.9
1470 | 1184.3
1480 | 1191.3
1490 | 1253.2
1500 | 1256.5
1510 | 1251.6
1520 | 1248.3
1530 | 1245.8
1540 | 1243.7
1550 | 1241.8
1560 | 1240.2
1570 | 1238.8
1580 | 1237.5
1590 | 1236.3
1600 | 1235.2
1610 | 1234.1
1620 | 1233.1
1630 | 1232.2
1640 | 1231.3
1650 | 1230.5
1660 | 1229.6
1670 | 1228.8
1680 | 1228
1690 | 1227.3
1700 | 1226.5
1710 | 1225.8
1720 | 1225
1730 | 1224.3
1740 | 1223.7
1750 | 1223.1
1760 | 1222.4
1770 | 1221.7
1780 | 1221.1
1790 | 1220.4
1800 | 1219.8
1810 | 1219.2
1820 | 1218.6
1830 | 1218
1840 | 1217.4
1850 | 1216.8
1860 | 1216.2
1870 | 1215.6
1880 | 1215
1890 | 1214.4
1900 | 1213.8
1910 | 1213.1
1920 | 1212.5
1930 | 1211.9
1940 | 1211.3
1950 | 1210.7
1960 | 1210.1
1970 | 1209.5
1980 | 1208.9
1990 | 1208.3
2000 | 1207.7
2010 | 1207.1
2020 | 1206.6
2030 | 1206
2040 | 1205.4
2050 | 1204.9
2060 | 1204.3
2070 | 1225.8
2080 | 1250.8
2090 | 1246.8
2100 | 1244.3
2110 | 1242.5
2120 | 1241
2130 | 1239.7
2140 | 1238.5
2150 | 1237.5
2160 | 1236.7
2170 | 1235.7
2180 | 1234.9
2190 | 1234.1
2200 | 1233.3
2210 | 1232.6
2220 | 1231.8
2230 | 1231.1
2240 | 1230.5
2250 | 1229.8
2260 | 1229.2
2270 | 1228.6
2280 | 1228
2290 | 1227.4
2300 | 1226.8
2310 | 1226.3
2320 | 1225.7
2330 | 1225.1
2340 | 1224.5
2350 | 1223.9
2360 | 1223.4
2370 | 1222.8
2380 | 1222.1
2390 | 1221.5
2400 | 1220.9
2410 | 1220.3
2420 | 1219.7
2430 | 1219.1
2440 | 1218.5
2450 | 1217.9
2460 | 1217.2
2470 | 1216.6
2480 | 1216
2490 | 1215.4
2500 | 1214.8
2510 | 1214.2
2520 | 1213.6
2530 | 1213.1
2540 | 1212.5
2550 | 1211.9
2560 | 1211.3
2570 | 1210.7
2580 | 1210.2
2590 | 1209.6
2600 | 1209
2610 | 1208.5
2620 | 1207.9
2630 | 1207.3
2640 | 1206.9
2650 | 1206.3
2660 | 1205.7
2670 | 1205.2
2680 | 1204.7
2690 | 1204.1
2700 | 1203.6
2710 | 1203.1
2720 | 1202.6
2730 | 1202.1
2740 | 1201.6
2750 | 1201.1
2760 | 1200.6
2770 | 1200.1
2780 | 1199.6
2790 | 1199.2
2800 | 1198.8
2810 | 1198.3
2820 | 1197.9
2830 | 1197.5
2840 | 1197.1
2850 | 1196.7
2860 | 1196.4
2870 | 1196.1
2880 | 1195.8
2890 | 1195.5
2900 | 1195.2
2910 | 1194.9
2920 | 1194.6
2930 | 1194.3
2940 | 1194
2950 | 1193.7
2960 | 1193.4
2970 | 1193
2980 | 1192.8
2990 | 1192.4
3000 | 1192.1
3010 | 1191.8
3020 | 1191.5
3030 | 1191.2
3040 | 1190.9
3050 | 1190.7
3060 | 1190.5
3070 | 1190.3
3080 | 1190.1
3090 | 1189.9
3100 | 1189.7
3110 | 1189.5
3120 | 1189.3
3130 | 1189.2
3140 | 1189
3150 | 1188.8
3160 | 1188.6
3170 | 1188.4
3180 | 1188.2
3190 | 1188
3200 | 1187.8
3210 | 1187.6
3220 | 1187.4
3230 | 1187.1
3240 | 1186.9
3250 | 1186.6
3260 | 1186.3
3270 | 1186
3280 | 1185.8
3290 | 1185.6
3300 | 1185.2
3310 | 1184.9
3320 | 1184.6
3330 | 1184.2
3340 | 1183.9
3350 | 1183.6
3360 | 1183.2
3370 | 1182.8
3380 | 1182.3
3390 | 1181.9
3400 | 1181.5
3410 | 1181.1
3420 | 1180.7
3430 | 1180.3
3440 | 1179.9
3450 | 1179.4
3460 | 1179.1
3470 | 1178.7
3480 | 1178.3
3490 | 1178
3500 | 1177.6
3510 | 1177.3
3520 | 1177
3530 | 1176.7
3540 | 1176.4
3550 | 1176.1
3560 | 1175.8
3570 | 1175.5
3580 | 1175.3
3590 | 1175
3600 | 1174.7
3610 | 1174.5
3620 | 1174.2
3630 | 1173.9
3640 | 1173.7
3650 | 1173.4
3660 | 1173.2
3670 | 1172.9
3680 | 1172.7
3690 | 1172.4
3700 | 1172.1
3710 | 1171.8
3720 | 1171.5
3730 | 1171.2
3740 | 1170.9
3750 | 1170.6
3760 | 1170.3
3770 | 1170
3780 | 1169.7
3790 | 1169.4
3800 | 1169.1
3810 | 1168.7
3820 | 1168.3
3830 | 1168
3840 | 1167.6
3850 | 1167.3
3860 | 1166.9
3870 | 1166.6
3880 | 1166.2
3890 | 1165.9
3900 | 1165.5
3910 | 1165.1
3920 | 1164.8
3930 | 1164.4
3940 | 1164.1
3950 | 1163.7
3960 | 1163.4
3970 | 1163.1
3980 | 1162.8
3990 | 1162.4
4000 | 1162.1
4010 | 1161.8
4020 | 1161.5
4030 | 1161.3
4040 | 1161
4050 | 1160.7
4060 | 1160.5
4070 | 1160.3
4080 | 1160
4090 | 1159.8
4100 | 1159.6
4110 | 1159.3
4120 | 1159
4130 | 1158.8
4140 | 1158.6
4150 | 1158.3
4160 | 1158.1
4170 | 1157.8
4180 | 1157.6
4190 | 1157.4
4200 | 1157.2
4210 | 1156.9
4220 | 1156.7
4230 | 1156.5
4240 | 1156.2
4250 | 1156
4260 | 1155.8
4270 | 1155.6
4280 | 1155.4
4290 | 1155.2
4300 | 1155
4310 | 1154.8
4320 | 1154.6
4330 | 1154.5
4340 | 1154.3
4350 | 1154.2
4360 | 1154
4370 | 1153.9
4380 | 1153.7
4390 | 1153.6
4400 | 1153.5
4410 | 1153.4
4420 | 1153.3
4430 | 1153.2
4440 | 1153
4450 | 1152.9
4460 | 1152.8
4470 | 1152.7
4480 | 1152.5
4490 | 1152.4
4500 | 1152.2
4510 | 1152.1
4520 | 1152
4530 | 1151.8
4540 | 1151.7
4550 | 1151.6
4560 | 1151.4
4570 | 1151.3
4580 | 1151.1
4590 | 1150.9
4600 | 1150.8
4610 | 1150.7
4620 | 1150.5
4630 | 1150.3
4640 | 1150.2
4650 | 1150
4660 | 1149.8
4670 | 1149.7
4680 | 1149.5
4690 | 1149.3
4700 | 1149.1
4710 | 1149
4720 | 1148.7
4730 | 1148.6
4740 | 1148.4
4750 | 1148.2
4760 | 1148
4770 | 1147.9
4780 | 1147.7
4790 | 1147.5
4800 | 1147.3
4810 | 1147.1
4820 | 1146.9
4830 | 1146.7
4840 | 1146.5
4850 | 1146.3
4860 | 1146.1
4870 | 1145.9
4880 | 1145.7
4890 | 1145.4
4900 | 1145.2
4910 | 1145
4920 | 1144.7
4930 | 1144.5
4940 | 1144.2
4950 | 1144
4960 | 1143.7
4970 | 1143.5
4980 | 1143.2
4990 | 1143
5000 | 1142.8
5010 | 1142.6
5020 | 1142.3
5030 | 1142.1
5040 | 1141.9
5050 | 1141.7
5060 | 1141.5
5070 | 1141.3
5080 | 1141.1
5090 | 1140.9
5100 | 1140.7
5110 | 1140.5
5120 | 1140.4
5130 | 1140.2
5140 | 1140
5150 | 1139.9
5160 | 1139.7
5170 | 1139.6
5180 | 1139.4
5190 | 1139.3
5200 | 1139.1
5210 | 1138.9
5220 | 1138.7
5230 | 1138.6
5240 | 1138.4
5250 | 1138.2
5260 | 1138
5270 | 1137.8
5280 | 1137.7
5290 | 1137.5
5300 | 1137.4
5310 | 1137.2
5320 | 1137
5330 | 1136.8
5340 | 1136.7
5350 | 1136.6
5360 | 1136.4
5370 | 1136.3
5380 | 1136.1
5390 | 1136
5400 | 1135.8
5410 | 1135.7
5420 | 1135.5
5430 | 1135.3
5440 | 1135.1
5450 | 1134.9
5460 | 1134.7
5470 | 1134.5
5480 | 1134.3
5490 | 1134.1
5500 | 1133.9
5510 | 1133.7
5520 | 1133.6
5530 | 1133.3
5540 | 1133.2
5550 | 1133
5560 | 1132.8
5570 | 1132.7
5580 | 1132.5
5590 | 1132.3
5600 | 1132.2
5610 | 1132
5620 | 1131.8
5630 | 1131.6
5640 | 1131.5
5650 | 1131.3
5660 | 1131.2
5670 | 1131
5680 | 1131
5690 | 986.5
5700 | 992.5
5710 | 1007.6
5720 | 1012.8
5730 | 1015.8
5740 | 1017.7
5750 | 1019.1
5760 | 1020
5770 | 1020.8
5780 | 1021.4
5790 | 1021.9
5800 | 1022.3
5810 | 1022.7
5820 | 1023
5830 | 1023.3
5840 | 1023.5
5850 | 1024.1
5860 | 1023.9
5870 | 1024.1
5880 | 1024.3
5890 | 1024.4
5900 | 1024.6
5910 | 1024.7
5920 | 1024.8
5930 | 1024.9
5940 | 1025
5950 | 1025.1
5960 | 1025.2
5970 | 1025.3
5980 | 1025.4
5990 | 1025.6
6000 | 1025.7
6010 | 1025.7
6020 | 1025.8
6030 | 1025.9
6040 | 1026
6050 | 1026
6060 | 1026
6070 | 1026.1
6080 | 1026.1
6090 | 1026.1
6100 | 1026.1
6110 | 1026.1
6120 | 1026.1
6130 | 1026.1
6140 | 1026.1
6150 | 1026.1
6160 | 1026.1
6170 | 1026
6180 | 1026
6190 | 1026
6200 | 1025.9
6210 | 1025.9
6220 | 1025.8
6230 | 1025.8
6240 | 1025.7
6250 | 1025.6
6260 | 1025.6
6270 | 1025.5
6280 | 1025.4
6290 | 1025.3
6300 | 1025.2
6310 | 1025.1
6320 | 1025
6330 | 1024.9
6340 | 1024.8
6350 | 1024.7
6360 | 1024.5
6370 | 1024.4
6380 | 1024.3
6390 | 1024
6400 | 1023.9
6410 | 1023.9
6420 | 1023.7
6430 | 1023.5
6440 | 1023.3
6450 | 1023.1
6460 | 1023
6470 | 1022.8
6480 | 1022.7
6490 | 1022.6
6500 | 1022.5
6510 | 1022.4
6520 | 1022.3
6530 | 1022.4
6540 | 1022.2
6550 | 1022.2
6560 | 1022.1
6570 | 1022.1
6580 | 1022.1
6590 | 1022.1
6600 | 1022.1
6610 | 1022.1
6620 | 1022.2
6630 | 1022.1
6640 | 1022.1
6650 | 1022.1
6660 | 1022.1
6670 | 1022.1
6680 | 1022.1
6690 | 1022.1
6700 | 1022.1
6710 | 1022.1
6720 | 1022
6730 | 1022
6740 | 1022
6750 | 1022
6760 | 1022
6770 | 1022.1
6780 | 1022.1
6790 | 1022.1
6800 | 1022.1
6810 | 1022.1
6820 | 1022.1
6830 | 1022
6840 | 1022.1
6850 | 1022
6860 | 1022
6870 | 1022
6880 | 1021.9
6890 | 1021.9
6900 | 1021.9
6910 | 1021.8
6920 | 1021.7
6930 | 1021.6
6940 | 1021.6
6950 | 1021.5
6960 | 1021.4
6970 | 1021.3
6980 | 1021.2
6990 | 1021.2
7000 | 1021.1
7010 | 1021
7020 | 1020.9
7030 | 1020.8
7040 | 1020.7
7050 | 1020.7
7060 | 1020.6
7070 | 1020.5
7080 | 1020.5
7090 | 1020.4
7100 | 1020.4
7110 | 1020.3
7120 | 1020.3
7130 | 1020.3
7140 | 1020.3
7150 | 1020.3
7160 | 1020.3
7170 | 1020.3
7180 | 1020.3
7190 | 1020.3
7200 | 1020.3
7210 | 1020.3
7220 | 1020.3
7230 | 1020.4
7240 | 1020.4
7250 | 1020.4
7260 | 1020.4
7270 | 1020.4
7280 | 1020.4
7290 | 1020.4
7300 | 1020.4
7310 | 1020.4
7320 | 1020.4
7330 | 1020.3
7340 | 1020.3
7350 | 1020.2
7360 | 1020.2
7370 | 1020.1
7380 | 1020
7390 | 1019.9
7400 | 1019.9
7410 | 1019.7
7420 | 1019.7
7430 | 1019.5
7440 | 1019.4
7450 | 1019.3
7460 | 1019.2
7470 | 1019.1
7480 | 1018.9
7490 | 1018.8
7500 | 1018.6
7510 | 1018.5
7520 | 1018.3
7530 | 1018.1
7540 | 1018
7550 | 1017.9
7560 | 1017.7
7570 | 1017.6
7580 | 1017.5
7590 | 1017.3
7600 | 1017.2
7610 | 1017.1
7620 | 1017
7630 | 1016.9
7640 | 1016.7
7650 | 1016.6
7660 | 1016.6
7670 | 1016.4
7680 | 1016.3
7690 | 1016.3
7700 | 1016.2
7710 | 1016.2
7720 | 1016.1
7730 | 1016.1
7740 | 1016.1
7750 | 1016
7760 | 1016
7770 | 1016
7780 | 1016
7790 | 1015.9
7800 | 1015.9
7810 | 1015.8
7820 | 1015.8
7830 | 1015.8
7840 | 1015.7
7850 | 1015.7
7860 | 1015.6
7870 | 1015.6
7880 | 1015.5
7890 | 1015.5
7900 | 1015.4
7910 | 1015.4
7920 | 1015.3
7930 | 1015.3
7940 | 1015.2
7950 | 1015.2
7960 | 1015.1
7970 | 1015
7980 | 1014.9
7990 | 1014.8
8000 | 1014.6
8010 | 1014.5
8020 | 1014.3
8030 | 1014.1
8040 | 1014
8050 | 1013.8
8060 | 1013.6
8070 | 1013.4
8080 | 1013.3
8090 | 1013.1
8100 | 1013
8110 | 1012.9
8120 | 1012.8
8130 | 1012.6
8140 | 1012.5
8150 | 1012.5
8160 | 1012.4
8170 | 1012.3
8180 | 1012.2
8190 | 1012.2
8200 | 1012.1
8210 | 1012.1
8220 | 1012
8230 | 1012
8240 | 1011.9
8250 | 1011.9
8260 | 1011.8
8270 | 1011.8
8280 | 1011.7
8290 | 1011.7
8300 | 1011.6
8310 | 1011.6
8320 | 1011.5
8330 | 1011.5
8340 | 1011.4
8350 | 1011.4
8360 | 1011.3
8370 | 1011.3
8380 | 1011.3
8390 | 1011.2
8400 | 1011.2
8410 | 1011.1
8420 | 1011.1
8430 | 1011.1
8440 | 1011
8450 | 1011
8460 | 1010.9
8470 | 1010.9
8480 | 1010.8
8490 | 1010.7
8500 | 1010.7
8510 | 1010.6
8520 | 1010.5
8530 | 1010.4
8540 | 1010.4
8550 | 1010.3
8560 | 1010.2
8570 | 1010.1
8580 | 1010
8590 | 1009.9
8600 | 1009.8
8610 | 1009.8
8620 | 1009.7
8630 | 1009.6
8640 | 1009.6
8650 | 1009.5
8660 | 1009.5
8670 | 1009.5
8680 | 1009.4
8690 | 1009.4
8700 | 1009.4
8710 | 1009.4
8720 | 1009.4
8730 | 1009.4
8740 | 1009.3
8750 | 1009.4
8760 | 1009.4
8770 | 1009.3
8780 | 1009.3
8790 | 1009.3
8800 | 1009.3
8810 | 1009.4
8820 | 1009.4
8830 | 1009.3
8840 | 1009.4
8850 | 1009.3
8860 | 1009.3
8870 | 1009.3
8880 | 1009.3
8890 | 1009.3
8900 | 1009.3
8910 | 1009.2
8920 | 1009.3
8930 | 1009.2
8940 | 1009.2
8950 | 1009.2
8960 | 1009.2
8970 | 1009.2
8980 | 1009.2
8990 | 1009.2
9000 | 1009.1
9010 | 1009.1
9020 | 1009.1
9030 | 1009
9040 | 1009
9050 | 1008.9
9060 | 1008.9
9070 | 1008.9
9080 | 1008.8
9090 | 1008.8
9100 | 1008.8
9110 | 1008.7
9120 | 1008.7
9130 | 1008.7
9140 | 1008.7
9150 | 1008.7
9160 | 1008.7
9170 | 1008.6
9180 | 1008.6
9190 | 1008.6
9200 | 1008.6
9210 | 1008.6
9220 | 1008.6
9230 | 1008.6
9240 | 1008.6
9250 | 1008.6
9260 | 1008.6
9270 | 1008.5
9280 | 1008.5
9290 | 1008.5
9300 | 1008.5
9310 | 1008.4
9320 | 1008.4
9330 | 1008.4
9340 | 1008.3
9350 | 1008.3
9360 | 1008.2
9370 | 1008.2
9380 | 1008.1
9390 | 1008
9400 | 1008
9410 | 1007.9
9420 | 1007.9
9430 | 1007.8
9440 | 1007.7
9450 | 1007.7
9460 | 1007.6
9470 | 1007.6
9480 | 1007.5
9490 | 1007.5
9500 | 1007.5
9510 | 1007.4
9520 | 1007.3
9530 | 1007.3
9540 | 1007.3
9550 | 1007.2
9560 | 1007.3
9570 | 1007.2
9580 | 1007.2
9590 | 1007.1
9600 | 1007.1
9610 | 1007.1
9620 | 1007
9630 | 1007
9640 | 1006.9
9650 | 1006.9
9660 | 1006.8
9670 | 1006.8
9680 | 1006.7
9690 | 1006.7
9700 | 1006.6
9710 | 1006.5
9720 | 1006.5
9730 | 1006.4
9740 | 1006.3
9750 | 1006.3
9760 | 1006.2
9770 | 1006.1
9780 | 1006
9790 | 1005.9
9800 | 1005.9
9810 | 1005.8
9820 | 1005.7
9830 | 1005.6
9840 | 1005.5
9850 | 1005.4
9860 | 1005.4
9870 | 1005.3
9880 | 1005.3
9890 | 1005.2
9900 | 1005.1
9910 | 1005.1
9920 | 1005
9930 | 1005
9940 | 1004.9
9950 | 1004.8
9960 | 1004.8
9970 | 1004.7
9980 | 1004.7
9990 | 1004.6
10000 | 1004.6
10010 | 1004.5
10020 | 1004.5
10030 | 1004.4
10040 | 1004.3
10050 | 1004.3
10060 | 1004.2
10070 | 1004.2
10080 | 1004.1
10090 | 1004.1
10100 | 1004
10110 | 1003.9
10120 | 1003.9
10130 | 1003.9
10140 | 1003.9
10150 | 1003.8
10160 | 1003.8
10170 | 1003.8
10180 | 1003.8
10190 | 1003.7
10200 | 1003.7
10210 | 1003.7
10220 | 1003.6
10230 | 1003.6
10240 | 1003.6
10250 | 1003.6
10260 | 1003.5
10270 | 1003.5
10280 | 1003.5
10290 | 1003.5
10300 | 1003.5
10310 | 1003.4
10320 | 1003.4
10330 | 1003.4
10340 | 1003.4
10350 | 1003.3
10360 | 1003.3
10370 | 1003.3
10380 | 1003.2
10390 | 1003.2
10400 | 1003.1
10410 | 1003.1
10420 | 1003
10430 | 1003
10440 | 1003
10450 | 1003
10460 | 1002.9
10470 | 1002.9
10480 | 1002.9
10490 | 1002.9
10500 | 1002.9
10510 | 1002.9
10520 | 1002.9
10530 | 1002.9
10540 | 1002.9
10550 | 1002.9
10560 | 1002.8
10570 | 1002.9
10580 | 1002.8
10590 | 1002.9
10600 | 1002.9
10610 | 1002.8
10620 | 1002.8
10630 | 1002.7
10640 | 1002.7
10650 | 1002.7
10660 | 1002.7
10670 | 1002.7
10680 | 1002.6
10690 | 1002.6
10700 | 1002.5
10710 | 1002.4
10720 | 1002.4
10730 | 1002.3
10740 | 1002.2
10750 | 1002.1
10760 | 1002.1
10770 | 1002
10780 | 1001.9
10790 | 1001.8
10800 | 1001.6
10810 | 1001.6
10820 | 1001.5
10830 | 1001.4
10840 | 1001.2
10850 | 1001
10860 | 1000.9
10870 | 1000.8
10880 | 1000.7
10890 | 1000.6
10900 | 1000.5
10910 | 1000.4
10920 | 1000.3
10930 | 1000.2
10940 | 1000
10950 | 999.9
10960 | 999.8
10970 | 999.7
10980 | 999.6
10990 | 999.6
11000 | 999.4
11010 | 998.9
11020 | 999.4
11030 | 999.2
11040 | 999.1
11050 | 999
11060 | 999
11070 | 998.9
11080 | 998.8
11090 | 998.7
11100 | 998.7
11110 | 998.6
11120 | 998.5
11130 | 998.5
11140 | 998.4
11150 | 998.5
11160 | 998.4
11170 | 998.4
11180 | 998.3
11190 | 998.3
11200 | 998.2
11210 | 998.3
11220 | 998.2
11230 | 998.7
11240 | 998.1
11250 | 998.1
11260 | 998.1
11270 | 998.1
11280 | 998.1
11290 | 998.1
11300 | 998
11310 | 998
11320 | 998
11330 | 998.1
11340 | 998
11350 | 998
11360 | 998
11370 | 998
11380 | 998
11390 | 998
11400 | 997.9
11410 | 998.1
11420 | 998.1
11430 | 998.1
11440 | 998
11450 | 998
11460 | 998.1
11470 | 998.1
11480 | 998.1
11490 | 998
11500 | 998
11510 | 998
11520 | 998
11530 | 998
11540 | 998
11550 | 998
11560 | 997.9
11570 | 997.9
11580 | 997.8
11590 | 997.8
11600 | 997.8
11610 | 997.7
11620 | 997.7
11630 | 997.6
11640 | 997.5
11650 | 997.4
11660 | 997.5
11670 | 997.4
11680 | 997.3
11690 | 997.3
11700 | 997.2
11710 | 997.2
11720 | 997.1
11730 | 997.1
11740 | 997.1
11750 | 997.1
11760 | 997
11770 | 997
11780 | 996.9
11790 | 996.9