## Table 1
INSPECTION TEST PLAN (ITP) – CONDUIT INSTALLATION
Client: |  |  |  | ITP Document No:
Project: |  |  |  | Work Area:
Sub-contractor:
ITEM | ACTIVITY DESCRIPTION | ACCEPTANCE CRITERIA |  |  | CONFORMS |  |  |  | REMARKS
[5 empty] | Y / N / N/A |  | BY | DATE
1 | Material Conformance
1.1 | Electrical Conduit | Orange Electrical PVC Conduit, heavy-duty type, fully complies with AS/NZS 2053 standards. [sizes indicated in the drawing]
1.2 | Communication Conduit | White Communication PVC Conduit, heavy-duty type, fully complies with AS/NZS 2053 standards. [sizes indicated in the drawing]
2 | Conduit Installation
2.1 | Trenching | Verify depth and alignment of trench.
2.2 | Base Preparation | Trench base is free of rocks, debris, and sharp objects; min 75 mm layer of compacted sand.
2.3 | Conduit Installation | Install conduits as per drawings, ensuring correct position, depth, route, alignment without sagging or sharp bends, secure joints, and proper spacing.
2.4 | Conduit Installation – Bends | Install conduit bends with bend and radius per drawings.
2.5 | Backﬁll Within Conduit Layer | Check conduits are undamaged and correctly placed as per drawings, replace any damaged sections, and backﬁll with thermal sand.
2.6 | Polymer tape | Install polymer tape 75 mm above the top conduits, in a straight, continuous line before backﬁlling, as per drawings.
2.7 | Marker tape | Install marker tape 300 mm above the polymer tape, in a continuous straight line as per drawing details, before backﬁlling.
3 | Backﬁll
3.1 | As constructed survey | Carry out as-constructed survey pickup to accurately record the location, alignment, and depth of installed conduits.
3.2 | Backﬁll | Backﬁll around conduits with approved material as per drawings.
INSPECTION SIGN-OFF
Name:
Position:
Signature:
Date:
Conformance status: |  |  | CONFORMING |  |  | NON-CONFORMING
Comments: