## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | YTTP-BT-ITP-001 - Conduit Installation | itp |  |  |  |  | YTTP-BT-ITP-001 - Conduit Installation
section | 1.0 Material Conformance
checkpoint | 1.1 Electrical Conduit
label | ACCEPTANCE CRITERIA:
textbox | Date Completed:
checkpoint | 1.2 Communication Conduit
label | ACCEPTANCE CRITERIA: White Communication PVC Conduit, heavy-duty type, fully complies with AS/NZS 2053 standards. [sizes indicated in the drawing]
textbox | Date Completed:
section | 2.0 Conduit Installation
checkpoint | 2.1 Trenching
label | ACCEPTANCE CRITERIA: Verify depth and alignment of trench.
textbox | Date Completed:
checkpoint | 2.2 Base Preparation
label | ACCEPTANCE CRITERIA: Trench base is free of rocks, debris, and sharp objects; min 75 mm layer of compacted sand.
textbox | Date Completed:
checkpoint | 2.3 Conduit Installation
label | ACCEPTANCE CRITERIA: Install conduits as per drawings, ensuring correct position, depth, route, alignment without sagging or sharp bends, secure joints, and proper spacing.
textbox | Date Completed:
checkpoint | 2.4 Conduit Installation – Bends
label | ACCEPTANCE CRITERIA: Install conduit bends with bend and radius per drawings.
textbox | Date Completed:
checkpoint | 2.5 Backﬁll Within Conduit Layer
label | ACCEPTANCE CRITERIA: Check conduits are undamaged and correctly placed as per drawings, replace any damaged sections, and backﬁll with thermal sand.
textbox | Date Completed:
checkpoint | 2.6 Polymer tape
label | ACCEPTANCE CRITERIA: Install polymer tape 75 mm above the top conduits, in a straight, continuous line before backﬁlling, as per drawings.
textbox | Date Completed:
checkpoint | 2.7 Marker tape
label | ACCEPTANCE CRITERIA: Install marker tape 300 mm above the polymer tape, in a continuous straight line as per drawing details, before backﬁlling.
textbox | Date Completed:
section | 3.0 Backﬁll
checkpoint | 3.1 As constructed survey
label | ACCEPTANCE CRITERIA: Carry out as-constructed survey pickup to accurately record the location, alignment, and depth of installed conduits.
textbox | Date Completed:
checkpoint | 3.2 Backﬁll
label | ACCEPTANCE CRITERIA: Backﬁll around conduits with approved material as per drawings.
textbox | Date Completed:
checkpoint | INSPECTION SIGN-OFF
note | Name:
textbox | Position:
date | Date:
dropdown | Conformance status: | CONFORMING,NON-CONFORMING
signoff | Signature: