## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Radiant Heaters |  |  |  |  | Yes | Radiant Heaters | 02a737b1-120e-4ae9-a929-ad526b7def6f
checkpoint-group |  |  | section | Radiant Heaters
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | VAV's Boxes Ducted |  |  |  |  | Yes | VAV's Boxes Ducted | 04141bf2-bc5c-4c03-9a83-747a08752edb
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Siesmic Bracing Installed
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | E4M - Mechanical Board ( MSSB ) |  |  |  |  | Yes | E4M - Mechanical Board ( MSSB ) | 243ea1ff-4a81-4fa5-8c0b-f909db108d88
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Switch Board Mounted in correct position and level
checkpoint-status |  |  | checkpoint | Switch Board terminations complete
checkpoint-status |  |  | checkpoint | Board Tested
checkpoint-status |  |  | checkpoint | COC's Complete
checklist-flat |  |  | checklist | Labelling of Equipment |  |  |  |  | Yes | Labelling of Equipment | 29adb24b-9f81-4270-95c4-30c8cdb8d028
checkpoint-status |  |  | checkpoint | Correct label installed as per reference on Equipment / Drawing
checkpoint-status |  |  | checkpoint | Label visible
checkpoint-status |  |  | checkpoint | Correct directional arrows / colour coding installed on system
checklist-sectioned |  |  | checklist | Fan Coil Units |  |  |  |  | Yes | Fan Coil Units | 4eb7b137-23c1-4da6-a63d-c9ba00d286cc
checkpoint-group |  |  | section | Unit First Fix QA
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Filters installed
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 1bfccad5-d854-5388-b15d-6a0be45daa06 |  | textbox | Drawing Reference Number
checkpoint-status |  |  | checkpoint | P - trap installed
checkpoint-status |  |  | checkpoint | Driptray installed
checkpoint-status |  |  | checkpoint | Condensate Drains installed
checkpoint-status |  |  | checkpoint | Tundish provided by others
checkpoint-status |  |  | checkpoint | Correct Fall to tundish , and water flow tested
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Metal Cladding |  |  |  |  | Yes | Metal Cladding | 51ae2ac3-0c5d-4c9f-b8ec-b16c7286168a
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Approved materials have been used - 0.6mm galvanised sheet metal, or 0.8mm stucco embossed aluminium
checkpoint-status |  |  | checkpoint | Min. 40mm overlap has been provided on longitudional and circumferential joints
checkpoint-status |  |  | checkpoint | Coned down ends of sheathing have been provided where insulation has been specified as being coned down
checkpoint-status |  |  | checkpoint | All bends have been neatly cut and formed into lobster-back segments
checkpoint-status |  |  | checkpoint | In applications not involving a vapour barrier, pop rivets are provided through pre-drilled holes
checkpoint-status |  |  | checkpoint | In applications involving vapour barrier, 12mm wide straps of 0.4mm sheet metal are used to secure cladding
checkpoint-status |  |  | checkpoint | Straps on straight lengths are no fewer than 3 on each section, c/w locking buckles
checkpoint-status |  |  | checkpoint | Suitcase Clips' are used for all readily removable items such as evaporator heads, strainers, etc which require access for routine maintenance
checkpoint-status |  |  | checkpoint | Penetrations are sealed for gauges, instruments, and drain vents (silicone)
checklist-sectioned |  |  | checklist | Fire Dampers |  |  |  |  | Yes | Fire Dampers | 56a077c9-84d0-4d53-87d3-759b8e53d892
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Correct FD Installed
checkpoint-status |  |  | checkpoint | Access Panel installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Drop Tested ( Sudeshan please use previous job sheet that is in your library)
checkpoint-status |  |  | checkpoint | Track is Clear
checkpoint-status |  |  | checkpoint | Builder to Fire Sealed
checklist-flat |  |  | checklist | CHW & HHW Insulation |  |  |  |  | Yes | CHW & HHW Insulation | 599f366e-7793-4bdf-a808-eebe59fb37df
checkpoint-status |  |  | checkpoint | Approved material thickness has been used (Thermobreak®).
checkpoint-status |  |  | checkpoint | Insulation is installed as per the manufacturers recommendations, as well as per any additional requirements set out in the project specification
checkpoint-status |  |  | checkpoint | Pipe sections firmly abutted to Insulation Blocks within the pipe supports, and Blocks have been glued
checkpoint-status |  |  | checkpoint | Insulation is glued to the pipe with a 50mm wide band of adhesive (Ados F2®) at both ends of section to form the vapour barrier
checkpoint-status |  |  | checkpoint | Adhesive is applied along all longitudinal and circumferential joints
checkpoint-status |  |  | checkpoint | A 50mm wide strip of pressure sensitive tape reinforced aluminium tape is applied to the insulation facing, along and around all joints
checkpoint-status |  |  | checkpoint | Mitre cut elbows have been used on all bends.
checklist-sectioned |  |  | checklist | AHU's |  |  |  |  | Yes | AHU's | 7424cff6-fe5a-4042-bc68-d856ede330f5
checkpoint-group |  |  | section | AHU's
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 02aeab4c-0d0f-59d4-a0ef-29ba7b59fe23 |  | textbox | Drawing Reference Number
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Commissioning Complete
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | Mechanical Duct |  |  |  |  | Yes | Mechanical Duct | 89004578-b1dc-4956-88cc-7482568c6758
checkpoint-group |  |  | section | First Fix QA
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | Ducting / equipment connections including flexibles, nuts, bolts and washers correct and tight.
checkpoint-status |  |  | checkpoint | U/S of duct heights correct as per Workshop Drawings.
checkpoint-status |  |  | checkpoint | Ducts to be removed relocated / relocated as per drawings
checkpoint-status |  |  | checkpoint | Duct Hangers (is spacing correct, installed level etc)
checkpoint-status |  |  | checkpoint | Duct jointing (Joints sealed, cleats fitted etc)
checkpoint-status |  |  | checkpoint | Fire Dampers installed in open position c/w access panel.
checkpoint-status |  |  | checkpoint | Sound attenuators installed
checkpoint-status |  |  | checkpoint | Filter box installed
checkpoint-status |  |  | checkpoint | Transfer ducts installed
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Motorized dampers orientation to be installed correct way for sealing purpose
checkpoint-status |  |  | checkpoint | Access Panels to be installed as per drawing
checkpoint-status |  |  | checkpoint | All volume control dampers set fully open.
checkpoint-status |  |  | checkpoint | Butterfly and outlet dampers installed as per drawing and in open position.
checkpoint-status |  |  | checkpoint | Seismic bracing installed as per Drawing
checkpoint-group |  |  | section | Fit Off QA
checkpoint-status |  |  | checkpoint | Flexible ducting installed c/w supports.
checkpoint-status |  |  | checkpoint | Correct Equipment / Correct Grills / Diffuser Installed
checklist-flat |  |  | checklist | CHW & HHW Piping ( VICTAULIC ) |  |  |  |  | Yes | CHW & HHW Piping ( VICTAULIC ) | 9631b408-42a2-42ee-b3eb-bb9a5473b7e2
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | 98f00e2f-274c-5567-b3bf-c7e027a26fde |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing i.e. Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | The pipe OD and groove dimensions are within tolerance range as per victaulic specification
checkpoint-status |  |  | checkpoint | The correct coupling has been used for the correct joint i.e. flexible or rigid
checkpoint-status |  |  | checkpoint | All fitting are vicataulic approved
checkpoint-status |  |  | checkpoint | Victaulic grease has been applied to the gasket and OD of pipe
checkpoint-status |  |  | checkpoint | Couplings are tightened by alternating sides equally
checkpoint-status |  |  | checkpoint | Bolt pads have firm metal to metal contact
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed ( Expansion joints , loops etc. )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 34d431c9-0158-50cc-9ae9-faa51326960e |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | External Duct Work Insulation |  |  |  |  | Yes | External Duct Work Insulation | a4c95ef4-dc07-4255-b1c1-1c9371011f3e
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Ductwrap materials - Multitel 18kg Density foiled 1-side 25mm thick
checkpoint-status |  |  | checkpoint | Cover entire surface with insulation including all flanges, stiffeners and support angles.
checkpoint-status |  |  | checkpoint | Provide 50mm over lapping at all joints.
checkpoint-status |  |  | checkpoint | Tape all joints with 75mm width (72mm on the Market) Aluminium foiled tape.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 375mm to 750mm steel weld pins on centreline at 400mm spacing bottom surface only.
checkpoint-status |  |  | checkpoint | Fixing for all Duct size 750mm and greater steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Fixing for all Duct riser steel weld pins at 400mm spacing maximum.
checkpoint-status |  |  | checkpoint | Using additional polypropylene fixing Bands 600mm centres.
checkpoint-status |  |  | checkpoint | Provide an overlap of atleast 300mm where insulation changes from the inside of the duct to the outside.
checklist-flat |  |  | checklist | Condensate Insulation |  |  |  |  | Yes | Condensate Insulation | ad68dfca-ab9c-4844-8d50-79a018607627
checkpoint-status |  |  | checkpoint | Approved materials have been used (e.g. Elastomeric closed cell insulation), min 9m thick
checkpoint-status |  |  | checkpoint | Entire surface of pipe is covered from the indoor units' condensate trap, for a distance of 2m down the line
checkpoint-status |  |  | checkpoint | Adhesive is applied to any longitudinal and circumferential joints, as well as to the ends of the insulation to the pipe
checkpoint-status |  |  | checkpoint | Finish circumferential joints by wrapping with 50mm wide pressure-sensitive pre-adhered PVC tape.
checklist-sectioned |  |  | checklist | Heater banks |  |  |  |  | Yes | Heater banks | ae2de4cf-f553-4809-ac0f-500f6dac8ddf
checkpoint-group |  |  | section | Heater banks
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Equipment heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | Second Fix QA
checkpoint-status |  |  | checkpoint | Fire rated insulation installed as per spec
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | Fans |  |  |  |  | Yes | Fans | c29918e5-e6e7-4f78-bd76-7919da82d88e
checkpoint-group |  |  | section | Fans
checkpoint-status |  |  | checkpoint | Correct Equipment / plant installed
checkpoint-status |  |  | checkpoint | Mountings / springs installed
checkpoint-status |  |  | checkpoint | Check-off Shop Drawings. Is it all installed correctly: i.e.., each run complete.
checkpoint-status |  |  | checkpoint | U/S of Fan heights correct as per Workshop Drawings.
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-sectioned |  |  | checklist | DX Units |  |  |  |  | Yes | DX Units | cb489de5-e6dd-45d5-af07-c20ee8e99c82
checkpoint-group |  |  | section | DX Units
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Out door Unit Installed
checkpoint-status |  |  | checkpoint | u/s of Unit at correct height
checkpoint-status |  |  | checkpoint | Mounting and Springs Installed
checkpoint-status |  |  | checkpoint | Pipe Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Correct Hanger Spacing
checkpoint-status |  |  | checkpoint | Unit Plenum Boxes to be installed
checkpoint-status |  |  | checkpoint | Refrigeration Pipework installed as per drawings
text | 8cf353a9-64c1-50fa-8f28-8779b0504ff2 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | Pipework Installed from DX unit box to Outdoor unit
checkpoint-status |  |  | checkpoint | Condensate Piping installed
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up
checkpoint-status |  |  | checkpoint | Pressure Tested
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
text | fe3dce3d-ac1c-5782-aa05-1ac3fa085898 |  | textbox | Sign Off by
checkpoint-status |  |  | checkpoint | Vacuum system down below 500 Microns
checkpoint-status |  |  | checkpoint | Triple Evacuation procedure to be done
checkpoint-status |  |  | checkpoint | Refrigeration ( Scale ) charge unit completed - According to Calculation for Pipe Size & Length
checkpoint-status |  |  | checkpoint | Insulation Complete for Piping and Condensate lines
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Filters Installed
checkpoint-status |  |  | checkpoint | Grilles Installed
checkpoint-status |  |  | checkpoint | Commissioning Complete
checkpoint-group |  |  | section | E4M QA
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checkpoint-status |  |  | checkpoint | Do not energize DX unit until commissioning , otherwise all solenoid will close resulting in no evacuation of Moisture from Indoor units
checklist-flat |  |  | checklist | Fire Rated Duct Insulation |  |  |  |  | Yes | Fire Rated Duct Insulation | d5fc6c8b-7f77-4aa0-973d-4118ab36b6a4
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Fire rated Ductwrap materials - 38mm thick Fyrewrap Elite 1.5 (FRL 120/120/120)
checkpoint-status |  |  | checkpoint | Install as per Manufacturer's Standards: (Trafalgar-Fyrewrap)
checkpoint-status |  |  | checkpoint | Fyrewrap duct wrap must completely covered the duct and there must not be any exposed sections or gaps.
checkpoint-status |  |  | checkpoint | A 100mm minimum overlap must be used on all joints. Only the Three specified methods (telescope, checkerboard and butt splice methods.) of overlap may be used when adjoining Fyrewrap duct wraps.
checkpoint-status |  |  | checkpoint | Cut edges must be completely sealed with the specified pressure-sensitive aluminium foiled tape.
checkpoint-status |  |  | checkpoint | ≤600 x600 duct size Steel banding only spacing 40mm from edges over the overlap and one additional between overlaps.
checkpoint-status |  |  | checkpoint | ≤1200 x1200 duct size Steel banding and pins bottoms only spacing 40mm from edges over the overlap and one additional between overlaps. Pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | ≥1200 x1200 duct size pins only all sides of duct pre-welded Pins grid 200mm centres.
checkpoint-status |  |  | checkpoint | Wall penetrations up to 1600mm duct size 75mm x 75mm x1.6mm steel angle 100mm width x 60mm thick maxilite board.
checkpoint-status |  |  | checkpoint | Length of second layer from the fire barrier FRL 60/60/60
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm or less -second layer 1350mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 1200mm or less -second layer 1600mm
checkpoint-status |  |  | checkpoint | Duct size 600mm x 600mm -second layer 1900mm
checkpoint-status |  |  | checkpoint | Duct size 200mm x 2400mm -second layer 2500mm
checkpoint-status |  |  | checkpoint | Duct size 2400mm x 3600mm -second layer 2700mm
checkpoint-status |  |  | checkpoint | Used only Trafalgar Access Panels -must be fitting directly over the existing duct access panels fixed with rivets and fyreflex fire rated sealant, with a second local layer of Fyrewrap.
checklist-sectioned |  |  | checklist | Chillers / Buffer Tank / Dosing Pod / Pumps |  |  |  |  | Yes | Chillers / Buffer Tank / Dosing Pod / Pumps | d77c4348-a43b-4799-9335-857e10d76225
checkpoint-group |  |  | section | Equipment QA
checkpoint-status |  |  | checkpoint | Check if plinth site is correct
checkpoint-status |  |  | checkpoint | Correct Unit Installed
checkpoint-status |  |  | checkpoint | Setting out point correct
checkpoint-status |  |  | checkpoint | Anti Vibration pads to be installed if required
checkpoint-status |  |  | checkpoint | Correct Springs installed ( If required )
checkpoint-group |  |  | section | Unit Second Fix QA
checkpoint-status |  |  | checkpoint | Condensate Piping installed ( If required )
checkpoint-status |  |  | checkpoint | Tundish installed by others and connected up ( If required )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | ea6f3b50-29f4-5093-a9b7-cebf69b19d42 |  | textbox | Drawing Reference Number
checklist-flat |  |  | checklist | Duct / Equipment Cleaning |  |  |  |  | Yes | Duct / Equipment Cleaning | dba8496a-43ea-47cc-b558-89c0ca78e160
checkpoint-status |  |  | checkpoint | Specialized Cleaning contractor to clean Outdoor / Supply and Return air Ducting and equipment in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Verification of ductwork cleanliness shall be by vacuum test ( gravimetric analysis ) in accordance with HVCA Guide TR/19 or NADCA Standard 1992-01
checkpoint-status |  |  | checkpoint | Undertake a second vacuum test immediately prior to handover.
checklist-flat |  |  | checklist | External Acoustic Insulation (FCU's) |  |  |  |  | Yes | External Acoustic Insulation (FCU's) | ea74bf2d-4ca2-4baf-a121-24bd83907561
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Acoustic wrap materials - 50mm Polyester sheet cover with 5kg wave bar
checkpoint-status |  |  | checkpoint | Cover all surface of the FCU units with insulation excluding the Vents and pipe outlet area.
checkpoint-status |  |  | checkpoint | fixing using self adhesive pins and polypropylene Bands with with buckles .
checkpoint-status |  |  | checkpoint | Tape all joints with 50mm width reinforced Aluminium foiled tape.
checklist-flat |  |  | checklist | Cowls |  |  |  |  | Yes | Cowls | ed1dd5ac-ad98-4dde-bb28-e2ec46137fcb
checkpoint-status |  |  | checkpoint | Outside Air Roof Cowl Installed
checkpoint-status |  |  | checkpoint | Builder - Waterproof and Seal to be installed
checklist-flat |  |  | checklist | E4M QA |  |  |  |  | Yes | E4M QA | ed94b6e7-b320-47cc-a900-6004cbe9b32b
checkpoint-status |  |  | checkpoint | Wiring First Fix Complete
checkpoint-status |  |  | checkpoint | Cable Tray Installed Correctly
checkpoint-status |  |  | checkpoint | Electrical Isolators installed in Correct location
checkpoint-status |  |  | checkpoint | Units Terminated
checkpoint-status |  |  | checkpoint | Temp Sensors and Controllers Installed
checkpoint-status |  |  | checkpoint | Units Tested and Running
checklist-flat |  |  | checklist | Internal Duct Work Insulation |  |  |  |  | Yes | Internal Duct Work Insulation | f2fe37b4-4f1e-40e1-b517-721e14bd04db
checkpoint-status |  |  | checkpoint | Insulate ducting as per drawing
checkpoint-status |  |  | checkpoint | Using Approved Insulation Duct materials - Fibreglass
checkpoint-status |  |  | checkpoint | Fixed with Adhesive weld pins and speed clips located not more than 75mm from the edges of the ducts and spaced not more than 300mm centres.
checkpoint-status |  |  | checkpoint | Longitudinal corner joints fixed with:
checkpoint-status |  |  | checkpoint | duct dimensions less than 300mm -25mmx25mm angles
checkpoint-status |  |  | checkpoint | duct dimensions 300mm and greater -50mmx50mm angles
checkpoint-status |  |  | checkpoint | Joints taped between adjacent of insulation with a 75mm wide strip of reinforced aluminium foil laminate tape.
checkpoint-status |  |  | checkpoint | Tape joints protected with 75mm wide sheet metal cover strip, pop riveted to the corner angles.
checklist-flat |  |  | checklist | Braze Bench Test |  |  |  |  | Yes | Braze Bench Test | f57d3cda-a159-4e97-b14f-e4107f104237
checkpoint-status |  |  | checkpoint | Test Sheet Completed
text | bfb6f45e-04e4-58d7-9190-b457ff78f764 |  | textbox | BUILDING:
text | a3a9af02-194f-5897-97f3-d6f125f706ed |  | textbox | AREA / SYSTEM:
text | d50863a6-b317-597e-8299-c7c9e9434fbd |  | textbox | DRAWING No.
text | 9c70197b-c415-5cf8-8170-6cbf5b2db861 |  | textbox | NAME OF WORKER:
text | 3cd9eb63-35e5-5e40-8735-33f713163029 |  | textbox | ASSIGNED BRAZE ID.
text | 9c9248c0-84a4-5e52-8a8a-4d3de0232742 |  | textbox | JOINT TYPE INSPECTED:
text | 8eca268a-0994-5b4c-81af-2d62052d12c4 |  | textbox | INSPECTING SUPERVISOR
checkpoint-status |  |  | checkpoint | Tube is cut by suitable means, ends are deburred & cleaned of any filings, and surfaces prepared with light grade emery paper.
checkpoint-status |  |  | checkpoint | Joint fit has correct clearance and expanded end of tube (if applicable) is to correct length for pipe size - as per NDY specified requirements
checkpoint-status |  |  | checkpoint | Heat from Oxy Acetylene torch is being applied uniformly to the fitting, and torch flame is slightly reducing/carburising.
checkpoint-status |  |  | checkpoint | Silfos used is 15% and is being applied so that through capillary action is achieved around the entire joint.
checkpoint-status |  |  | checkpoint | Shoulder build-up of Sipfos is just present around the entire circumference of the brazed joint, and completed joint is left to air cool.
checkpoint-status |  |  | checkpoint | Sign Off Complete
checkpoint-status |  |  | checkpoint | Signed off By AE Smith
checkpoint-status |  |  | checkpoint | Signed off By Witness
text | 73e76eaf-d41b-5599-8e04-6d7e16bddbb6 |  | textbox | Witness Name
checkpoint-status |  |  | checkpoint | Signed off by Consultant
text | fc3dfcdb-3319-5d33-b661-e0dd6058c771 |  | textbox | Consultant Name
checklist-flat |  |  | checklist | CHW & HHW Piping ( WELDING ) |  |  |  |  | Yes | CHW & HHW Piping ( WELDING ) | f692c9e1-89e0-497b-9ce2-0c3c3c39e444
checkpoint-status |  |  | checkpoint | Pipework installed as per Drawing
text | 11588f71-c860-5803-90bf-777be7597473 |  | textbox | Installation done by
checkpoint-status |  |  | checkpoint | All fabricators/welders are qualified and have current tickets
checkpoint-status |  |  | checkpoint | Pipe sizing is correct and valving in correct location
checkpoint-status |  |  | checkpoint | Valve arrangement installed as per Detail specified drawing i.e. Chiller/ AHU / Pump / FCU / VAV / Buffer tank /Expansion tank / Dosing Pod
checkpoint-status |  |  | checkpoint | Insulation blocks installed where required
checkpoint-status |  |  | checkpoint | Correct hanger spacing
checkpoint-status |  |  | checkpoint | Isolating and Control valve installed correctly
checkpoint-status |  |  | checkpoint | Hose piping installed
checkpoint-status |  |  | checkpoint | Air vents installed at all high points
checkpoint-status |  |  | checkpoint | All materials are in accordance with applicable AS/NZ standard
checkpoint-status |  |  | checkpoint | Welding procedure specification to be applied as per attached
checkpoint-status |  |  | checkpoint | Steel is primed and weld painted after works are completed (PA10)
checkpoint-status |  |  | checkpoint | Welding of pipework
checkpoint-status |  |  | checkpoint | Pipework Seismic to be installed ( Expansion joints , loops etc. )
checkpoint-status |  |  | checkpoint | Seismic Bracing Installed
text | 9a289631-8886-5770-92c7-abda10d9a2b3 |  | textbox | Drawing Reference Number