## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-075-CIV-CPD-General Concrete Melbourne Water | itp |  |  |  | Yes | ITP-075-CIV-CPD-General Concrete Melbourne Water Rev 0
section | 1. Referenced Documentation
checkpoint-no-status | 1. Referenced Documentation
label | Document Title: ITP-CIV-CPD-General Concrete_Melbourne Water
label | ITP Description: General Concrete_Melbourne Water
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): CIV-CPD
label | Revision Number: 0
label | Revision Date: 8/09/2023
label | ITP created by: Ethan CARUANA-SMITH
label | ITP approved for use by: Pradeep TALASILA
checkpoint | 1.1 - Non Dependent
label | Reference - VicRoads Section 703 June 2018
checkpoint | 1.2 - Non Dependent
label | Reference - VicRoads Section 812 July 2016
checkpoint | 1.3 - Non Dependent
label | Reference - Melbourne Water 7251/08/420
checkpoint | 1.4 - Non Dependent
label | Reference - AS1379-2007
checkpoint | 1.5 - Non Dependent
label | Reference - AS3610-2018
checkpoint | 1.6 - Non Dependent
label | Reference - AS4671-2019
section | 2. Preliminaries - Materials
checkpoint | 2.1 - Bedding Material / Base Layer
label | Reference - IFC Drawings 703.21 812.04
label | Acceptance Criteria - 20mm Class 3 bedding material conforms to specified requirements applicable to the class of product as detailed on the drawings.
label | ○ Material is registered with VicRoads in accordance with Code of Practice RC500.02.
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Once, for each mix design, prior to placement of material
label | Category - HP
label | Responsibility - Nominated Authority
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.2 - Concrete Mix
label | Reference - IFC Drawings 703.05 (a), 703.07 MRPA Quality Management Plan Melbourne Water 7251/08/420
label | Acceptance Criteria - Concrete mix meets strength, grade, and maximum aggregate size as detailed on the drawings.
label | ○ Paving concrete mix conforms to AS1379.
label | ○ SUP concrete mix is registered with VicRoads.
label | ○ No air entraining chemical admixtures shall be used without approval from the Nominated Authority.
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Once, for each mix design, prior to placement of concrete
label | Category - IP
label | Responsibility - Nominated Authority
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
checkpoint | 2.3 - Reinforcement Certification (or ACRS Certification)
label | Reference - 703.13 MRPA Quality Management Plan
label | Acceptance Criteria - Reinforcement shall comply with AS4671.
label | ○ Alternatively, provide a current ACRS certification for materials and for bar processing (as this covers a higher certification)
label | Note: ACRS certificate may cover both aspects or be for each separate portion (e.g 1 for the material supplier and another for the bar processor (bending, cropping and delivery)
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Once for each supplier, prior to placement of order
label | Category - IP
label | Responsibility - Nominated Authority
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.4 - Evaporative Retardant
label | Reference - 703.09
label | Acceptance Criteria - Details of evaporative retardant, application procedure (including application rates) to be submitted for review to the Nominated Authority.
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Once, for each product, prior to placement of concrete
label | Category - WP
label | Responsibility - Nominated Authority
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.5 - Curing Compound
label | Reference - 703.10 (a)
label | Acceptance Criteria - Details of curing compound and NATA test certificate stating compliance with AS3799 no more than 3 years from issue, to be submitted for review to the Nominated Authority.
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Once, for each product, prior to placement of concrete
label | Category - IP
label | Responsibility - Nominated Authority
label | Verifying Documents - This ITP
date | Date Completed:
section | 3. Pre-construction Activities
checkpoint | 3.1 - IFC Drawings
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | Method - Document Review
label | Frequency - Prior to starting Works and at regular intervals
label | Category - HP*
label | Responsibility - All
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 3.2 - Survey Set-out
label | Reference - IFC Drawings 703.17
label | Acceptance Criteria - The work shall be constructed in accordance with the confirmed set out to the line and level and cross-sectional profiles as shown on the drawings.
label | ○ The Nominated Authority will review and confirm the set out.
label | ○ Maximum deflection angle of 18 degrees
label | Attach: Survey Report
label | Method - Document Review, Measure, Visual
label | Frequency - Where applicable, each lot
label | Category - HP
label | Responsibility - Nominated Authority
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
section | 4. Construction Activities
checkpoint | 4.1 - Excavation
label | Reference - 703.20 Melbourne Water 7251/08/420
label | Acceptance Criteria - Excavation shall be to a sufficient depth to allow for the required compacted thickness of bedding material under the full width of concrete paving.
label | ○ Excavation to allow for a minimum of 50mm reinforcement cover on earth face and a minimum of 375mm from pipe joint.
label | Method - Visual, Measure
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.2 - Bedding Material Placement & Compaction
label | Reference - 703.21
label | Acceptance Criteria - Place bedding material to the minimum thicknesses (post-compaction) as per the IFC drawings (equal to or greater than the relevant Council drawings).
label | ○ Bedding shall be trimmed to the appropriate levels, moistened as necessary, and firmly compacted.
label | ○ The foundation shall be true to grade and cross section as shown on the drawings by filling and excavating as necessary.
label | ○ All soft wet or unstable material shall be removed to a depth of not less than 100 mm below the design level of the underside of bedding and filled with bedding material moistened and compacted to form a stable foundation.
label | Attach: Bedding Material Delivery Dockets
label | Method - Visual, Measure
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.3 - Formwork Construction & Placement
label | Reference - IFC Drawings 703.12
label | Acceptance Criteria - Designed and constructed in such a manner so it can be removed without damage to the concrete.
label | ○ Formwork to be rigid, braced, full depth of the concrete & tied together to restrict movement during concreting operations to maintain dimensional comformance.
label | ○ Joints in formwork shall be constructed such that loss of mortar is prevented.
label | ○ Prior to placing concrete in an earth excavation, formwork shall be erected so that fresh concrete is not placed directly against the sides of the excavation.
label | Method - Visual, Measure
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.4 - Construction Joints & Matching Exisiting Surfaces
label | Reference - IFC Drawings 703.24
label | Acceptance Criteria - Where applicable, construction joints shall be placed where the new construction ties into existing structures.
label | ○ Consult the relevant Council Standard drawings for the joint detail, these may require:
label | i. Concrete cutting of a shear-key
label | ii. Surface roughening
label | iii. Drilling and insertion of dowel bars (may also be galvanised)
label | iv. Cutting a groove for sealant
label | ○ Where it is necessary to join to an existing section of profile different from that being constructed, the change of profile shall be made at a constant rate between 10 and 20 mm per metre.
label | ○ Transitions between different profiles shall be made in accordance with the drawings.
label | ○ Matching of new to existing concrete paving shall be such that it appears identical to the existing section.
label | Method - Visual, Measure
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.5 - Isolation Joints
label | Reference - IFC Drawings 703.26 (c)
label | Acceptance Criteria - Where applicable, isolation joints shall be placed:
label | i. around all abutting structures such as pits, utility services, power poles, kerbs and other such features
label | ii. at any location marked on the drawings
label | ○ The joint shall be made with a compressable material extending for the full width and full depth of the paving and secured into position prior to concrete operations.
label | Method - Visual, Measure
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.6 - Reinforcement Placement
label | Reference - IFC Drawings 703.13 Melbourne Water 7251/08/420
label | Acceptance Criteria - The correct mesh type and location as shown on the IFC drawings.
label | ○ Any splice lengths achieve the minimum length and are in contact for this length.
label | ○ The reinforcement surface condition is free from dirt, debris and damage.
label | ○ The resulting cage securely held with sufficient ties and/or bar chairs to limit displacement or deformation during the concrete pour (typically 900mm crs maximum).
label | ○ Wire chairs with or without plastic tips, bricks or pieces of timber or coarse aggregate shall not be used to support steel reinforcement.
label | ○ Minimum cover of 50mm at edges has been achieved (including tie wire locations).
label | Method - Measure, Visual
label | Frequency - Each element
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.7 - Pre-pour Inspection
label | Reference - IFC Drawings 703.15, 703.21 Melbourne Water 7251/08/420
label | Acceptance Criteria - Inspection to ensure that forms, reinforcement dowels and other embedments conform to the requirements of the specifications and drawings.
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.8 - Weather Conditions & Evaporation Limits
label | Reference - 703.09
label | Acceptance Criteria - Concrete shall not be placed when the air temperature at the point of placement is less than 5°C or greater than 35°C.
label | ○ The temperature of concrete, measured immediately prior to placing, shall not be less than 10°C or greater than 32°C.
label | ○ The air temperature, relative humidity, concrete temperature and wind velocity are measured to determine the evaporation rate of water from the concrete.
label | ○ When the evaporation rate exceeds 0.50 kg/m²/hr apply evaporation retardant at the rates specified on the manufacturer’s TDS.
label | Record: Required information on the Concrete Pour Record.
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.9 - Concrete Testing - Sampling Frequencies
label | Reference - 703.11 Melbourne Water 7251/08/420
label | Acceptance Criteria - Concrete cast in one continuous operation to be tested at a frequency as shown below:
label | ○ 0m³ to 50m³ = 1 sample
label | ○ Each sample shall consist of 1 no. slump test and 2 no. compressive strength cylinders minimum.
label | ○ Compressive strength cylinders = 2 no. 28 day strength.
label | Record: Required information on the Concrete Pour Record.
label | Method - Test
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Concrete Tester, Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.10 - Concrete Testing - Slump
label | Reference - 703.11 Melbourne Water 7251/08/420
label | Acceptance Criteria - Slump testing tolerances =
label | <60mm = ±10mm
label | ≥60mm to ≤80mm = ±15mm
label | >80mm to ≤110mm = ±20mm
label | >110mm to ≤150mm = ±30mm
label | >150mm = ±40mm
label | Record: Required information on the Concrete Pour Record.
label | Method - Test
label | Frequency - Each sample
label | Category - IP
label | Responsibility - Concrete Tester
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.11 - Concrete Testing - Compressive Strength Cylinders
label | Reference - 703.11
label | Acceptance Criteria - Correct quantity of cylinders manufactured per sample.
label | Record: Required information on the Concrete Pour Record.
label | Method - Test
label | Frequency - Each sample
label | Category - IP
label | Responsibility - Concrete Tester
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.12 - Supply & Discharge Rates
label | Reference - 703.08, AS1379 Clause 4.4.1, AS1379 Clause 4.2.3, AS1379 Clause 4.2.5
label | Acceptance Criteria - Concrete is supplied at an adequate rate to ensure no cold joints are formed.
label | ○ Maximum elapsed time for discharge (including compaction) is 90 minutes from batching.
label | ○ Concrete that stiffens or is showing signs of stiffening shall not be used.
label | ○ If water is added once discharge commences, the volume shall not exceed the water-cement ratio for the mix design and the water volume is recorded on the concrete pour record.
label | Record: Required information on the Concrete Pour Record.
label | Method - Measure, Visual
label | Frequency - Each load
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.13 - Placement & Compaction
label | Reference - 703.08 Melbourne Water 7251/08/420
label | Acceptance Criteria - All concrete batches are traceable.
label | ○ Where concrete pumps are used, the initial discharge is pumped to waste until a consistent workable mix is discharged.
label | ○ Fresh concrete shall not be placed against concrete which has taken its initial set, except at properly formed construction joints.
label | ○ Concrete shall be thoroughly compacted by means of continuous tamping and internal vibration and shall be worked around any embedments and into corners of formwork or excavations to produce a dense concrete free from voids, honeycombing, segregation or surface defects.
label | ○ Vibration continued at each point until air bubbles cease to emerge from the concrete.
label | ○ Unformed surfaces shall be hand tamped to ensure a smooth surface with a uniform colour and appearance, and screeded to achieve the specified level, dimensions, falls and tolerances.
label | Record: Required information on the Concrete Pour Record.
label | Attach: Concrete Pour Record
label | Attach: Concrete Dockets
label | Method - Visual
label | Frequency - Each load
label | Category - SP
label | Responsibility - Foreman, SE/PE/SPE
date | Date Completed:
checkpoint | 4.14 - Surface Finishes
label | Reference - IFC Drawings Melbourne Water 7251/08/420 703.25
label | Acceptance Criteria - Surface finish shall be as per the drawings or; as a minimum, finished to grade and cross section with a wooden float to produce a lightly textured non-skid surface.
label | ○ All outside edges of slabs and all joints shall be finished with a suitable edging tool.
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.15 - Marking of Conduit Locations
label | Reference - IFC Drawings Relevant Council Drawings 703.28
label | Acceptance Criteria - The positions of any existing conduits passing under edgings shall be marked by a chase in the edging immediately above the conduit together with the nominated identification mark shown on the drawings.
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.16 - Crack-control Joints / Weaken Plane Joints
label | Reference - IFC Drawings Relevant Council Drawings 703.26 (b) (ii)
label | Acceptance Criteria - Crack-control joints shall be finished with a suitable edging tool, full-width of the pavement to the required depth and locations and/or longitudinal spacings as shown on the drawings.
label | Method - Visual
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.17 - Curing
label | Reference - 703.10 Melbourne Water 7251/08/420
label | Acceptance Criteria - The curing of exposed concrete surfaces shall commence immediately after finishing operations are progressively completed either by water curing, wet hessian, polyethylene sheeting which is adequately sealed, curing compound or a combination of these.
label | ○ Where curing compounds are used, 2 coats of the shall be applied in accordance with the manufacturer's TDS.
label | ○ The curing membrane shall be maintained intact for not less than the specified period of curing. Any damage to the curing membrane during the period of curing shall be repaired immediately at the original rate of application
label | ○ Curing shall continue uninterrupted for a period of not less than 7 days after placing the concrete, or 3 days for concrete edgings.
label | ○ Freshly finished exposed concrete surfaces shall be effectively protected from rain or damage from other sources, until hard set has occurred.
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
section | 5. Post-construction Activities
checkpoint | 5.1 - Protection of Newly Poured Concrete
label | Reference - 703.27
label | Acceptance Criteria - All concrete shall be protected from damage from early loading by pedestrians, animals, vehicles and from rain or any other cause.
label | ○ Suitable flagging, signage or bunding shall be erected to prevent vehicles from crossing over residential and/or commercial vehicle crossings a minimum of four days after completion of casting of the concrete. Vehicles greater than 1.5 tonnes may be permitted to cross after 7 days.
label | Method - Visual
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.2 - Stripping Formwork
label | Reference - 703.12 AS3610
label | Acceptance Criteria - Formwork shall not be stripped until the minimum times have elapsed from the time of completion of the placing of concrete:
label | i. 2 days for vertical formwork on external surfaces; and
label | ii. 1 day for vertical forms on permanently hidden surfaces
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.3 - Backfilling & Pavement Restoration
label | Reference - 703.29
label | Acceptance Criteria - At no earlier than 3 days after concrete placement, topsoil material shall be placed and firmly compacted in layers not exceeding 150 mm in thickness and to a width not less than 300 mm behind the edging to the top of the edging.
label | Method - Visual, Measure
label | Frequency - Each lot
label | Category - IP
label | Responsibility - Foreman, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.4 - Surface Inspection - Cracks
label | Reference - 703.3
label | Acceptance Criteria - No cracks greater than 0.2mm. If cracking greater than this is observed follow Structural Concrete Crack Repair ITP for investigation and repair.
label | Method - Visual, Measure
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.5 - Surface Inspection - Surface Finish
label | Reference - IFC Drawings Melbourne Water 7251/08/420 703.25, 703.10 (a) AS3610 Clause 3.2
label | Acceptance Criteria - After finishing, all work shall present a consistently neat appearance of uniform colour.
label | ○ All edges shall be sharp and clean and bullnoses shall be regular and of uniform radius.
label | Class of finish:
label | Permanently hidden surfaces = Class 4
label | All other surfaces = Class 3
label | ○ At the end of the curing period, concrete paving and shared user paths shall provide a dense, hard wearing surface.
label | ○ Where surface finishes are non-conforming follow Structural Concrete Patch Repair ITP for investigation and repair.
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.6 - Compressive Strength Test Results
label | Reference - IFC Drawings Melbourne Water 7251/08/420 703.11 Table 703.111
label | Acceptance Criteria - 28 day compressive strength (average of the 2 no. cylinders) per sample comply with the design strength.
label | Note: 1 of the 2 no. 28 day cylinders per sample may be as low as 90% of the required strength, so long as the average meets the required strength.
label | Attach: Compressive Strength Test Results
label | Method - Document Review
label | Frequency - Each cylinder
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.7 - As-built Survey
label | Reference - IFC Drawings 703.15
label | Acceptance Criteria - Provide record of dimensional measurements to demonstrate that all Works meet level and location requirements within the tolerances below:
label | Departure from RL = ±10mm
label | Departure from alinment = ±10mm
label | Rate of change of deviation from RL or alignment = 10mm in 10m
label | Irregularities in alignment = 5mm in 3m
label | Section dimensions = ±5mm
label | Section dimensions (less than 25mm) = ±3mm
label | Width of pavement = -5mm, +15mm
label | ○ Where median surfacings are to be constructed between edge sections of the same level, paving shall be crowned to produce a crossfall between 1% and 3% towards the edges.
label | Attach: Survey As-builts / Survey Report
label | Method - Document Review
label | Frequency - Where applicable, each lot
label | Category - IP
label | Responsibility - Surveyor, SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 5.8 - Non-conformance Report (NCR) Closure
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in CAMs.
label | Method - Document Review
label | Frequency - Once, prior to closure of this lot / element / Work area
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed above have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
text | Name:
text | Position:
date | Date Completed:
holdpoint | Sign ITP