## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Installation of FSMH | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawing C4400 or aggreed with the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/SP/QE
signoff | HOLD POINT
checkpoint | 3.3 - Backfill / Bedding Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
note | Acceptance Criteria - As per DCC code of subdiviison 10329
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4400
note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
note | ○ Floor of Trench to be even across width and length
note | Acceptance Criteria - As per 561467-TW-04-DRW-02
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - Minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - Visual, On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Bedding
note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
note | Acceptance Criteria - Bedding to comply with requirements
note | Verifying Document - Photo
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Measurement Check
note | Inspection: Key - C
note | Inspection: By (Role Key) - QE/SP
checkpoint | 4.4 - MH Installation
note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
note | Acceptance Criteria - Final levels are in accordance with the C4400 or within tolerance and agreed with the Engineer
note | Verifying Document - Photos, As-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.5 - Benching
note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
note | ○ Benching shape to have smooth transitions at bends and junctions
note | Acceptance Criteria - Benching built up to the specifications
note | Verifying Document - Photos
note | Frequency - During benching contruction
note | Inspection Type (Visual, other) - Visual, Test Results
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
note | Verifying Document - Photos, test records
note | Frequency - For every manhole
note | Inspection Type (Visual, other) - Test, visual
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After installation of FSMH
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of PVC FS Pipe - 150 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
note | ○ Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket,
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/QE/PE/CR
signoff | HOLD POINT
checkpoint | 3.3 - Backfill Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
note | Acceptance Criteria - As per DCC code of subdiviison 10324
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4400
note | ○ Floor of trench to be even across width and length
note | Acceptance Criteria - Allow 100mm for bedding
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE/CM
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Install Pipe
note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4400
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.4 - Laterals connections and installation
note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4410
note | Acceptance Criteria - – Lateral connection as per drawing C4410 and DCC standard details and project specs.
note | Verifying Document - Photos, measurement checks
note | Frequency - Every Lateral
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.5 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
note | Acceptance Criteria - min 100mm bedding
note | ○ 100mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, measurement check
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - CCTV
note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
note | ○ Dips or ponding of water inside the pipe
note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
note | Verifying Document - Test Records, CCTV footage
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Leak testing
note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - Test Records
note | Frequency - Every section of pipe installed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.3 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After completion of pipe section
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of PVC SW pipe - 300 zone 5 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
note | ○ Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket,
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/QE/PE/CR
signoff | HOLD POINT
checkpoint | 3.3 - Backfill Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
note | Acceptance Criteria - As per DCC code of subdiviison 10324
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4300
note | ○ Floor of trench to be even across width and length
note | Acceptance Criteria - As per 561467-TW-04-DRW-02
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By (Role Key) - SP/QE/CM
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Install Pipe
note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4300
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.4 - Laterals connections and installation
note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
note | Verifying Document - Photos, measurement checks
note | Frequency - Every Lateral
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.5 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
note | Acceptance Criteria - min 100mm bedding
note | ○ 100mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, measurement check
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - CCTV
note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
note | ○ Dips or ponding of water inside the pipe
note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
note | Verifying Document - Test Records, CCTV footage
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Leak testing
note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - Test Records
note | Frequency - Every section of pipe installed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.3 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After completion of pipe section
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of PVC SW pipe - 300 zone 6 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
note | ○ Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket,
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/QE/PE/CR
signoff | HOLD POINT
checkpoint | 3.3 - Backfill Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
note | Acceptance Criteria - As per DCC code of subdiviison 10324
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4301
note | ○ Floor of trench to be even across width and length
note | Acceptance Criteria - As per 561467-TW-04-DRW-02
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By (Role Key) - SP/QE/CM
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Install Pipe
note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4301
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.4 - Laterals connections and installation
note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
note | Verifying Document - Photos, measurement checks
note | Frequency - Every Lateral
note | Inspection Type (Visual, other) - Visual, Survey
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.5 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
note | Acceptance Criteria - min 100mm bedding
note | ○ 100mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, measurement check
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - CCTV
note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
note | ○ Dips or ponding of water inside the pipe
note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
note | Verifying Document - Test Records, CCTV footage
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Leak testing
note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - Test Records
note | Frequency - Every section of pipe installed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.3 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After completion of pipe section
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of SW Manhole Zone 2 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawing C4200 or aggreed with the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/SP/QE
signoff | HOLD POINT
checkpoint | 3.3 - Backfill / Bedding Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
note | Acceptance Criteria - As per DCC code of subdiviison 10329
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
note | ○ Floor of Trench to be even across width and length
note | Acceptance Criteria - As per 561467-TW-04-DRW-002
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - Minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - Visual, On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Bedding
note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
note | Acceptance Criteria - Bedding to comply with requirements
note | Verifying Document - Photo
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Measurement Check
note | Inspection: Key - C
note | Inspection: By (Role Key) - QE/SP
checkpoint | 4.4 - MH Installation
note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
note | Verifying Document - Photos, As-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.5 - Benching
note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
note | ○ Benching shape to have smooth transitions at bends and junctions
note | Acceptance Criteria - Benching built up to the specifications
note | Verifying Document - Photos
note | Frequency - During benching contruction
note | Inspection Type (Visual, other) - Visual, Test Results
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
note | Verifying Document - Photos, test records
note | Frequency - For every manhole
note | Inspection Type (Visual, other) - Test, visual
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After installation of FSMH
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of SW Manhole Zone 5 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawing C4300 or aggreed with the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/SP/QE
signoff | HOLD POINT
checkpoint | 3.3 - Backfill / Bedding Material
note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
note | Acceptance Criteria - As per DCC code of subdiviison 10329
note | Verifying Document - Delivery dockets, photos
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4300
note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
note | ○ Floor of Trench to be even across width and length
note | Acceptance Criteria - As per 561467-TW-04-DRW-002
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - V
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.2 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - Minimum of 2 blows per 100mm
note | Verifying Document - Test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - Visual, On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.3 - Bedding
note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
note | Acceptance Criteria - Bedding to comply with requirements
note | Verifying Document - Photo
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, Measurement Check
note | Inspection: Key - C
note | Inspection: By (Role Key) - QE/SP
checkpoint | 4.4 - MH Installation
note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
note | Acceptance Criteria - Final levels are in accordance with the C4300 or within tolerance and agreed with the Engineer
note | Verifying Document - Photos, As-built
note | Frequency - During installation
note | Inspection Type (Visual, other) - Survey
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.5 - Benching
note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
note | ○ Benching shape to have smooth transitions at bends and junctions
note | Acceptance Criteria - Benching built up to the specifications
note | Verifying Document - Photos
note | Frequency - During benching contruction
note | Inspection Type (Visual, other) - Visual, Test Results
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - Leak Testing
note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
note | Verifying Document - Photos, test records
note | Frequency - For every manhole
note | Inspection Type (Visual, other) - Test, visual
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
note | Acceptance Criteria - Signed ITP
note | Verifying Document - Red pen markup drawings
note | Frequency - After installation of FSMH
note | Inspection Type (Visual, other) - Document
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM
signoff | HOLD POINT
checklist | Installation of RCRRJ SW pipe - 750 | itp
section | SECTION 3 - RECEIVING INSPECTIONS
checkpoint | 3.1 - Material Delivery
note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
note | ○ Items are approved as per contract specification
note | ○ DCC approved
note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
note | Frequency - On Delivery
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SV/QE
checkpoint | 3.2 - Set out
note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
note | Verifying Document - Survey marks, photos
note | Frequency - Prior to commencement of works
note | Inspection Type (Visual, other) - Visual, Instrumental
note | Inspection: Key - H
note | Inspection: By (Role Key) - SV/SP/QE/PE
signoff | HOLD POINT
section | SECTION 4 - IN-PROCESS INSPECTIONS
checkpoint | 4.1 - Trench Excavation
note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200
note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
note | ○ Floor of Trench to be even across width and length
note | Acceptance Criteria - Allow 100mm for bedding
note | ○ Allow for minimum cover of 750mm.
note | Verifying Document - Photos, measurement checks
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE/CM
checkpoint | 4.2 - Geotextile
note | Inspection Point: Quality Control Activity - Install Bidim A29 or approved equivalient around bedding, haunch, overlay zone and trench fill up to the subbase.
note | Acceptance Criteria - Geotextile not damged during pipe installation and backfilling
note | Verifying Document - photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.3 - Foundation
note | Inspection Point: Quality Control Activity - Scala tests on base of trench
note | Acceptance Criteria - minimum of 2 blows per 100mm
note | Verifying Document - test results
note | Frequency - During installation, per 20m
note | Inspection Type (Visual, other) - Visual, On site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
checkpoint | 4.4 - Install Pipe
note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
note | Acceptance Criteria - Pipe not damaged during installation
note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
note | Frequency - During installation
note | Inspection Type (Visual, other) - Visual, instrumental
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.5 - Embedment zone
note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
note | Acceptance Criteria - min 100mm bedding
note | ○ 150mm overlay
note | Verifying Document - Photos
note | Frequency - During Installation
note | Inspection Type (Visual, other) - Visual, measurement check
note | Inspection: Key - C
note | Inspection: By (Role Key) - SP/QE
checkpoint | 4.6 - Backfill and Compact
note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
note | ○ Compaction testing one test every two layers as required
note | ○ Conductive signal strip to be laid at 300mm above pipe
note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
note | Verifying Document - Photos, Compaction test results
note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
note | Inspection Type (Visual, other) - Visual, On Site test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE
signoff | HOLD POINT
section | SECTION 5 - FINAL INSPECTION AND HANDOVER
checkpoint | 5.1 - CCTV
note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
note | ○ Dips or ponding of water inside the pipe
note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
note | Verifying Document - Test Records, CCTV footage
note | Frequency - Every section of pipe completed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.2 - Leak Testing
note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - Test Records
note | Frequency - Every section of pipe installed
note | Inspection Type (Visual, other) - On-Site Test
note | Inspection: Key - H
note | Inspection: By (Role Key) - SP/QE/CM/CR
signoff | HOLD POINT
checkpoint | 5.3 - Red pen markups
note | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
note | Frequency - After completion of pipe section
note | Inspection Type (Visual, other) -
note | Inspection: By (Role Key) - SP/QE/CM
checkpoint | 5.4 - As built
note | Acceptance Criteria - Engineer Approval
note | Verifying Document - QA records
note | Frequency - at completion
note | Inspection Type (Visual, other) - Asbuilt drawings
note | Inspection: Key - H
note | Inspection: By (Role Key) - PE/PM/SV
signoff | HOLD POINT