## Table 1
WATER MAIN RETICULATION | [6 empty] | ITP No. CHA -02-ITP- WATERMAIN | [12 empty] | Inspection Key |  |  |  |  | Responsibilities
[20 empty] | C Check |  |  |  |  | PM Chadoak PM
[20 empty] | H Hold Point |  |  |  |  | LH Chadoak LH
Job Address: Calder level crossing removal Lot/Stage/Section | [19 empty] | I Inspection R Review S Subcontractor |  |  |  |  | SP Supervisor
V Visual
Verification
WP Witness Point
References: |  |  | WSA 03-2011-3.2 Project Risk Management Plan (PRMP) MRWA Standard Drawings | [16 empty] | Prepared By: Daniel Griffin Date 24/07/2023
Reviewed By: Date:
QM Approved for Use:
# | OPERATIONAL ACTIVITIES |  |  | PERFORMANCE CRITERIA | [9 empty] | INSPECTION or TEST by
|  |  |  | Specification |  |  | Acceptance Criteria |  |  |  | Test/ Inspection Frequency |  |  | Key |  |  | By |  |  | Record/ evidence |  |  |  | Signed Responsible Representative
1.0 PRELIMINARIES
1.1 | The current Water Authority Approved revision drawings are being used. including subcontractors’ copy | [5 empty] | Current revision drawings are being used, ensure drawings have been Issued as IFC |  |  |  | Each Lot |  |  | R |  |  | PM SP |  |  | This ITP signed
1.2 | Applicable Permits obtained (includes Excavation Permits, BYD, Road Opening Permits, YVW Approvals & etc.) |  |  | Design Drawings (Refer to General Notes & Legend) |  |  | Permits obtained prior to demolition or construction from the relevant authorities |  |  |  | Before job start |  |  | R |  |  | PM SP |  |  | This ITP signed
1.3 | Check pipeline material’s compliances |  |  | Design Drawings WSA 03-2011-3.2 Section 12.1 |  |  | Use only products and materials specified by the Project Specification, Design Drawings or as approved by the Water Agency |  |  |  | Before job start |  |  | R |  |  | PM |  |  | Material Certificates
1.4 | Delivery and On-Site Storage of Pipes and Fittings |  |  | Manufactures Requirements WSA 03-2011-3.2 11.5.3.4 |  |  | Goods received satisfactory condition. Handled and stored in accordance with manufacturer’s recommendations. Pipes are clean and free of mud/debris. Pipe Ends to be capped prior to installation to avoid Debris entering Pipe |  |  |  | Each Delivery |  |  | R |  |  | PM |  |  | This ITP signed
1.5 | Delivery of Pipe Bedding and embedment |  |  | WSA 03-2011-3.2 14.2 |  |  | Material to comply with WSA requirements. Material from an approved quarry From the Approved Products List |  |  |  | Each Delivery |  |  | R |  |  | PM |  |  | Material Certificates
1.6 | Site Set out Survey |  |  | Design Drawings |  |  | Confirm extent of works and ensure all services are pegged/marked. Clearly labelled offset pegs indicating chainage and depth to invert. Ensure survey set out is to latest revision of drawings |  |  |  | Before job start |  |  | R |  |  | PM |  |  | Survey Pegs, records
2 |  | EXCAVATION (TRENCHING)
2.1 |  | Excavate Topsoil within Clearing Limits |  |  | WSA 03-2011-3.2 13.12 |  |  | Prior to excavating trenches, remove topsoil within the width of the Formation to a depth of 150mm |  |  |  | As required |  |  | SP | [5 empty] | ITR-W- 02
2.2 |  | Excavate to required Width and Depth |  |  | WSA 03-2011-3.2 13.9.1 MRWA-W-202 |  |  | 1. Keep sides of the excavation vertical to at least 150 above the pipes in strata other than sand. 2. Lay marking tape along route of the water main as per WSA03- 2012, MRWA edition. 3. Maintain minimum clearances between mains and services in accordance with Table. 5.5 of MRWA edition of WSA 03-2011. 4. Excessive excavation to be treated in accordance with MRWA edition of WSA 03- 2011. 5. Lay pipes in a shared trench at the same invert level where possible. 6. Maximum cover is 1.5 x minimum cover. This does not apply where main crosses under other services. 7. Cross water mains above other services (except Gas) wherever practical. When water mains pass under other services or obstructions, clearance under the obstruction or other service shall be. minimised. |  |  |  | Each Trench |  |  | SP/CR (WP) | [5 empty] | ITR-W- 02
2.3 |  | Ensure pipe work is installed as per Minimum cover requirements |  |  | MRWA-W-210 |  |  | As per Table 210-A - Railway 1600mm - Waterways 1000mm - Tramways 1200mm Major Roads 1200mm | [6 empty] | SP
3.0 PIPE INSTALLATION AND JOINTING
3.1 |  | Pipe laying – Confirm Levels |  |  | WSA 03-2011-3.2 Section 15 MRWA-W- 202 |  |  | Pipes are laid to levels, grade, and alignment as per drawings Tolerances: ±100mm lateral ± 50mm vertical |  |  |  | Each Pipe Section |  |  | SP/CR (IP) |  |  | SP (WP) |  |  |  | ITR-W-03
3.2 |  | Pipe Joint – Deflection |  |  | As per applicable Design drawings. |  |  | Joint deflection shall not exceed the maximum permitted deflection as recommended by the manufacturer. |  |  |  | Each Joint |  |  | SP/CR (IP) |  |  | SP (WP) |  |  |  | ITR-W-03
WSA 03-2011-3.2 Section 15.2
3.3 |  | Pipe & Fittings Jointing |  |  | WSA 03-2011-3.2 15.1.4 |  |  | Pipe to be installed as per manufacturers. requirements. |  |  |  | Every Joint |  |  | SP/CR (IP) | [6 empty] | ITR-W-03
[5 empty] | MRWA-W-103 |  |  | Pipes to have Witness mark and correct chamfer angle.
3.4 |  | Installation of valves, air valves & hydrants |  |  | WSA 03-2011-3.2 Section 15.4 MRWA-W- 109, 205A, 300, 301, 302, 303, 304, 305, 307 and MRWA- W-308 |  |  | Ensure fittings are installed as per specification |  |  |  | Every valve and fitting |  |  | SP/CR (IP) | [6 empty] | ITR-W-03
3.5 |  | Thrust and Anchor Blocks |  |  | WSA 03-2011-3.2 Section 15.7 MRWA-W- 104A, 104B, 204, 205A, 205B, 205C, 206, and MRWA-W207 |  |  | Ensure anchor blocks are constructed to WSA Standard Drawing WAT 1205 Concrete to be approved supplier |  |  |  | Every valve and fitting |  |  | SP/CR (IP) | [6 empty] | ITR-W-03
3.7 |  | PE BUTT WELDING |  |  | MRWA 15.21.2 |  |  | All joints for polyethylene mains and fittings are to be butt welded in accordance with MRWA. 15.21.2. Electrofusion welds and fittings are not permitted for use without the express written permission of YVW inspector. Butt welding equipment shall be inspected, tested, tagged, and calibrated every 12 months by an approved agent, and be subject to electrical equipment inspection test in accordance with AS/NZS 3760. Before commencing a welding operation, the operator shall check the machine as per manufacturer’s instructions, and the electrical cord shall not be damaged and check electrical test tag. Conduct visual inspection of weld. Check:  beads are same size and shape.  beads are projected evenly around diameter of pipe.  beads are acceptable height.  no cracks or obvious faults in beads Note: Randomly selected welds from pipeline should be removed and tested during operations. Control static electricity build-up/discharge:  wet entire exposed pipe surface (use anti-static liquid or dilute soap and water)  wrap exposed pipe with wet tape conductors (or similar)  Re-wet as needed. | [6 empty] | SP/CR (IP) | [5 empty] | Poly Weld Joint Report – WSA- ITR- W-03
4.0. Backfill and Compaction
4.1 |  | Embedment |  |  | WSA 03-2011-3.2 Section 16 Table 19.1 MRWA-W-200, 201, 202, & MRWA-W-203 MRWA Backfill Specification Design Drawings |  |  | Material to be worked around pipe to ensure all voids at haunches are filled. Standard compaction test as nominated on the design drawings |  |  |  | 1 Test at Start of Works |  |  | SP (WP) |  |  | WR (WP) |  |  | ITR-W-04 NATA Test Sheet
4.2 |  | Backfill Material |  |  | WSA 03-2011-3.2 Section 17 Dwgs MRWA-W- 200, 201, 202, & MRWA-W-203 |  |  | Non-Pavement - Backfilled using select backfill material. Pavement - Backfilled using 20mm Class 2 CR to underside of road preparation. - Approved Materials to be used |  |  |  | Each Lot |  |  | SP/CR (WP) | [5 empty] | ITR-W-04
4.3 |  | Backfill Compaction |  |  | WSA 03-2011-3.2 Section 16 Table 19.1 Dwgs MRWA-W- 200, 201, 202, & MRWA-W-203 MRWA Backfill Specification Design Drawings |  |  | Material to be compacted in layers as specified. Standard compaction test as nominated on the design drawings |  |  |  | Tests determined by length of section and depth |  |  | SP/CR (WP) |  |  | WR (WP) |  |  | ITR-W-04
4.4 |  | Detectable Marking Tape |  |  | WSA 03 2011 Section 15.12 |  |  | Install detectable marking tape on top of the first compacted backfill layer of all water mains constructed using open-cut. trenching |  |  |  | Entire pipeline length |  |  | SP/CR (IP) | [5 empty] | ITR-W-04
5.0 OTHER ITEMS
5.1 |  | Marker Posts |  |  | WSA 03 2011-3.2 Section15.18 MRWA 300 |  |  | Provide location marker posts, plates, and other markings for the location of hydrants and valves as per drawings. |  |  |  | Each |  |  | SP/CR (WP) | [5 empty] | ITR-W-04
6.0 TESTING & REINSTATEMENT
6.1 |  | Swabbing of Mains |  |  | WSA 03 2011 3.2 Section 18.3 |  |  | Entire pipe network to be swabbed to remove any foreign matter. Swab mains as nominated on the Design Drawings. Ensure Foam swabs are numbered and sized to be flushed through the pipe in full, and two swabs are used. for each run. |  |  |  | As required |  |  | SP/CR (WP) | [6 empty] | ITR-W-07.1
6.2 |  | Flushing of Mains |  |  | WSA 03 2011 3.2 Section 18.3 |  |  | Mains to be flushed in sections through hydrants of washouts which can develop a velocity of 0.75m/s. Mains shall then be drained and filled slowly with clean potable. water |  |  |  | As required |  |  | SP/CR (IP) | [6 empty] | ITR-W-07.2
6.3 |  | Hydrostatic Testing Mains |  |  | WSA 03 2011 3.2 Section 19.4 MRWA 19.4.1.1 Design Drawings |  |  | Test Mains to nominated pressure on design drawings. Duration and allowable top up volume as per MRWA 19.4.1.1 Test pressures, durations and witnessing. recorded on record sheet |  |  |  | As required |  |  | SP/CR (HP) |  |  |  | WR/SP (HP) |  |  | ITR-W-07.3
6.4 |  | Reinstatement / Finished Surface Levels |  |  | WSA 03 2011 3.2 Section 21.4 |  |  | ±5 mm in road reserves, including sealed pavements. ±5 mm in trafficable, private properties +50 mm, -20 mm in non- trafficable areas |  |  |  | Each Lot |  |  | SP/CR (WP) | [6 empty] | ITR-W-07.4
6.5 |  | Disinfection |  |  | WSA 03 2011 3.2 Section 20.1 |  |  | Mains >225mm to be disinfected in accordance with the MRWA Water Quality Compliance Specification |  |  |  | Each Lot |  |  | SP/CR (WP) | [6 empty] | ITR-W-07.5
6.6 |  | Asset Recording |  |  | Design Drawings WSA 03-2011 3.2 Section 21 & 24 |  |  | As-Built survey data, prepared, collated and submitted |  |  |  | At completion of each section and the job |  |  | SP/CR (WP) | [6 empty] | As built Survey
Applicable Construction Checklists & Records to be scanned into Project File
Chadoak Pty Ltd, 168-188 Wellington Rd, Clayton, 3168, Vic, ABN: 46 005 063 249
WATER MAIN RETICULATION – TEST SHEET ITP NO. CHA-02-ITP-WATER MAIN
WATER MAINS INSTALLATION CERTIFICATE OF COMPLIANCE & CONFORMANCE This certificate of compliance has been issued as verification that the following inspections and tests have been completed in accordance with the associated inspection test plan, and the installation has been deemed. conforming and meets the quality control acceptance criteria prescribed
Project: Calder level crossing removal | [8 empty] | Work Location: Hillside Issue Date: 24/07/23
Inspection & Test Description | [5 empty] | Work Zone Inspected Tested |  |  |  | Measuring Equipment Identification Reference | [5 empty] | Foreman / Supervisor | [6 empty] | Signature |  |  |  | Date
Final Inspection Verification Inspections tests have been completed | [5 empty] | Foreman: | [6 empty] | Signature: | [12 empty] | Date:
Final Inspection Approval Inspections tests have been accepted | [5 empty] | Project Supervisor: | [6 empty] | Signature: | [12 empty] | Date:
Plumbing Industry Commission Certificate of Compliance issued for hydraulic installation | [5 empty] | Project Supervisor: | [6 empty] | Signature: | [12 empty] | Date: