## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist-sectioned | DS2672-ITP-S116 - Wall And Slab Installation - Rev 4 | itp |  |  |  | Yes | DS2672-ITP-S116 - Wall And Slab Installation - Rev 4 | 93a78a01-86f2-4551-9c67-5fd10b389d49
checkpoint-group | 5.04 Placement and Compaction of Fill General
checkpoint-status | 5.04.01 - Retaining Wall foundation Inspection
label | Acceptance / Conformance Criteria - Excavated natural ground in foundation area of retaining wall upgrade/extension works prior to placement of fill or concrete must be inspected by the Engineer prior to further work being carried out in the area.
label | Standard / Specification - 14AED/AD4-C - 030.3
label | Verifying Document - Hold Point Release
label | Frequency - 48 Hours Notice Prior to Each Occurrence
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-group | 8.01 Concrete Subgrade Preparation
checkpoint-status | 8.01.01 - Wall Type 1 Subgrade Preparation
label | Acceptance / Conformance Criteria - Concrete of the existing dam surface to be water blast cleaned and roughened to provide NZS3109 Type B Construction Joint.
label | Standard / Specification - RSV - GS - 1.1
label | Verifying Document - Approved Surface
label | Frequency - Prior to Pour
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 8.01.02 - Wall Type 2 Subgrade Preparation
label | Acceptance / Conformance Criteria - Existing concrete under and to the sides of the foundation to be thoroughly water blasted back to sound concrete.
label | Standard / Specification - RSV - GS - 1.1
label | Verifying Document - Approved Surface
label | Frequency - Prior to Pour
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 8.01.03 - Wall Type 3 & 4 Subgrade Preparation
label | Acceptance / Conformance Criteria - Any soft soil or silts to be removed from site and subgrade to be inspected. Fill to underside of foundation with AP40 or approved fill. Fill to be compacted in 200mm layers.
label | Standard / Specification - RSV - GS - 1.1
label | Verifying Document - Approved Subgrade
label | Frequency - Prior to Pour
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 8.01.04 - Return Wall Subgrade Preparation
label | Acceptance / Conformance Criteria - Ground excavated to footing level. Backfill as required with AP40 or approved fill. Fill to be compacted in 200mm layers.
label | Standard / Specification - RSV - GS - 1.1
label | Verifying Document - Approved Backfill
label | Frequency - Prior to Pour
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-group | 8.02 Concrete Pour (Pre Pour Checksheet)
checkpoint-status | 8.02.01 - Construction Joint Locations
label | Acceptance / Conformance Criteria - Proposed location of construction joints to be submitted to the engineer for review prior to concrete pour.
label | Standard / Specification - RSV - CS - 1.15
label | Verifying Document - Site Records
label | Frequency - Prior to Pour
label | Activity - R
label | By - SE
checkpoint-status | 8.02.02 - Grouting of Bars
label | Acceptance / Conformance Criteria - Reinforcement installed into existing concrete shall be epoxied into the cured concrete with Hilti HIT RE 500 V3 epoxy mortar to the depth shown on the drawings and all strictly installed to the manufacturers written instructions.
label | Standard / Specification - RSV - CS - 1.18
label | Verifying Document - Photos
label | Frequency - Prior to Pour
label | Activity - R
label | By - SE
checkpoint-status | 8.02.04 - Pre-Pour Inspections
label | Acceptance / Conformance Criteria - Pouring of any concrete must be inspected by the Engineer prior to further work being carried out in the area with a signed pre pour checksheet attahced.
label | Standard / Specification - P&G 14
label | Verifying Document - Pre Pour Checksheet
label | Frequency - 48 Hours Notice Prior to Each Occurrence
label | Activity - HP
label | By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint-status | 8.02.05 - Delivery Dockets
label | Acceptance / Conformance Criteria - The delivery docket of each batch delivered certifying the mix designation, cement type, specified strength, slump, date, mixing time, water added during batching and maximum aggregate size.
label | Standard / Specification - RSV - CS - 1.9
label | Verifying Document - Dockets
label | Frequency - Each Pour
label | Activity - R
label | By - PE
checkpoint-status | 8.02.06 - Slump Testing
label | Acceptance / Conformance Criteria - Slump tests shall be taken for each delivery of concrete and the results recorded by the Contractor.
label | Standard / Specification - RSV - CS - 1.12
label | Verifying Document - Concrete Register
label | Frequency - Each Pour
label | Activity - R
label | By - PE
checkpoint-status | 8.02.07 - Compression Testing
label | Acceptance / Conformance Criteria - A set of specimens for concrete tests shall consist of four specimens from each major pour of concrete, one of which shall be tested at 7 days and the remaining three at 28 days after casting.
label | Standard / Specification - RSV - CS - 1.12
label | Verifying Document - Test Results
label | Frequency - Each Pour
label | Activity - R
label | By - PE
checkpoint-group | Concrete Pour (Post Pour Checksheet)
checkpoint-status | Post-Pour Inspection
label | Acceptance / Conformance Criteria - Conformation that the pour was acceptable and apporved by the Engineer
label | Verifying Document - Post Pour Checksheet
label | Frequency - Each Pour
label | Activity - R
label | By - SE