## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Pre-Sheet QA & Sign-Off |  |  |  |  | Yes | Fitout - Pre-Sheet ITP (Residential Prototype Room) | 1745646b-eb39-4be9-935d-41e8b80a63a9
checkpoint-group |  |  | section | Fire Walls (Corridor & Party Walls)
checkpoint-status |  |  | checkpoint | Electrical - Apps Electrical - Pass once below is completed
label | 9b9695ee-f99a-42e3-82a5-a7c02f1ac4a5 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 9304a7be-9391-48eb-9283-51362ce1e122 |  | button | Rough-in Complete | No,Yes
button | 97a17f3c-c8b5-48c1-b858-c914ce60d890 |  | button | Cutouts Marked | No,Yes
button | 3b225879-eb44-4601-8973-4d6c57ec36d2 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Joinery - Trendgosa
label | e5de6c70-aa57-419a-a525-f5f10fdf4b5e |  | note | Attach any comments/photos & ITP reports as applicable below
button | 8dda70b3-60d9-4dc0-8e06-474589ae675a |  | button | Noggins Marked Out | No,Yes
checkpoint-status |  |  | checkpoint | Sanitary Hardware - Casello
label | 06216be5-f1ba-4e08-9b70-bf6ab419d35f |  | note | Attach any comments/photos & ITP reports as applicable below
button | 3fe92fed-12ad-434a-b864-eb548c8614ec |  | button | Noggins Marked Out | No,Yes
checkpoint-status |  |  | checkpoint | Plasterboard - Expoconti
label | 4efa6788-8136-45f9-8dfe-6da44c5a6d8f |  | note | Attach any comments/photos & ITP reports as applicable below
button | 4c7043d4-a04b-4e77-aa81-ef34f23bd89c |  | button | All Noggins Installed (Incl. Shower Screen, TV & Laundry) | No,Yes
button | 9a7a48ff-b7a7-4066-b899-72b91eae0f40 |  | button | Fire Rating Complete | No,Yes
button | 908f86a0-0837-410e-9de6-5416f6dcd500 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Building Surveyor
label | 4799df32-0b11-4f37-a8c3-065a53da1d52 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 48b8c0d7-ec76-4174-8fe5-fe9dcc0ffbb1 |  | button | Inspection Completed - Attached below | Fail,Pass
label | b5341f39-3e58-4842-a4e1-7d2a253171c3 |  | note | If Fail, Comment/Photo remedial items below
checkpoint-status |  |  | checkpoint | MPX FINAL SIGN-OFF
label | 0ec4ff0e-d1f9-424c-842f-b3695fad17e1 |  | note | Attach any comments/photos as applicable below
button | 531fef06-cbf6-4beb-8abb-64a7bd1ee3ae |  | button | Each Subcontractor Has Signed Off Their Duties | No,Yes
button | 59c26d58-5474-4c42-bbc4-3e76237c6514 |  | button | The Wall Cavity is Clean & Tidy | No,Yes
button | 8eed369e-f954-4c91-b991-7c9820863a38 |  | button | No Fixings to Head Track or Between Stud & Top Track | No,Yes
label | 35972117-22a7-45d5-9861-0e516dfcbaf1 |  | note | Photos taken & Attached below
checkpoint-group |  |  | section | Internal Walls
checkpoint-status |  |  | checkpoint | Electrical - Apps Electrical - Pass once below is completed
label | 92a6e549-54d5-4cf8-949f-044d16204cfe |  | note | Attach any comments/photos & ITP reports as applicable below
button | dc4ae786-0a82-4df8-8dd7-730585823445 |  | button | Rough-in Complete/Fire Rating Complete | No,Yes
button | ed06b862-f9fe-43cf-b1c0-9f90e3d2f5c8 |  | button | Cutouts Marked | No,Yes
button | 7e4682c1-71b3-4566-b03e-f645b2d3d0e5 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Security/Comms/NBN - Expert/Apps Electrical
label | 0c293f76-f7e8-4288-ac66-c16707afb9fb |  | note | Attach any comments/photos & ITP reports as applicable below
button | 3dc60c89-54c7-4984-9bf7-92dcd7346fda |  | button | Rough-in Complete/Fire Rating Complete | No,Yes
button | f4904e1a-818e-485e-a902-4954e9535d56 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Hydraulic - CDC Plumbing
label | 918a7a47-586d-48f3-9e24-c7772038e691 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 7530c029-e245-4bd4-9697-3d0cf4ceebfc |  | button | Rough-in Complete/Fire Rating Complete | No,Yes
button | 8fb86c90-35d3-4e0b-afd2-a5565646a7bf |  | button | Noggins Marked Out | No,Yes
button | 32e877d4-69af-42cc-876c-73dcb41b3169 |  | button | Lagging Complete | No,Yes
button | 4da7842e-d4eb-448c-a856-225a073d062f |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Mechanical - Ellis Air
label | 9729b90b-895f-4aaf-8944-6edc19358537 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 4eb59737-26ba-431a-94ab-de969d516cda |  | button | Refrigeration Rough-In Complete | No,Yes
button | d0e52ce6-dd85-4311-bac8-f92884dc3ae5 |  | button | Noggins Marked Out | No,Yes
button | 3dbfbd46-3764-4897-ad7f-791580b0c20e |  | button | Lagging Complete | No,Yes
button | f73a977f-d774-414c-a7b7-e1115c2cf079 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Dry Fire - Jaycon
label | 281e217a-c0ca-4772-a5e8-f9adb2491f33 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 4126fd5f-7e7f-4819-b488-efdb2f993d34 |  | button | Rough-in Complete/Fire Rating Complete | Fail,Pass
button | 8870b900-f8da-4890-9ab4-be8177afcada |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Joinery - Trendgosa
label | 81648265-b208-4768-bf60-1ceba8625dd3 |  | note | Attach any comments/photos as applicable below
button | 39fbba3e-5656-4234-b4b0-109d5797cc2f |  | button | Noggins Marked Out | No,Yes
checkpoint-status |  |  | checkpoint | Sanitary Hardware - Casello
label | 75a07f8c-0d14-43c7-a52e-d1f9b9582e59 |  | note | Attach any comments/photos as applicable below
button | 6175097d-4107-489a-bc80-32a4218b0f4c |  | button | Noggins Marked Out | No,Yes
checkpoint-status |  |  | checkpoint | Plasterboard - Expoconti
label | f9d50a73-85a6-4319-80fa-9af8f07ce2a3 |  | note | Attach any comments/photos & ITP reports as applicable below
button | b2ed458c-1fa3-483c-b05a-cddb6c37bce2 |  | button | All Noggins Installed (Incl. Shower Screen, TV & Laundry) | No,Yes
button | 0961188b-66d5-4ad2-a77a-90ead0228c6c |  | button | Walls Do Not Deviate From Plane (bow) by More Than 4mm Within Any 2m Length of Wall | No,Yes
button | 81dd3395-3b2c-413d-b517-9728320091c9 |  | button | Gaps Beneath Plaster Sheets do Not Exceed 10mm in Bathrooms or Laundries | No,Yes
button | 45340657-b0c7-433b-b125-e7b878505256 |  | button | All Plastic Clips Installed As Required | No,Yes
checkpoint-status |  |  | checkpoint | MPX FINAL SIGN-OFF
label | 3917111a-2a24-4dbe-9afd-f759a3bb6eac |  | note | Attach any comments/photos as applicable below
button | 508497ea-f908-4ba5-a3bd-1c544a5a9d69 |  | button | Each Subcontractor Has Signed Off Their Duties | No,Yes
button | fa346136-74de-4d53-b7c2-b63dbd0c1c78 |  | button | The Wall Cavity is Clean & Tidy | No,Yes
button | c73eadd0-d440-46d7-a3f4-1c4ee697f4f0 |  | button | No Fixings to Head Track or Between Stud & Top Track | No,Yes
label | d00e060c-6c96-4d81-a636-51f4a09b1ab7 |  | note | Photos taken & Attached below
checkpoint-group |  |  | section | Ceilings
checkpoint-status |  |  | checkpoint | Electrical - Apps Electrical - Pass once below is completed
label | 80ef10c7-a2d1-482d-9953-164b01c1f887 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 83a83382-8629-471b-9e10-25586518f42f |  | button | Rough-in Complete | No,Yes
button | e6baa908-4de9-4e99-a406-5f4cf740081c |  | button | Fire Rating Around Patches in Party Walls | No,Yes
button | ce0a6ca4-45ee-4cb6-b900-0ea4382ff03d |  | button | Acoustic Rating Complete | No,Yes
button | 0eba48f9-4369-4f9e-87c7-8830fac224f3 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Hydraulic - CDC Plumbing
label | 90e1490f-1d06-45df-a2e9-f2ef8b8637dc |  | note | Attach any comments/photos & ITP reports as applicable below
button | 6b64f9f6-5c6a-4c17-a122-988b36c5e342 |  | button | Rough-in Complete | No,Yes
button | 46379452-58ce-4d8b-9663-89abca2ef9a1 |  | button | Lagging Complete | No,Yes
button | 7c685ba5-eda8-4b4b-afaa-323910530178 |  | button | Acoustic Rating Complete | No,Yes
button | 7306c794-5e99-443f-8a21-4c9d0f0dc32e |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Mechanical - Ellis Air
label | 98f3848b-2e3e-4bbe-8030-161930bcd3cc |  | note | Attach any comments/photos & ITP reports as applicable below
button | 471c5ac1-9759-4943-9dff-b9b371cd7ed0 |  | button | Refrigeration & Gas Rough-In Complete | No,Yes
button | ec14895f-1d32-48e0-811e-871a7966ab17 |  | button | Fire Damper Install Complete | No,Yes
button | 3800f852-e34f-499d-bcad-ec5be1a83385 |  | button | Noggins Marked Out | No,Yes
button | a4803b10-a0b0-4edc-b72e-675233c8cc88 |  | button | Acoustic Rating Complete | No,Yes
button | 2b13b0b4-c042-4275-9697-5967ed06bfc1 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Wet Fire - Geelong Fire
label | 88f065da-30ed-4c5a-a036-716d32e5bdaf |  | note | Attach any comments/photos & ITP reports as applicable below
button | 28358dcd-735c-4497-ac8f-879748a6f398 |  | button | Sprinkler Rough-in Complete | No,Yes
button | 8d0a6aa2-e944-4023-9987-8ad5ca93b1e4 |  | button | Pressure Test Complete | No,Yes
button | 6fe4d0f9-ac3a-45f5-97d3-0e9a75675e69 |  | button | Acoustic Rating Complete | No,Yes
button | 391f33ad-154f-4e8a-a385-ae81b22100c5 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Dry Fire - Jaycon
label | 81c3707a-ae66-497e-8325-2b63a721ed40 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 5025e34c-fef7-4fd5-9206-1282e0ca5ecb |  | button | Rough-in Complete | No,Yes
button | bbd1356f-9d1d-46f8-b9d3-67ffddf9bcc1 |  | button | Acoustic Rating Complete | No,Yes
button | bf63fcfb-a267-40f3-a7ca-74e3206e832e |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Security - Expert
label | f3449444-50fc-4445-b9c8-86fb881680e5 |  | note | Attach any comments/photos as applicable below
button | 5ae5a168-6d49-4b63-b1f1-ba9416850220 |  | button | Rough-In Complete | No,Yes
button | e8cb50a5-499d-4589-83bc-87bf81f27538 |  | button | Acoustic Rating Complete | No,Yes
button | 7f82dd78-8d06-4d6f-9831-b07e27bcd4dc |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | Plasterboard - Expoconti
label | 6b348692-ddd5-4352-a943-cb6e8f11d4b6 |  | note | Attach any comments/photos & ITP reports as applicable below
button | 23bd62bf-0957-45bf-9cc0-874d1071de3c |  | button | All Noggins Installed | No,Yes
button | 6a156da1-8919-4958-9567-a2415bb98ba4 |  | button | Fire Rating to Party Walls Complete & in Compliance With Supplier Requirements | No,Yes
button | f0808ec9-2df4-48d7-9353-b2ccda9fae8b |  | button | Ceiling Grid Position is Off-Set From Ceiling Services | No,Yes
button | 3b290a55-24c0-4147-b62e-65a3d87a13c6 |  | button | Access Panels Installed | No,Yes
button | 758656b5-b567-4da0-a5ba-db1f5a21fbc0 |  | button | Insulation Complete | No,Yes
button | 577b6bad-62d0-4703-8b2b-eec11074148c |  | button | Access Panel Openings Constructed | No,Yes
button | 5ad030ea-c09a-4881-857b-623a4c14e9e7 |  | button | All Installed as Per Manufacturer's Specification | No,Yes
button | 7e199524-1cd5-44b9-9921-e32cc58d83eb |  | button | Acoustic Rating Complete | No,Yes
button | 110fbdaa-cbd1-4db5-b25c-d6eec51fca13 |  | button | ITP Complete - Attached below as applicable | N/A, No,Yes
checkpoint-status |  |  | checkpoint | MPX FINAL SIGN-OFF
label | e45a1355-4db5-4565-98be-a941331d490b |  | note | Attach any comments/photos as applicable below
button | b4bf306b-804f-4331-8577-62510b2f5d83 |  | button | Each Subcontractor Has Signed Off Their Duties | No,Yes
button | 691295b5-0c5c-40c6-8055-a92139406bb5 |  | button | No Fixings to Head Track or Between Stud & Top Track | No,Yes
label | 091dbaa9-c2c3-4bc2-aa29-44191b3ebcf3 |  | note | Photos taken & Attached below
checklist-sectioned |  |  | checklist | MPX - Feature Precast Installation |  |  |  |  | Yes | MPX - Feature Precast Installation | 19376e39-5ad7-4bb4-b98e-d352c9c7b5a5
checkpoint-group |  |  | section | Acceptance / Installation
checkpoint-status |  |  | checkpoint | Subcontractor checklist Completed
label | c8569dd4-a77b-5b5c-84e8-119599ce0f1c |  | note | ITP Completed by precast manufacturer and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Birth Certificate received
label | 814d5755-51f6-575b-b81b-5da0c5f3ece9 |  | note | Attach a photo / upload
checkpoint-status |  |  | checkpoint | Accept Panel
label | 3183eb68-c33a-5499-8c7d-6c133434898c |  | note | Visual check - no cracks / damage to any face of the panel / attach photo
checkpoint-status |  |  | checkpoint | Edge lifter block out and baffle grooves
label | fb9c1a23-9f53-5bcc-9fd2-920b76afcb76 |  | note | Attach photos of all edge lifters and baffle grooves
checkpoint-status |  |  | checkpoint | Slab cast-ins clear of obstructions
label | d1411ccc-a146-58ed-96fb-127d349cbb24 |  | note | Attach photos of cast-ins
checkpoint-status |  |  | checkpoint | Marking plan / location of panel attached below
checkpoint-status |  |  | checkpoint | Packers / shims placed so as not to block the grout tubes
checkpoint-status |  |  | checkpoint | Panel bracket dowel pins aligned with slab cast-in bracket
label | 25db63ff-7106-59d7-9ac1-8a0494a7c0ec |  | note | If dowel has been cut or not provided on panel attach a photo
checkpoint-status |  |  | checkpoint | Panel installed - Correct alignment and plumb
checkpoint-status |  |  | checkpoint | Props installed as per propping design supplied by RBG - DWG Number
text | aed7ef47-16e8-5220-a641-f10024081610 |  | textbox | Drawing reference
text | b3c1a05f-1df8-5417-87c3-69ebe1cdd1de |  | textbox | Revision
checkpoint-status |  |  | checkpoint | Area clean - All debris removed
checkpoint-status |  |  | checkpoint | Form 700 Checklist received and complete
checkpoint-group |  |  | section | Bracket Grouting
checkpoint-status |  |  | checkpoint | Rectification of panel dowel pin completed
label | 8ea7d098-1986-5d32-a8cc-73ae7efd9267 |  | note | Attach a photo / upload
checkpoint-status |  |  | checkpoint | Area clean - Ensure area are bracket is clear of any debris
checkpoint-status |  |  | checkpoint | Dam installed around perimeter of precast element ensuring 10-15mm gap is maintained
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | e9fe6477-d973-58af-8d69-3ae66645db80 |  | textbox | Grout type
text | 1eca449f-f6b3-54e1-bde4-88d18c05d24a |  | textbox | Strength (Mpa)
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | Base filled with grout to top of dam
checkpoint-status |  |  | checkpoint | Grout samples taken
checkpoint-group |  |  | section | Tube Grouting
checkpoint-status |  |  | checkpoint | Confirm base is filled - no gaps and grout is cured
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | ccf9338a-6afb-54da-ba25-31bd2efcd653 |  | textbox | Grout type
text | b85052f9-fe39-56eb-8cfd-be48309e9728 |  | textbox | Strength (Mpa)
button | 33e6ce04-9eca-5c61-91e9-7f0ad38522e8 |  | button | Grout samples taken | Yes,No
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | All grout tubes are full using approximately the same amount of grout in each tube
checkpoint-group |  |  | section | Grout Strength
checkpoint-status |  |  | checkpoint | 28 day grout test result attached below
text | 2d064c08-0010-5b7d-b8a3-8f1539fd7f0e |  | textbox | Specified Strength
text | ca47e9f1-b768-5253-ae75-e61ad9e3f2ab |  | textbox | 28 day test result
checkpoint-group |  |  | section | Lateral Restraints
checkpoint-status |  |  | checkpoint | Confirm structural specification developed and design approved
checkpoint-status |  |  | checkpoint | Base of panel lateral restraint installed (10mm EA)
checkpoint-status |  |  | checkpoint | Soffit lateral restraint installed (20mm EA)
checkpoint-group |  |  | section | Stitch Plates
checkpoint-status |  |  | checkpoint | Confirm structural specification developed and design approved
checkpoint-status |  |  | checkpoint | Bolted stitch plates installed
checkpoint-status |  |  | checkpoint | Welding procedure developed and communicated to welders undertaking the work
checkpoint-status |  |  | checkpoint | All welders are certified and certificates provided
checkpoint-status |  |  | checkpoint | Welding works inspected and approved by supervisor / coordinator - name and signoff attached below
checkpoint-status |  |  | checkpoint | Weld inspection report received and attached below
checklist-sectioned |  |  | checklist | Pre Grid Ceilings |  |  |  |  | Yes | Pre Grid Install Ceilings | 22467b0e-a84f-4c8c-bf41-11d665ebaedd
checkpoint-group |  |  | section | Electrical - Apps Electrical - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | Access Panel / ceiling set out location marked
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Hydraulics - Planet Plumbing - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete including lagging to drains and pipes
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Access Panel locations marked and isolation valves accessible
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Mechanical - DE-ELLIS - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete including lagging to drains and pipes
checkpoint-status |  |  | checkpoint | All penetrations through fire rated / smoke /pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire dampers installed correctly and sealed and labeled
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Access Panel / ceiling set out location marked
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Medical Gas - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Pneumatic Piping - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Wet Fire - Contract Fire -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Ceiling set out marked
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | In ceiling sprinklers / detectors have been fitted off / spray pattern unobstructed
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Dry Fire - Jaycon -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Ceiling set out marked
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Security- Honeywell -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Data - SKS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Service separation to power verified
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Nurse Call - APPS Electrical-Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | AV - SKS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough in complete
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | TV support poles installed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Patient lifters- -Pass once below is completed
checkpoint-status |  |  | checkpoint | Patient lifter track / hanger system installed
checkpoint-status |  |  | checkpoint | Patient lifter track / hanger system load test completed and passed
checkpoint-status |  |  | checkpoint | Power supply correctly located
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Equipment pendants - Device technologies -Pass once below is completed
checkpoint-status |  |  | checkpoint | Pendant supports installed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Plaster - Express / Expo - Pass once below is completed
checkpoint-status |  |  | checkpoint | All penetrations through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | All walls caulked to slab and soffitt / joints and screws stopped
checkpoint-status |  |  | checkpoint | No screws in top track
checkpoint-status |  |  | checkpoint | Screws installed to correct centers as per specification to walls
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | MPX FINAL SIGN-OFF
checkpoint-status |  |  | checkpoint | All subcontractors signed off
checkpoint-status |  |  | checkpoint | Building Surveyor Fire Wall inspection complete
checkpoint-status |  |  | checkpoint | No Fixings to Head Track or Between Stud & Top Track
checkpoint-status |  |  | checkpoint | Photos taken of all walls prior to sheeting
holdpoint |  |  | signoff | MPX sign-off
checklist-sectioned |  |  | checklist | MPX - Precast Installation (V.130722) |  |  |  |  | Yes | ZSYS - MPX - Precast Installation (V.130722) [old version] | 23aeffad-6ed2-4f74-97ad-85e5b3560b50
checkpoint-group |  |  | section | Acceptance / Installation
checkpoint-status |  |  | checkpoint | Subcontractor checklist Completed
label | 228bab6b-b767-5322-bc10-cdcabdff75d3 |  | note | ITP Completed by precast manufacturer and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Birth Certificate received
label | 2512c625-4dbb-59c1-be68-e6c26e1b6a60 |  | note | Attach a photo / upload
checkpoint-status |  |  | checkpoint | Accept Panel
label | 5e9876ea-cca2-5dae-874d-0f5a6aeafad8 |  | note | Visual check - no cracks / damage to any face of the panel / attach photo
checkpoint-status |  |  | checkpoint | Grout tubes clear of obstructions
label | 8cf2e214-807e-5e28-90ca-40e066ad44e7 |  | note | Attach photos of grout tubes
checkpoint-status |  |  | checkpoint | Marking plan / location of panel attached below
checkpoint-status |  |  | checkpoint | Packers / shims placed so as not to block the grout tubes
checkpoint-status |  |  | checkpoint | Panel installed - Correct alignment and plumb
checkpoint-status |  |  | checkpoint | Props installed as per propping design supplied by RBG - DWG Number
text | 4b22e6ba-9493-5e9f-a501-e725c81cf56a |  | textbox | Drawing reference
text | 26def9b0-4c23-51bf-ac58-58295990d32d |  | textbox | Revision
checkpoint-status |  |  | checkpoint | Area clean - All debris removed
checkpoint-status |  |  | checkpoint | Form 700 Checklist received and complete
checkpoint-group |  |  | section | Base Grouting
checkpoint-status |  |  | checkpoint | Area clean - Ensure base of column is clear of any debris, lightly wet column base and blow-out excess water
checkpoint-status |  |  | checkpoint | Dam installed around perimeter of precast element ensuring 10-15mm gap is maintained
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | db8e1993-0fdf-5492-ad56-f4419111cec8 |  | textbox | Grout type
text | 8e8dbde0-7239-55b4-8b7e-31d6356053f3 |  | textbox | Strength (Mpa)
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | Base filled with grout to top of dam
checkpoint-status |  |  | checkpoint | Grout samples taken
checkpoint-group |  |  | section | Tube Grouting
checkpoint-status |  |  | checkpoint | Confirm base is filled - no gaps and grout is cured
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | c50f3321-6faf-5e81-8029-338ac601c4b7 |  | textbox | Grout type
text | e37425dd-93a5-57f0-a891-907465d52544 |  | textbox | Strength (Mpa)
button | 7d46080a-2a4b-540c-af6f-d1cc64b98d1b |  | button | Grout samples taken | Yes,No
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | All grout tubes are full using approximately the same amount of grout in each tube
checkpoint-group |  |  | section | Grout Strength
checkpoint-status |  |  | checkpoint | 28 day grout test result attached below
text | 1f93a3d0-6290-598e-9ab0-a29c9bd76183 |  | textbox | Specified Strength
text | 537e646a-a455-5ab7-923e-c5478de31fda |  | textbox | 28 day test result
checkpoint-group |  |  | section | Welding of Stitch Plates
checkpoint-status |  |  | checkpoint | Confirm structural specification developed and design approved
checkpoint-status |  |  | checkpoint | Welding procedure developed and communicated to welders undertaking the work
checkpoint-status |  |  | checkpoint | All welders are certified and certificates provided
checkpoint-status |  |  | checkpoint | Welding works inspected and approved by supervisor / coordinator - name and signoff attached below
checkpoint-status |  |  | checkpoint | Weld inspection report received and attached below
checklist-sectioned |  |  | checklist | Waterproofing (Level/Zone to be inputted here before adding checklist) |  |  |  |  | Yes | Ground Works - Waterproofing ITP (V.071021) | 2e8a2717-cc0d-443f-a303-d3a6eb492e84
checkpoint-group |  |  | section | Materials
checkpoint-status |  |  | checkpoint | Pass once details are confirmed/entered
text | 8c996384-14a6-510f-878c-232ee86107a2 |  | textbox | Primer
text | d1410a26-8ba1-5058-aed4-663f8a015973 |  | textbox | Membrane
select | 426b827d-bdd2-5933-87f7-029c7c4df1af |  | dropdown | Application | Roll On, Brush On, Spray On, Torch On, Other (Specify Below)
text | 32914380-a2a0-5e69-ae67-c49d044c7a18 |  | textbox | Other (Specify Here)
checkpoint-group |  |  | section | Substrate
checkpoint-status |  |  | checkpoint | Substrate Moisture checked and ready for installation
text | 85c4bb0b-d4e5-5366-95d3-38391357f613 |  | textbox | Moisture Content (%)
checkpoint-status |  |  | checkpoint | Slab curing time frame checked and referenced
text | 7e57342f-8aa3-509c-b946-840c5b9bfa35 |  | textbox | No. of days curing
checkpoint-status |  |  | checkpoint | Substrate clean of debris and slurry, substrate free of surface imperfections
label | 0985ae69-6e6b-59d4-bd3f-106f4c46338f |  | note | Check for Nails, Sawdust, honeycombing etc
label | 294e1d98-6b6d-5f3c-99e0-807e77c44df5 |  | note | Photos attached below
checkpoint-status |  |  | checkpoint | Bond Breakers installed to corners & expansion joints
label | b62a00af-0d20-552e-afc5-566066c34916 |  | note | Photos attached below
checkpoint-status |  |  | checkpoint | Cracks larger than 1.0mm are filled
label | 01a4d712-1835-5f16-bc3c-2cd9d7acbdef |  | note | Photos attached below
checkpoint-status |  |  | checkpoint | Primer installed and checked
label | d7abb455-5f99-590f-8ebd-cd557ca334a2 |  | note | Photos attached below
text | add8f23e-5879-5753-a35a-dfe13930b046 |  | textbox | No. of Coats
text | 8a42af10-9e51-58c0-9ee4-58c19f3c9643 |  | textbox | Thickness (mm)
checkpoint-status |  |  | checkpoint | Substrate prepared in accordance with the manufacturer's instructions & Area left clean/tidy
label | 8ac4071c-d06e-56aa-8fbf-d82b76fbeeb2 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
boolean | 6b87a6ee-0f67-5565-a29b-61f5394c1399 |  | tickbox | MPX USER to Attach manufacturer's instruction PDF Document below
button | da08263f-dea2-5c6d-850e-2b753e05425e |  | button | MPX Signature Sign-Off added below | Yes, No
button | 886e2487-4b52-5ecc-bbf9-742a9ad64670 |  | button | Subcontractor Signature Sign-Off added below | Yes, No
holdpoint |  |  | signoff | Request Subcontractor/3rd Party Sign-Off
checkpoint-group |  |  | section | Membrane
checkpoint-status |  |  | checkpoint | 1st Coat installed to Specifications / Drawings
text | 492452e5-edf3-5a32-865d-e691249af4bb |  | textbox | Application Time
text | 07c61082-d02f-52f8-a73d-a46e249a57cf |  | textbox | Date - If applicable
text | 408b098c-48b5-59d3-a304-0b064a16c39f |  | textbox | Thickness of Application - (WFT)
checkpoint-status |  |  | checkpoint | 2nd Coat installed to Specifications / Drawings
text | 3b4f4382-212b-5d06-a2d3-b8a6163481ca |  | textbox | Application Time
text | ce542dbb-138e-5ecd-be5e-257e99a9f445 |  | textbox | Date - If applicable
text | 00d34e74-c457-5ce4-bf5b-dc0cc9e49f5d |  | textbox | Thickness of Application - (WFT)
checkpoint-group |  |  | section | Testing
checkpoint-status |  |  | checkpoint | Adhesion test results checked and referenced
text | 5dd1890a-d768-5319-8a3c-81a7b4013323 |  | textbox | Adhesion (MPa)
checkpoint-status |  |  | checkpoint | Holiday Test completed
label | 2ef13405-97b6-5ffb-82d3-3e669b25ad13 |  | note | Photos attached below
checkpoint-status |  |  | checkpoint | Flood Test completed
text | 0bd4ae34-952b-5a77-b567-b438d8e41507 |  | textbox | Commencement Time
text | 9452470d-4f26-522a-a8d5-430af691d481 |  | textbox | Completion Time
label | f91c89a1-415b-54f9-9a3d-dc67d821b840 |  | note | Photos attached below
label | 1acfe30f-7ab1-5a0a-b055-ccd9c697693a |  | note | Membrane applied in accordance with the Manufacturer’s instructions
label | cadf291a-1130-570c-b77a-0f854b1d3737 |  | note | Records Obtained and reviewed, copy attached
checkpoint-group |  |  | section | Compliance & Sign-Off
checkpoint-status |  |  | checkpoint | Work(s) completed to specification/drawings & Area left clean/tidy
label | 7a0f18eb-e9e1-55cc-922f-691c18ff5ce5 |  | note | FINAL - Pass when happy to proceed with work(s) (Any issues please comment below)
label | bd8d2a0a-b20b-5504-9b84-d235dc124576 |  | note | Photos attached below of completed work as applicable
text | dc8c8821-47f7-51b8-adf6-7cbea06d72bc |  | textbox | Subcontractor Name
button | 571f93a8-fd6f-5ea8-b7e9-f23797d01e28 |  | button | Subcontractor Signature Sign-Off added below | Yes, No
button | 340e6f5b-6f7d-55c4-9706-0ff295dd682e |  | button | MPX Signature Sign-Off added below | Yes, No
holdpoint |  |  | signoff | Request Subcontractor/3rd Party Sign-Off
checklist-sectioned |  |  | checklist | Pre-Sheet Wall |  |  |  |  | Yes | Pre-Sheet Wall Sign-Off | 547ee3fa-2a6a-4346-aea2-949a69779a80
checkpoint-group |  |  | section | Electrical - Apps Electrical - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in Complete
checkpoint-status |  |  | checkpoint | Cutouts Marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | FR GPO boxes installed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Hydraulics - Planet Plumbing - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
checkpoint-status |  |  | checkpoint | Access panel / Valve box locations framed as marked
checkpoint-status |  |  | checkpoint | Lagging complete
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Mechanical - DE-ELLIS - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Noggins installed as marked
checkpoint-status |  |  | checkpoint | Access panel locations framed as marked
checkpoint-status |  |  | checkpoint | Lagging complete
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Medical Gas - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Access panel / Valve box locations framed as marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Pneumatic Piping - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Wet Fire - Contract Fire -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked (Fire extinguishers)
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Dry Fire - Jaycon -Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Security- Honeywell - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Fire rated boxes installed
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Data - SKS - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Fire rated boxes installed
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Nurse Call - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Fire rated boxes installed
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | AV - SKS - Pass once below is completed
checkpoint-status |  |  | checkpoint | Rough-in complete
checkpoint-status |  |  | checkpoint | Pressure boxes installed
checkpoint-status |  |  | checkpoint | Pressure box rough-in sealed
checkpoint-status |  |  | checkpoint | Fire rated boxes installed
checkpoint-status |  |  | checkpoint | Cut outs marked
checkpoint-status |  |  | checkpoint | Noggins installed as marked / TV support
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Joinery - GOSA/Jacaranda -Pass once below is completed
checkpoint-status |  |  | checkpoint | Noggins installed as marked
checkpoint-status |  |  | checkpoint | Cut outs framed as marked (mental health)
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Sanitary Hardware - Casello - Pass once below is completed
checkpoint-status |  |  | checkpoint | Cut outs framed as marked (mental health)
checkpoint-status |  |  | checkpoint | Noggins installed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Plaster - Expo / Express - Pass once below is completed
checkpoint-status |  |  | checkpoint | All rough-in complete
checkpoint-status |  |  | checkpoint | Studs installed @ correct centres (max 600mm) and framing noggins as per wall type
checkpoint-status |  |  | checkpoint | Wall cavity clean / no waste / vacuumed
checkpoint-status |  |  | checkpoint | No screws in head track
checkpoint-status |  |  | checkpoint | Secondary steel (walls) as marked - (drug safe / drop down rails / gun safes etc)
checkpoint-status |  |  | checkpoint | Door frames installed and filled when in fire rated wall
checkpoint-status |  |  | checkpoint | Special door openings framing and noggins for autoclosers etc
checkpoint-status |  |  | checkpoint | Insulation installed
holdpoint |  |  | signoff | Noggins installed as marked
checkpoint-no-status |  |  | checkpoint | Subcontractor presheet works complete (S/C to sign)
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | MPX FINAL SIGN-OFF
checkpoint-status |  |  | checkpoint | All services signed off
checkpoint-status |  |  | checkpoint | Wall cavity clean and free of any rubbish / dust
checkpoint-status |  |  | checkpoint | Photos taken of all walls prior to sheeting
holdpoint |  |  | signoff | MPX sign-off
checklist-flat |  |  | checklist | V-Column Grouting |  |  |  |  | Yes | V-Column Grouting | 549f1e9b-5881-4f09-b707-28afda596a0d
checkpoint-status |  |  | checkpoint | Verify base grouting complete (Photo)
checkpoint-status |  |  | checkpoint | Product verification SS Motor grout production date within 12 months (Photo of bag code)
checkpoint-status |  |  | checkpoint | Temperature range between 10-35 degrees as per manufactures requirements - record temperature
checkpoint-status |  |  | checkpoint | Grout mixing as per manufactures specification - xx litres of water per bag mixed for xx minutes
checkpoint-status |  |  | checkpoint | Pressure grout dowel bar tubes using pump on speed xx
checkpoint-status |  |  | checkpoint | Volume check - each grout tube filled with aproximately xx bags. Record any tube where volume is less than expected in comments below
checkpoint-status |  |  | checkpoint | Dry pack remaining ungrouted portion of grout tube and finish smooth (Photo)
checkpoint-status |  |  | checkpoint | Sample cubes taken
checklist-sectioned |  |  | checklist | Concrete Pour ITP |  |  |  |  | Yes | Ground Works - Concrete Pour ITP | 6b2e4d20-3848-4989-b87f-ebb180b086a9
checkpoint-group |  |  | section | Pour Details
checkpoint-status |  |  | checkpoint | Pour Details - Pass once entered
text | b6826331-f458-4148-93a5-1b54ebb4dae2 |  | textbox | Element
text | 2d7a3424-33ed-4589-a156-6eee6b9c2902 |  | textbox | Location of Pour
text | ff333482-61a5-434b-bc93-70d9538dc3c4 |  | textbox | Date of Pour
checkpoint-group |  |  | section | Pre-Pour Requirements
checkpoint-status |  |  | checkpoint | Reinforcement steel installation completed
label | 3a08c617-476d-4285-a5dc-d1968532d5cb |  | note | Inspected by Structural Engineer & corrective actions completed/signed-off
text | c94e1682-9719-4476-876d-26f7293cf611 |  | textbox | Inspection report Reference
checkpoint-status |  |  | checkpoint | Services penetrations Completed
label | c3e52771-6f6c-440e-b86e-feee2c428ad0 |  | note | Inspections completed for all slabs & walls - Drawing’s signed off by each of the services Sub-Contractor's
boolean | 4501cd86-e202-4943-a6bf-ba20ea39b140 |  | tickbox | Electrical Signature Sign-Off Attached below
boolean | b0d867bc-3a38-49bc-819c-302f16a28b83 |  | tickbox | Plumbing Signature Sign-Off Attached below
boolean | dfb63926-1ec4-443f-993c-baacd691a7e5 |  | tickbox | Wet Fire Signature Sign-Off Attached below
boolean | 89e58dc0-7b67-4ba8-99e7-0b3f3136b882 |  | tickbox | Dry Fire Signature Sign-Off Attached below
boolean | 01fcf046-76e7-443c-901f-9fa79ece6a43 |  | tickbox | Mechanical Signature Sign-Off Attached below
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts completed
label | 6caf09e3-acb8-4e56-871f-93e00a65c909 |  | note | Inspected by Sub-Contractor & ITP(s) Submitted
text | 347c52b6-a59b-423f-b531-965bd95afa42 |  | textbox | ITP/checklist Reference (Or attached below)
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-group |  |  | section | Approval to Pour
checkpoint-status |  |  | checkpoint | Approval to Pour - Pass Once Completed
text | 761aa95a-904a-45d4-a048-5e03defa88ad |  | textbox | Name
label | a7a8d74a-32e8-4149-ba22-8bc61ef0220b |  | note | Click to attach signature below
checkpoint-status |  |  | checkpoint | Concrete Supply - Delivery docket matches the Design Mix
text | 2cf51d2c-bbbd-46e2-82e8-77db5754800f |  | textbox | Design Mix
checkpoint-status |  |  | checkpoint | Placement of concrete around cast in items to be monitored by Multiplex and subcontractor supervision to ensure adequate compaction/ vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Collection of compressive testing samples and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - mud map established to indicate date and location of pour
checkpoint-group |  |  | section | Post-Pour Requirements
checkpoint-status |  |  | checkpoint | Class of finish checked
select | 6c97e9f2-6ef1-47dc-903d-ba599c4fbb9c |  | dropdown | Class | 1, 2, 3
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
text | e68ddaeb-66a1-4b68-a813-fb304d25b58a |  | textbox | Report Reference (Or attached below)
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
text | 164016bd-1dca-4c43-ae08-01bd8529a961 |  | textbox | Report Reference (Or attached below)
checkpoint-status |  |  | checkpoint | As Built Drawings – received from subcontractor
text | 5719002b-2267-44d7-82c2-72e08a457d38 |  | textbox | Drawing Reference (Or attached below)
checkpoint-status |  |  | checkpoint | Sign-Off - Pass once completed
text | 930ccc33-5261-4550-90c1-02f4789c8b0e |  | textbox | Completed by
label | a32ad028-171b-409e-bd22-b0a0cee7ef9d |  | note | Click to attach Signature below
checklist-sectioned |  |  | checklist | Pre Sheet Ceilings |  |  |  |  | Yes | Pre Sheet Install Ceilings | 6c209445-b611-4afc-98a0-ac7917d218a9
checkpoint-group |  |  | section | Electrical - Apps Electrical - Pass once below is completed
checkpoint-status |  |  | checkpoint | Ceiling fitting / rough-in complete and correctly located
checkpoint-status |  |  | checkpoint | Access Panel Openings Constructed and equipment is accessible
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Ceiling noggins installed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Hydraulics - Planet Plumbing - Pass once below is completed
checkpoint-status |  |  | checkpoint | All pipes connected
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Access Panel openings constructed and isolation valves accessible
checkpoint-status |  |  | checkpoint | Lagging complete to pipes and drains
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Mechanical - DE-ELLIS - Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling fit off complete
checkpoint-status |  |  | checkpoint | All penetrations through fire rated / smoke /pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire dampers installed correctly and sealed and labeled
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Access Panel Openings Constructed and equipment is accessible for servicing
checkpoint-status |  |  | checkpoint | Lagging complete to pipes
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Medical Gas - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling fit off complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Pneumatic Piping - DE-ELLIS -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling fit off complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Wet Fire - Contract Fire -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling sprinklers / detectors have been fitted off / spray pattern unobstructed
checkpoint-status |  |  | checkpoint | Fit off to ceiling grid complete
checkpoint-status |  |  | checkpoint | All pipes through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
checkpoint-status |  |  | checkpoint | Pressure test completed and passed
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Dry Fire - Jaycon -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling rough in complete and cables correctly located
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Security- Honeywell -Pass once below is completed
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Data - SKS -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling rough in complete and cables correctly located
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Nurse Call -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling rough in complete and cables correctly located
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | AV - SKS -Pass once below is completed
checkpoint-status |  |  | checkpoint | In ceiling rough in complete and cables correctly located
checkpoint-status |  |  | checkpoint | All cables through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | TV support poles / noggins installed
checkpoint-status |  |  | checkpoint | Fire rated penetrations have stickers, and photos taken
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Patient lifters- -Pass once below is completed
checkpoint-status |  |  | checkpoint | Patient lifter track / hanger system installed
checkpoint-status |  |  | checkpoint | Patient lifter track / hanger system load test completed and passed
checkpoint-status |  |  | checkpoint | Power supply correctly located
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Equipment pendants - Device Technologies -Pass once below is completed
checkpoint-status |  |  | checkpoint | Pendant supports clear of ceiling grid and level correct
checkpoint-status |  |  | checkpoint | Pendant services rough in complete (Power and Medical gas)
checkpoint-status |  |  | checkpoint | Framed opening in ceiling installed as per detail
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | Plaster - Express / Expo - Pass once below is completed
checkpoint-status |  |  | checkpoint | All penetrations through fire rated / smoke / pressurized walls are all sealed
checkpoint-status |  |  | checkpoint | All walls caulked to slab and soffitt / joints and screws stopped
checkpoint-status |  |  | checkpoint | Ceiling grid installed as per design
checkpoint-status |  |  | checkpoint | Thermal and acoustic insulation installed
checkpoint-status |  |  | checkpoint | Ceiling Grid frame is clear from Ceiling Services
checkpoint-status |  |  | checkpoint | Access Panel Openings Constructed as marked
holdpoint |  |  | signoff | Subcontractor presheet works complete (S/C to sign)
checkpoint-group |  |  | section | MPX FINAL SIGN-OFF
checkpoint-status |  |  | checkpoint | All subcontractors signed off
checkpoint-status |  |  | checkpoint | Photos taken of all ceiling system / services prior to sheeting
holdpoint |  |  | signoff | MPX sign-off
checklist-flat |  |  | checklist | Form 700 Column ITP upload |  |  |  |  | Yes | Form 700 Column ITP upload | 72e23dbb-4a32-4c47-8cf7-ddab869bd3e3
checkpoint-status |  |  | checkpoint | Form 700 Column ITP uploaded below
checklist-flat |  |  | checklist | Multiplex Column Concrete Pour ITP (V.132121) |  |  |  |  | Yes | ZSYS - Multiplex Column Concrete Pour ITP (V.132121) [old version 2] | 762155fd-abf6-4b9f-b24b-eeb034981931
checkpoint-status |  |  | checkpoint | Reinforcement installation - inspected by MPX
label | bbb22557-e123-5d22-b1bd-3dd3a53a02ad |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | 9831d89b-a9bc-5e6c-b2c4-f7ca4e5f63ad |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | 2842a63b-2ad2-5d1b-af0e-26e8acdc0c6e |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | a626a2ff-632b-5f95-9d64-fadaeeb5f222 |  | note | Mudmap attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | dde9c55b-cecf-55b9-8915-de5f84a8629e |  | note | Report attached below
checklist-flat |  |  | checklist | Concrete Infill |  |  |  |  | Yes | Concrete Infill Checklist | 7c9ca637-ff85-4a58-910f-403596bbc43c
checkpoint-status |  |  | checkpoint | Infill approval issued from Consultant group (CoxBLP, Stantec, HKI), attach relevant mark up.
checkpoint-status |  |  | checkpoint | Attach mudmap to show location of infil
checkpoint-status |  |  | checkpoint | Slab scabbled and primer applied
checkpoint-status |  |  | checkpoint | Services installed and accepted by APPS (Type name of Apps representative)
checkpoint-status |  |  | checkpoint | Starter bars pinned at 250mm centres extending approximately 250mm into void and minimum depthn of inbedment 100mm
checkpoint-status |  |  | checkpoint | Mesh installed and tied off prior to commencement of pour. Mesh layers overlapping at junction (approx. 200mm) Bar chairs installed to support mesh
checkpoint-status |  |  | checkpoint | Checklist complete and Approval to pour
checkpoint-status |  |  | checkpoint | Pour completed in accordance with approval
checklist-flat |  |  | checklist | Hole Coring Sign-off |  |  |  |  | Yes | Hole Coring Sign-off | 85963dd4-eb7c-40af-961c-092e7b3eb3ba
checkpoint-status |  |  | checkpoint | Coring permits issued and approved
label | c9642b78-b5c0-5182-bd09-36b9aeb3b137 |  | note | Attach copy of all permits issues
checkpoint-status |  |  | checkpoint | Location of cast in services identified and clear of core locations
button | abc3d65b-782c-5261-a3d5-ee91cb207190 |  | button | Confirm no cast in hydraulic services in core location | Pass,Fail,Note
button | 5eb9a3d4-4a5a-5027-9fe4-b59cf62b2117 |  | button | Confirm no cast in electrical services in core location | Pass,Fail,Note
checkpoint-status |  |  | checkpoint | Coring location inspected - both sides of slab and confirmed clear of any services / emf shielding
checklist-flat |  |  | checklist | Facade QAQC Checklist |  |  |  |  | Yes | Facade QAQC Checklist | 8ba199f4-e29c-45a5-aa62-cf3a073fadd8
checkpoint-status |  |  | checkpoint | Check for any visual defects (scratches, dents, marks, discolouration, oxidisation)
checkpoint-status |  |  | checkpoint | Ensure tek screws have been removed from panels prior to installation
checkpoint-status |  |  | checkpoint | Ensure there are no visible gaps in sealant, caulking and waterproofing components.
checkpoint-status |  |  | checkpoint | Ensure weep holes are present and are free of blockages
checkpoint-status |  |  | checkpoint | Ensure gaskets run the full length of the panel and are not cut, or falling away from the panel
checkpoint-status |  |  | checkpoint | Ensure no additional cuts have been made for lifting purposes and if so, remedial action has been implemented.
checkpoint-status |  |  | checkpoint | Torque testing of brackets are present once installed - photo of spray painted evidence
checkpoint-status |  |  | checkpoint | Gutter plate and sleeve installed in correct position and sealed
checkpoint-status |  |  | checkpoint | No loose items on panel that could come loose whilst lifting (i.E. Gutter sleeves, clip on extrusions, etc.)
checkpoint-status |  |  | checkpoint | Ensure end dams are present in areas adjoining other elements
checkpoint-status |  |  | checkpoint | Check for low-e coating glazing
checklist-flat |  |  | checklist | Hole Coring 125 |  |  |  |  | Yes | Hole Coring 125 | 9310d232-2410-4b69-803f-ce50a8823241
checkpoint-status |  |  | checkpoint | Confirm correct size of core hole for service penetration - 125mm
checkpoint-status |  |  | checkpoint | Hole coring complete in accordance with approval and sign-off
label | e49f7a28-561e-56f0-8a2c-ab6907f2a359 |  | note | Provide photo of each core and hole showing any reinforcement cut / no PT cut
checklist-flat |  |  | checklist | SYS - Calcs & Drawings Upload |  |  |  |  | Yes | ZSYS - Calcs & Drawings Upload [old version] | 979ceb7d-8313-4043-b036-86321b36c643
checkpoint-status |  |  | checkpoint | Calcs & Drawings uploaded
checklist-sectioned |  |  | checklist | MPX - Concrete Pour ITP |  |  |  |  | Yes | Structure - Concrete Pour ITP | 99288166-f0c0-4818-8dba-18a224a13b13
checkpoint-group |  |  | section | Pre-Pour
checkpoint-status |  |  | checkpoint | Subcontractor Slab Prepour Completed
label | 1d671d4c-93f5-5a1e-8b6e-a5d2ce89e27b |  | note | ITP Completed by Form700 and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Subcontractor PT Prepour
label | 47d4a5b4-8139-5e3c-b478-c0ab05a18bfd |  | note | ITP Completed by Postenco and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Reinforcement and Post Tensioning installation - inspected by MPX
label | 88ea856b-899d-5794-86fc-9bc5003d1ce5 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Services penetrations - Inspected for all slabs/walls and "CONQA-Service Penetrations Matrix" verified as passed off by each of the services subcontractors
label | 32b1b9b1-3c5e-558e-ae56-8250b3396bf2 |  | note | Markup attached as applicable
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - Confirmation of Form700 completed ITP
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - MPX Inspection of all elements
label | 3aa3db45-edc4-5435-ba49-807e2519e265 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement and Post Tensioning installation - Inspected by structural engineer and corrective actions completed and signed-off
label | 0dcd7c90-d2a4-5135-ac05-00d3151562b4 |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | e64e8b10-7113-5354-9c62-93b350cca0b1 |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Placement of concrete checked
label | 9b43f7c0-5f00-54fe-be04-0546cfa51a0c |  | note | Monitored by Multiplex and subcontractor supervision to ensure adequate compaction/vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | aeae06ec-ad9a-533c-b962-e6c38323bdbd |  | note | Mudmap attached below
checkpoint-group |  |  | section | Post-Pour
checkpoint-status |  |  | checkpoint | Curing – Application rate of approved curing compound being applied in accordance with manufacturers recommendations
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
label | cc34723b-53bb-549c-9946-c701c8abe053 |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | e7ba588b-ebe4-545e-a4be-861b148343f5 |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Stressing records – Postenco checklist reviewed including extensions
checkpoint-status |  |  | checkpoint | Stressing extensions – Postenco records reviewed by Stressing Engineer and approval to cut all strands has been received
label | 2b920319-de7d-578d-adaa-d04336cbb3a1 |  | note | Aconex reference linked/commented below
checkpoint-status |  |  | checkpoint | Grouting - Completed by Postenco and ITP reviewed
checkpoint-status |  |  | checkpoint | As Built Drawings – Review of Form700 as builts
label | 26114066-28e4-5600-adb9-ea712a3eb90a |  | note | Aconex reference linked/commented below
checklist-sectioned |  |  | checklist | Concrete Pour ITP |  |  |  |  | Yes | Concrete Pour ITP | 9a950b72-0283-4d17-8cf2-b2390642c993
checkpoint-group |  |  | section | Pre-Pour Requirements
checkpoint-status |  |  | checkpoint | Subcontractor Slab Prepour Completed
label | c4439f50-c651-5190-8aef-beb57b1967d5 |  | note | ITP Completed by Form700 (attach copy)
checkpoint-status |  |  | checkpoint | Reinforcement steel installation completed
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | 4a997351-e248-50df-bfad-695e1e23e7f8 |  | note | MANDATORY - Attach photos below of inspected elements
label | 83b8ae6c-7032-5b85-b274-d95c0d7bc70f |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | e94aa035-b8da-585e-9dd5-c99bc1538f49 |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
checkpoint-status |  |  | checkpoint | Services penetrations Completed
label | 2afc1834-7e68-56fe-a59c-1e906d338796 |  | note | All penetrations / services / conduits are installed and verified by subcontractor as per latest services drawing (Attach photo of title block showing revision)
boolean | bd5d0ccd-4e34-5f5c-a845-816c4a7751c7 |  | tickbox | Electrical Signature Sign-Off Attached below
boolean | 6a5bcab1-a971-50a9-ab33-f72b0b270f27 |  | tickbox | Plumbing Signature Sign-Off Attached below
boolean | fd78821b-609f-5a10-81ca-964e5b361f18 |  | tickbox | Kitchen Contractor Signature Sign-Off Attached below
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Concrete Supply - Delivery docket matches the Design Mix
text | c5f01ae7-5fb0-521d-a7eb-0d662971f1b1 |  | textbox | Design Mix
checkpoint-status |  |  | checkpoint | Placement of concrete around cast in items to be monitored by Multiplex and subcontractor supervision to ensure adequate compaction/ vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Collection of compressive testing samples and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Slump verified within tolerance as specified
text | 9022973f-1026-5b28-bc6e-ccaf36fcd524 |  | textbox | Enter measured slump
checkpoint-status |  |  | checkpoint | Concrete Traceability - mud map established to indicate date and location of pour
checkpoint-group |  |  | section | Post-Pour Requirements
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
text | f4a8f890-e36a-5f3a-84fb-94386c33cf68 |  | textbox | Report Reference (attached below)
checkpoint-status |  |  | checkpoint | As Built Drawings – received from subcontractor
text | 5d17d273-0ed7-53e9-aef5-d06a021056cf |  | textbox | Drawing Reference (Or attached below)
checklist-sectioned |  |  | checklist | Multiplex Stairs Concrete Pour ITP (V.132121) |  |  |  |  | Yes | Multiplex Stairs Concrete Pour ITP (V.132121) | b4522d88-8a30-4772-9343-ffe4639049fa
checkpoint-group |  |  | section | Pre-Pour
checkpoint-status |  |  | checkpoint | Subcontractor Stairs Prepour Completed
label | 2976cf97-aeb8-5bf2-a30a-9ff5a00db0b3 |  | note | ITP Completed by Form700 and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Reinforcement installation - inspected by MPX
label | 444fd6be-d0de-5612-808d-e25310272a95 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Services penetrations - Inspected for all slabs/walls and "CONQA-Service Penetrations Matrix" verified as passed off by each of the services subcontractors
label | f711af43-49e0-56b1-a006-003cd6152e31 |  | note | Markup attached as applicable
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - Confirmation of Form700 completed ITP
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - MPX Inspection of all elements
label | 1dee898f-31bd-55da-987b-4bff5e5de59f |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | 5a16536c-7daa-5502-88e6-a66fa1a0553e |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | 2425cd6d-44bd-5a53-ac85-fd425529361f |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Placement of concrete checked
label | 57528d7b-8166-5fde-ac33-19d8ac4cbd08 |  | note | Monitored by Multiplex and subcontractor supervision to ensure adequate compaction/vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | cfc1c895-3e98-54fa-ad8c-784d7a72364d |  | note | Mudmap attached below
checkpoint-group |  |  | section | Post-Pour
checkpoint-status |  |  | checkpoint | Curing – Application rate of approved curing compound being applied in accordance with manufacturers recommendations
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
label | be7cdea0-7909-570c-a7a9-bad7308233a4 |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | 54494dde-b552-57ad-b0f3-6d6843527c5a |  | note | Report attached below
checklist-sectioned |  |  | checklist | Multiplex Slab Concrete Pour ITP (V.132121) |  |  |  |  | Yes | Multiplex Slab Concrete Pour ITP (V.132121) | c1264f6f-7d8e-4498-916b-a194d687e530
checkpoint-group |  |  | section | Pre-Pour
checkpoint-status |  |  | checkpoint | Subcontractor Slab Prepour Completed
label | 845bd41b-2c0a-5a63-82b3-e15d8190fde6 |  | note | ITP Completed by Form700 and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Subcontractor PT Prepour
label | 1ac7bc8d-d32f-5fe1-9800-54bb74f57c2b |  | note | ITP Completed by Postenco and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Reinforcement and Post Tensioning installation - inspected by MPX
label | 4fa62fb8-3090-5c99-9d0a-55a533f36358 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Services penetrations - Inspected for all slabs/walls and "CONQA-Service Penetrations Matrix" verified as passed off by each of the services subcontractors
label | c7595e2d-16e3-56d6-b171-0db76ad52ba7 |  | note | Markup attached as applicable
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - Confirmation of Form700 completed ITP
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - MPX Inspection of all elements
label | 38140462-3f7d-56d5-9ec3-b71d2c1ac45e |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement and Post Tensioning installation - Inspected by structural engineer and corrective actions completed and signed-off
label | e84b3853-7173-5331-bcc9-52fea64c4373 |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | ec1a57c2-a65a-59d5-9a84-ccdeee42b83b |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Placement of concrete checked
label | 1ea876b9-d4ee-5beb-8dde-ca9e8f00468f |  | note | Monitored by Multiplex and subcontractor supervision to ensure adequate compaction/vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | f6ddddff-4ea1-523b-8b53-46f98d3023dd |  | note | Mudmap attached below
checkpoint-group |  |  | section | Post-Pour
checkpoint-status |  |  | checkpoint | Curing – Application rate of approved curing compound being applied in accordance with manufacturers recommendations
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
label | 4a3e2290-f2c0-56fa-9ffe-bfae165bb109 |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | c1683439-70ee-57f3-99e2-24325440327f |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Stressing records – Postenco checklist reviewed including extensions
checkpoint-status |  |  | checkpoint | Stressing extensions – Postenco records reviewed by Stressing Engineer and approval to cut all strands has been received
label | 32b33ca3-4342-50cc-b7b7-4687e8637f1b |  | note | Aconex reference linked/commented below
checkpoint-status |  |  | checkpoint | Grouting - Completed by Postenco and ITP reviewed
checkpoint-status |  |  | checkpoint | As Built Drawings – Review of Form700 as builts
label | 5ded9279-774a-5e8e-a036-16f8b3a857e6 |  | note | Aconex reference linked/commented below
checklist-flat |  |  | checklist | Hole Coring 65 |  |  |  |  | Yes | Hole Coring 65 | c61140b3-a46c-4275-ac32-97de8a5a0887
checkpoint-status |  |  | checkpoint | Confirm correct size of core hole for service penetration - 65mm
checkpoint-status |  |  | checkpoint | Hole coring complete in accordance with approval and sign-off
label | 8247e50c-5413-5300-b543-b7440c392c29 |  | note | Provide photo of each core and hole showing any reinforcement cut / no PT cut
checklist-flat |  |  | checklist | Hole Coring Approval |  |  |  |  | Yes | Hole Coring Approval | cd8f1c77-142a-4286-9621-bfaaf0c4b07a
checkpoint-status |  |  | checkpoint | Upload marked up drawing of core locations with core holes numbered. Current revision referenced
checkpoint-status |  |  | checkpoint | Stride survey completed and core locations marked
checkpoint-status |  |  | checkpoint | 4D approval issued with locations identified and approved
button | 43b6c07f-9611-5a79-b09c-327fa409ac70 |  | button | 4D confirm core location has no adverse effect on future redundancy | Yes,No
label | fd4019c3-4bdd-5110-9506-4a5be96a0b73 |  | note | Attach copy of approval DA
checkpoint-status |  |  | checkpoint | Slab scanned to confirm PT and reo location
label | 0c6c1adb-86c9-5e70-8b31-dbbe90af1cdc |  | note | Attach copy of scan report from Vic Sawing
checklist-flat |  |  | checklist | Multiplex Column Concrete Pour ITP (V.132121) |  |  |  |  | Yes | Multiplex Column Concrete Pour ITP (V.132121) | d0431bba-2529-42df-a4e2-0a5b016ca555
checkpoint-status |  |  | checkpoint | Reinforcement installation - inspected by MPX
label | 0659813f-b7c3-5d00-b958-d1534438db3c |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | b55e9c9e-27b7-587f-b77c-5f623da711cc |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | 5f7fcedb-0425-529a-b30c-39afd57f75d4 |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | d29525c3-f55d-5491-b820-a227e70bf8c9 |  | note | Mudmap attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | 6268e4c4-1419-500c-83a3-db1d1e8c71d0 |  | note | Report attached below
checklist-sectioned |  |  | checklist | Multiplex Column Concrete Pour ITP (V.132121) |  |  |  |  | Yes | ZSYS - Multiplex Column Concrete Pour ITP (V.132121) [old version 1] | e50a7bd2-fc39-44c7-b4b8-57eacaa035c9
checkpoint-group |  |  | section | Pre-Pour
checkpoint-status |  |  | checkpoint | Subcontractor Column Prepour Completed
label | 9e91e8d1-9bb4-5464-9e26-a090072dc4a4 |  | note | ITP Completed by Form700 and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Reinforcement installation - inspected by MPX
label | f8220674-17f1-571d-a15a-c25a0454a2aa |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Services penetrations - Inspected for all slabs/walls and "CONQA-Service Penetrations Matrix" verified as passed off by each of the services subcontractors
label | 23615f76-de26-5792-bc64-aaae63df41ba |  | note | Markup attached as applicable
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - Confirmation of Form700 completed ITP
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - MPX Inspection of all elements
label | 4827a212-0fd1-54dc-8656-bd5273939874 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | f45cf4df-2ed0-5535-bd98-b7ffa8efb128 |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | db84f5f3-71f7-5d76-8973-bd3678bc0b17 |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Placement of concrete checked
label | 560bb140-8e3b-54d0-a600-fb15848a684f |  | note | Monitored by Multiplex and subcontractor supervision to ensure adequate compaction/vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | 4d722110-5b2c-55e9-bbd5-75cde9f06c78 |  | note | Mudmap attached below
checkpoint-group |  |  | section | Post-Pour
checkpoint-status |  |  | checkpoint | Curing – Application rate of approved curing compound being applied in accordance with manufacturers recommendations
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
label | edaae7a5-41bb-5a4c-a09a-da5ec2479dec |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | 49e07ba5-6a0e-5e26-9cad-b02cc40b271f |  | note | Report attached below
checklist-flat |  |  | checklist | Crack Tests |  |  |  |  | Yes | Crack Tests | e982cace-c0e3-4be6-9951-27ec7de7adb3
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
checklist-sectioned |  |  | checklist | Multiplex Core Concrete Pour ITP (V.132121) |  |  |  |  | Yes | Multiplex Core Concrete Pour ITP (V.132121) | ebfad144-149c-41bb-8490-340ad4f50c67
checkpoint-group |  |  | section | Pre-Pour
checkpoint-status |  |  | checkpoint | Subcontractor Core Prepour Completed
label | 0ce66f35-7231-5162-b217-1b00ffe43712 |  | note | ITP Completed by Form700 and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Reinforcement installation - inspected by MPX
label | e3f1cfa9-8efd-5d13-88ae-23295625ed18 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Services penetrations - Inspected for all slabs/walls and "CONQA-Service Penetrations Matrix" verified as passed off by each of the services subcontractors
label | 5b4317af-cb96-5f57-80a3-d5fa41dd0b0e |  | note | Markup attached as applicable
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - Confirmation of Form700 completed ITP
checkpoint-status |  |  | checkpoint | Cast in items and holding down bolts - MPX Inspection of all elements
label | cf21c6f8-c6cd-5ffa-8aed-29585c1c51f1 |  | note | MANDATORY - Attach photos below of inspected elements
checkpoint-status |  |  | checkpoint | Area clean - All debris removed from the area prior to pouring concrete
checkpoint-status |  |  | checkpoint | HOLD POINT - Reinforcement installation - Inspected by structural engineer and corrective actions completed and signed-off
label | 25e1a502-e45b-55ab-b28d-a1552ff0a5de |  | note | Structural Engineer Inspection report attached below (If applicable)
boolean | a5c79fb0-d1d0-59b9-9820-ae70b7de36e4 |  | tickbox | Corrective actions completed and signed-off - Attach corrective action photos below
holdpoint |  |  | signoff | Request Structural Engineer Sign-Off
checkpoint-group |  |  | section | During Pour
checkpoint-status |  |  | checkpoint | Placement of concrete checked
label | f000050c-f0c1-5b0c-b3f7-1b9d7ac540a8 |  | note | Monitored by Multiplex and subcontractor supervision to ensure adequate compaction/vibration of concrete is achieved
checkpoint-status |  |  | checkpoint | Concrete Testing - Compressive testing and slump tests samples completed by supplier
checkpoint-status |  |  | checkpoint | Concrete Traceability - Mud map established to indicate date and location of pour
label | cd1948e2-4bc5-5ffd-84e7-f53f951e7f1b |  | note | Mudmap attached below
checkpoint-group |  |  | section | Post-Pour
checkpoint-status |  |  | checkpoint | Curing – Application rate of approved curing compound being applied in accordance with manufacturers recommendations
checkpoint-status |  |  | checkpoint | Concrete test results - Compressive strength results for initial and final stress submitted and compliant
label | fd762f93-3e95-5e65-bf16-72142f5bed34 |  | note | Report attached below
checkpoint-status |  |  | checkpoint | Concrete test results - 28 day compressive strength results submitted and compliant
label | 07c555da-6e79-5577-8fb3-e335b301bbbb |  | note | Report attached below
checkpoint-status |  |  | checkpoint | As Built Drawings – Review of Form700 as builts
label | 038dac70-5408-58e6-acdc-5398529b4e0a |  | note | Aconex reference linked/commented below
checklist-flat |  |  | checklist | Hole Coring 180 |  |  |  |  | Yes | Hole Coring 180 | ee7b8c16-17f9-4849-8bde-e88e8cbe77ff
checkpoint-status |  |  | checkpoint | Confirm correct size of core hole for service penetration - 180mm
checkpoint-status |  |  | checkpoint | Hole coring complete in accordance with approval and sign-off
label | a04ec403-7273-5c41-a203-85d3d9d2aca0 |  | note | Provide photo of each core and hole showing any reinforcement cut / no PT cut
checklist-sectioned |  |  | checklist | MPX - Precast Installation (V.130722) |  |  |  |  | Yes | MPX - Precast Installation (V.130722) | ffd2dea7-1b81-4c17-bdd5-a1c913947728
checkpoint-group |  |  | section | Acceptance / Installation
checkpoint-status |  |  | checkpoint | Subcontractor ITP / checklist Completed
label | 4e540b9a-b08c-53eb-990c-973839d3eb69 |  | note | ITP Completed by precast manufacturer and all documents uploaded to CONQA
checkpoint-status |  |  | checkpoint | Slab / element has reached min 20 Mpa
text | 54ada4b1-4903-5eb0-a222-3dd99823dcc2 |  | textbox | Strength (Mpa)
label | 89595b85-9d8b-5b3b-85ac-5e398458d1b7 |  | note | Attach a photo / upload
checkpoint-status |  |  | checkpoint | Accept Panel
label | 25ddd500-a065-5673-8c8f-68b6e18c85fd |  | note | Visual check - no cracks / damage to any face of the panel / attach photo
checkpoint-status |  |  | checkpoint | Grout tubes clear of obstructions
label | 43e2d25a-09f8-57e8-9e93-4249798e5b55 |  | note | Attach photos of grout tubes
checkpoint-status |  |  | checkpoint | Marking plan / location of panel attached below
checkpoint-status |  |  | checkpoint | Packers / shims placed so as not to block the grout tubes
checkpoint-status |  |  | checkpoint | Panel installed - Correct alignment and plumb
checkpoint-status |  |  | checkpoint | Props installed as per propping design supplied by RBG - DWG Number
text | 2c67d8d2-934d-5da7-8c8d-16cb73a5b926 |  | textbox | Drawing reference
text | 3e4bbc40-3126-5cc4-b1f3-9afbb473d4e1 |  | textbox | Revision
checkpoint-status |  |  | checkpoint | Area clean - All debris removed
checkpoint-status |  |  | checkpoint | Form 700 installation checklist received and complete
checkpoint-group |  |  | section | Base Grouting
checkpoint-status |  |  | checkpoint | Area clean - Ensure base of column is clear of any debris, lightly wet column base and blow-out excess water
checkpoint-status |  |  | checkpoint | Dam installed around perimeter of precast element ensuring 10-15mm gap is maintained
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | e7fe6514-1ea5-5711-b097-67c436d8d6fb |  | textbox | Grout type
text | 32d635df-0841-51af-8f78-0670a6e3808a |  | textbox | Strength (Mpa)
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | Base filled with grout to top of dam
checkpoint-status |  |  | checkpoint | Grout samples taken
checkpoint-group |  |  | section | Tube Grouting
checkpoint-status |  |  | checkpoint | Confirm base is filled - no gaps and grout is cured
checkpoint-status |  |  | checkpoint | Verify grout used type / strength
text | fed63e29-c7dd-55d0-8ec2-66323e448a51 |  | textbox | Grout type
text | 4a4afe02-df9d-51d1-9aec-481c8ce8d8c0 |  | textbox | Strength (Mpa)
button | 5372dbf8-5cd0-5faa-85ff-4a6ea0653b00 |  | button | Grout samples taken | Yes,No
checkpoint-status |  |  | checkpoint | Grout mixed as per manufacturer's specification
checkpoint-status |  |  | checkpoint | All grout tubes are full using approximately the same amount of grout in each tube
checkpoint-group |  |  | section | Grout Strength
checkpoint-status |  |  | checkpoint | 28 day grout test result attached below
text | c3add552-b454-5e38-b3ff-63f2c77d0276 |  | textbox | Specified Strength
text | ecee3118-6892-5ec6-8190-40988cd59bdb |  | textbox | 28 day test result
checkpoint-group |  |  | section | Welding of Stitch Plates
checkpoint-status |  |  | checkpoint | Confirm structural specification developed and design approved
checkpoint-status |  |  | checkpoint | Welding procedure developed and communicated to welders undertaking the work
checkpoint-status |  |  | checkpoint | All welders are certified and certificates provided
checkpoint-status |  |  | checkpoint | Welding works inspected and approved by supervisor / coordinator - name and signoff attached below
checkpoint-status |  |  | checkpoint | Weld inspection report received and attached below
checklist-flat |  |  | checklist | Site Inspection number: |  |  |  |  | Yes | Add Site Inspection ITP (V.020721) | fffa26d0-41d0-4087-95c4-bc8f8ea24bcd
checkpoint-status |  |  | checkpoint | Status - Pass=Completed / FAIL=Overdue / Un-selected=Pending
boolean | 8b69fe45-515b-5051-8bcf-515036595743 |  | tickbox | Inspection report attached below
select | d2bacbc8-2011-5fef-92af-590a6f1e7669 |  | dropdown | Consultant: | 4D, FSG, MA Civil, Philip Chun, RBG
text | 5ad4ea72-111e-5768-9dd4-877cfb035bb5 |  | textbox | SIR Number
text | 68911d63-7467-5e66-92dc-4f3667ecdfe4 |  | textbox | Date inspected
text | c6d82e31-1c66-54ef-a55f-1b2949c10771 |  | textbox | Aconex Reference
select | 839e409e-e178-52ce-bd27-2ff16c1c905e |  | dropdown | MPX Responsible | Dom Kumosz, Trent Cox, Other (Specify below)
text | 434c0d1c-ea56-54ef-8f3c-94a3e1d5300d |  | textbox | Other (Specify here)
select | d405f2b8-c8a5-5290-bbf9-5b7fbe7e7876 |  | dropdown | Trade Responsible | Delta/Browns, Other (Specify below)
text | 3efb4422-e692-571b-abc8-57adca3258fa |  | textbox | Other (Specify here)
text | fa4f96d5-52a2-5ab3-94a0-e5a585ecafec |  | textbox | Aconex Subject
text | 00bc2452-7676-54b6-8fde-34c7e81d2b89 |  | textbox | MPX Close-Out Thread (Aconex)
text | f7c35b9c-4ed3-5481-9bfa-627e8c164078 |  | textbox | Comments
text | 23eb237a-da07-51c4-9c3e-1ce6b962fbc0 |  | textbox | Close-Out Date
label | 49748c61-2e33-58eb-9619-e01ed16760b1 |  | note | Photos attached below as applicable