## Project Structure
Folder Structure |  |  |  | Checklists
Site Diary
Undocumented variations
|  | Builder |  | Undocumented Variations
|  | Subcontractors |  | Undocumented Variations
| Site Diary comments/notes |  |  | Site Diary Checklist
Toolbox Meetings
| 2023-08-01 |  | ability to add
| 2023-09-01 |  | ability to add
| 2023-10-01 |  | ability to add
| 2023-11-01 |  | ability to add
| 2023-12-01 |  | ability to add
Project Drawings
| Peno Drawings |  |  | Project Drawings
| Fabb Sheets |  |  | Project Drawings
| Fitters Drawings |  |  | Project Drawings
| RCP |  |  | Project Drawings
| Material Sheets |  |  | Project Drawings
Site QA
Rough In
|  | Ground Floor Retail |  | Sprinkler Rough In checklist
|  | Ground Floor Carpark |  | Sprinkler Rough In checklist
|  | Level 1 |  | Sprinkler Rough In checklist
|  | Level 2 |  | Sprinkler Rough In checklist
|  | Roof |  | Sprinkler Rough In checklist
Fit Off
|  | Ground Floor Retail |  | Sprinkler Fit Off checklist
|  | Ground Floor Carpark |  | Sprinkler Fit Off checklist
|  | Level 1 |  | Sprinkler Fit Off checklist
|  | Level 2 |  | Sprinkler Fit Off checklist
|  | Roof |  | Sprinkler Fit Off checklist
Fire Penetrations
|  | Ground Floor Retail |  | Fire Penetrations checklist
|  | Ground Floor Carpark |  | Fire Penetrations checklist
|  | Level 1 |  | Fire Penetrations checklist
|  | Level 2 |  | Fire Penetrations checklist
|  | Roof |  | Fire Penetrations checklist
Hydrant/ Sprinkler Mains / Risers / Hose Reels
|  | Ground |  | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist
|  | Level 1 |  | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist
|  | Level 2 |  | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist
| Sprinkler Control Valves |  |  | Sprinkler Control Valves checklist
| Fire Booster Cupboard |  |  | Fire Booster Cupboard checklist
Fire Extinguishers
|  | Ground Floor Retail |  | Fire Extinguishers/Blankets
|  | Ground Floor Carpark |  | Fire Extinguishers/Blankets
|  | Level 1 |  | Fire Extinguishers/Blankets
|  | Level 2 |  | Fire Extinguishers/Blankets
|  | Roof |  | Fire Extinguishers/Blankets
| Commissioning |  |  | Commissioning
Variations |  |  | ability to add
Incident Reports |  |  | ability to add

## Checklists
type | name
checklist | Sprinkler Rough In checklist
checkpoint | Rough In: All Mains, range pipes, clips installed & secured
checkpoint | Concealed Space Sprinklers & Flexible droppers Installed
checkpoint | Arm pieces / Under Duct pipework installed and secured
checkpoint | Balcony Sprinklers installed
checkpoint | Car Park Sprinklers Installed
checkpoint | Car Stackers pipework installed & secured (if applicable)
checkpoint | Install Remote Test drain pipework
checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
text | Start time:
text | Completion time:
checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
text | Start time:
text | Completion time:
checkpoint | PFP Foreman signature
checklist | Sprinkler Fit Off checklist
checkpoint | Fit Off: Check all sprinklers have been fit off
checkpoint | Check sprinkler heights pre paint
checkpoint | Fit off Escutcheon plates
checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
text | Start time:
text | Completion time:
checkpoint | Water Test: Pressure test to 1600Kpa for duration of 2 hours
text | Start time:
text | Completion time:
checkpoint | PFP Foreman signature
checklist | Hydrant/ Sprinkler Mains / Risers / Hose Reel checklist
checkpoint | Rough In: All Mains & isolation valves installed
checkpoint | Install Hydrant/ Sprinkler/Test Drain Risers & Mill Cocks
checkpoint | Sprinkler Floor Control Valves installed and secured
checkpoint | Fit Off: Check all millcock clearances/angles/Mill cocks in closed position & Install 2400kPa pressure gauge to top of risers
checkpoint | Install Fire Hose Reels & pipework
checkpoint | Air Test: Pressurized air test for a period of 30 mins (if applicable)
text | Start time:
text | Completion time:
checkpoint | Water Test: Pressure test to 1700Kpa for duration of 2 hours
text | Start time:
text | Completion time:
checkpoint | FHR: All FHR been bled from excess air & proof of water
checkpoint | PFP Foreman signature
checklist | Sprinkler Control Valves checklist
checkpoint | Install Sprinkler Control Valves/ Jacking Pump
checkpoint | Test full operation of Control Valves
checkpoint | Install Sprinkler Spares box, spare sprinklers & spanner
checkpoint | Set Jacking Pump pressure switch min 150 kPa above towns main/manifold pressure
checkpoint | Install Gong/Electric Bell & test operation
checkpoint | Check for adequate drainage and test
checklist | Fire Booster Cupboard checklist
checkpoint | Install Suction/ Millcocks & Hydrant, Sprinkler Boosters
checklist | Fire Pumps/Tanks checklist
checkpoint | Install Plinth & secure
checkpoint | Install Pumps & secure to plinths
checkpoint | Install all pipework/isolation valves to pumps
checkpoint | Install Annubar/coolant drains
checkpoint | Install Pump Exhaust to designated point
checkpoint | Water Test all Pipework to pumps
checkpoint | Install all Pipework and Valves to Fire Tank
checkpoint | Water test all pipework to and from Water Tank
checklist | Commissioning
checkpoint | SCV-Locks/chain/labels/pipework stickers/sprinkler spares & spanner/block plans
checkpoint | Booster Cupboard-Signage/Locks/chain/labels/plan sleeve+block plans label/block plans
checkpoint | Hydrant Mains/Isolation Valves-Locks/chain/labels/pipework stickers
checkpoint | Water Meter Assembly-Locks/chain/labels
checkpoint | Check sluice valves & water meter valves are open
checkpoint | Fire Pump/Tank-Fuel full, Exhaust piped, Mains power, Drains/Relief Valve piped, Water Supply on, Locks/chain/labels/pipework stickers
checkpoint | Adjust Bermads & float Valves to fire tanks
checkpoint | Pump Room-Block Plans
checkpoint | FIP-Block plans/test all alarm devices
checkpoint | Test all Valves & Flow switches to ensure correct operation
checkpoint | Set Pressure switches to Jacking pump & alarm line
checkpoint | Block plans/Tactical Fire plans/FRV way finding plan
checkpoint | FRV Shortfall drawings & FRV stat signage ie: x2 30m hose
checkpoint | Individual Floor Block plans (If applicable)
checklist | Fire Extinguishers/Blankets
checkpoint | Install Extinguishers
checkpoint | Install appropiate signage
checkpoint | Install Fire Blankets
checkpoint | Fire Hose Reel signs
checklist | Fire Penetrations checklist
checkpoint | Fire Penetration labelled & caulked in accordance with AS 4072.1 Drawing Reference No.
checklist | Toolbox Meeting Checklist
section | Attendance
checkpoint | Attendance - list of attendees added below
section | Minutes
checkpoint | Actions from last meeting
checkpoint | Safety: (including hazards / near misses / controls / site specific)
checkpoint | Plant, tools & Equipment all in good working order?
checkpoint | PPE-ensure everyone has PPE
checkpoint | Housekeeping to be maintained
checkpoint | Ensure Electrical equipment test and tagged
section | New Business / Other
checkpoint | Any new business / other comments added below
section | Meeting Closure
checkpoint | Meeting Closed
textbox | Meeting Closed time
textbox | Minutes taken by (Name)
checkpoint | Employee sign off
checklist | Variations
section | Payer Details
checkpoint | Payer Details entered below
text | Contact
text | Company
text | Contact No.
section | Variation Details
checkpoint | Variation Details Entered
text | Description of work
text | Reason for variation (unless stated in instruction)
text | Area/Location
text | As directed and requested by
text | Date
text | Normal Hours
text | Overtime Hours
text | Material used to complete task
checkpoint | Variation Completed
section | Sign Off
checkpoint | Variation signed
signoff | Builder / Client signature
label | I hereby authorise you to carry out the extra work detailed above and I agree that the same shall be paid as an addition to your original contract order
checklist | Incident Reports
section | Details of accident/incident
checkpoint | Please attach any relevant photos & documents
textbox | Date of incident
textbox | Time of incident:
textbox | Time of report:
checkpoint | Nature of incident
tickbox | injury (attach completed WHSE Form 01 Injury report)
tickbox | environmental (pollution)
tickbox | damage to property/assets/services
tickbox | incident
section | Names of person(s) involved
checkpoint | Please attach any relevant photos & documents
textbox | Name
textbox | Phone Number
note | (home, mobile & work)
textbox | Address
textbox | D.O.B
textbox | Email
textbox | Activity in which the person(s) was engaged at the time:
textbox | Exact site location where injury/incident occurred:
textbox | Type of injury/pollution/damage/ incident:
textbox | Describe the accident/incident in detail:
section | Witness to incident (each witness may need to provide an account of what happened
checkpoint | Please attach any relevant photos & documents
textbox | Witness Name
textbox | Witness Contact
textbox | Witness Name
textbox | Witness Contact
section | Are there any notable/significant factors relevant to the accident/incident?
checkpoint | Please attach any relevant photos & documents
textbox | Details
section | Arrangements made to store any equipment that believed to have contributed to injury/incident?
checkpoint | Please attach any relevant photos & documents
textbox | Details
section | Did any third parties (subcontractors, visitors, etc.,) contribute to the incident? If so, how?
checkpoint | Please attach any relevant photos & documents
textbox | Details
section | Immediate corrective actions taken? (e.g., works ceased, area made safe, barriers erected, etc.,)
checkpoint | Please attach any relevant photos & documents
textbox | Details
section | Future actions taken (e.g., engineering solutions, training, toolbox talk, etc.,)
checkpoint | Please attach any relevant photos & documents
textbox | Details
section | Review & Sign off
checkpoint | Have all actions been completed and reviewed as effective?
checkpoint | Have all documents relating to the incident, including corrective action evidence been completed
signoff | Signed Off
checklist | Project Drawings
checkpoint | Upload project drawings
checklist | Site Diary Checklist
checkpoint | Comment/notes
checklist | Undocumented Variations
checkpoint | Attach relevant details