## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat | 62dac2ce-7a26-41a8-8fcf-45d819199b53 |  | checklist | Ceilings |  |  |  |  | Yes | Ceiling Checklist | 28610923-45f1-46b1-8756-5bf1c47c3341
checkpoint-status | 2d498162-6548-43c0-ae7c-419d03ebe423 |  | checkpoint | SAMPLES
label | f5f62851-571e-50d2-9ead-979edbb48ea7 |  | note | Submitted and approved via Multiplex sample register
checkpoint-status | 46fa2ea6-a61a-49ab-8710-137726931d39 |  | checkpoint | MATERIALS
label | 949de2f6-b053-571b-bffe-3f19ebe486e7 |  | note | Checked at delivery for compliance to internal material schedule
checkpoint-status | 695ea998-68b0-42bf-b688-976a6978e35a |  | checkpoint | SET OUT
label | 2e34ac74-d686-5480-bd89-acd00fe76d41 |  | note | As per RCP DRAWING series
checkpoint-status | 85e860ef-98b0-4ccd-99be-3be287853d23 |  | checkpoint | FRAMING
label | acd9a45f-219e-59a5-8ffd-b4de72a32fba |  | note | Rondo- concealed key lock system- Hanger grid max 1200 x 1200
label | d6b80999-7ca4-507f-89dd-f3fa5d65c258 |  | note | Rondo- exposed grid tile system-Hanger grid max 1200 x 1200
label | 534e10ec-fdcf-55ae-b5a0-849792aab7ab |  | note | Provision for -Access panel - Electrical - mechanical framed out
label | 54c12bed-66d7-59dc-8508-9e559f10a178 |  | note | Any noggin requirements
label | a6dba487-f084-5155-8550-8d50feecb6f8 |  | note | Seismic considerations
checkpoint-status | e43ae240-f4b8-4051-b5dc-70c0804f203b |  | checkpoint | HOLDPOINT / INSPECTION
label | 4c8bf869-1cfe-5b32-b34d-13da647b1bc8 |  | note | Expoconti - Multiplex- Suppliers inspection of works
label | a276e854-73e5-5a9a-ba3f-c4678ab5a97b |  | note | Reworks noted and actioned prior to pre sheet sign off
holdpoint | 5b4c1af7-e106-4f38-a64d-c5dc1e1bca90 |  | signoff | Request Sign Off
checkpoint-status | 1f8770b4-c5a9-4084-bc66-4472365e05d8 |  | checkpoint | PRE SHEET SIGN OFF
label | 09ff4dca-bc93-56a7-ad84-d596c25c3f03 |  | note | Multiplex sign off system completed and instruction to proceed granted
checkpoint-status | 86b94cdc-3ea4-4afb-ad6b-f5d1cb87a2bf |  | checkpoint | INSULATION
label | ded25b49-d03b-5057-94f4-ae23d89442f1 |  | note | Glasswool insulation -Type, "R" value and location as per RCP series
label | 4a91cdfb-2159-5d83-a533-98df870ae2ce |  | note | no gaps, all ceiling area covered with insulation
checkpoint-status | 3563fcba-10c5-4f55-9064-74acfd308629 |  | checkpoint | LININGS
label | feeff56d-56c3-5d47-b7b2-f29a6d5aafd8 |  | note | Fire rated board- standard- wet areas- acoustic- impact CSR Red Book
label | a006f19a-9b30-562c-bc99-d45961bf1b7f |  | note | Nominated linings -RCP revisions
label | c31411aa-0f31-5d8a-a6b7-9b68eba2cbc9 |  | note | Fixings -spacings and staggered joins
label | 6c35370d-f3fb-5197-ab93-22b17b71d16f |  | note | Penetrations / lights cut outs
label | 3a57fb1f-aa21-50ee-b8a7-6d403ec41780 |  | note | Specialised linings
checkpoint-status | f6123c5d-a110-4611-82cf-0635eda480ee |  | checkpoint | ACCESS PANELS
label | 3f90932e-3d19-5c36-9fd9-ea91f296687f |  | note | Panel type and size nominated drawings (RCP) revisions (Checkpoint: attach photo)
label | 328e255b-3591-597f-bf8e-e037b10062be |  | note | Installed to manufacturers recommendations
label | f27e2632-dae5-527f-b1c8-e226e8337dc0 |  | note | Positioning -As marked by service trades requirements - RCP
checkpoint-status | f2c326d8-cd96-4067-a461-06eb873cacf0 |  | checkpoint | STOPPING / SANDING
label | 9c9b73f3-59de-5887-aefd-ff3fea5b238a |  | note | Class 4 finish
checkpoint-status | c4622951-284f-42be-9ef1-3e06f49def07 |  | checkpoint | CAULKING /PENETRATIONS
label | 2350c9b3-fc01-55e0-8705-7ccbb7cb7170 |  | note | Gap between plaster & substrate 15mm max
label | 0d9823cb-16d0-5b6f-a14b-d561036870ba |  | note | All penetrations sealed and caulked
label | aa1e5a0d-88f1-568f-9a13-5911d8ac87d4 |  | note | All gaps sealed in presurised rooms-perimmitter, pressure boxes
checkpoint-status | 44b53626-f351-41f0-9c8a-4fadc6c66fe8 |  | checkpoint | HOLD POINT / INSPECTION
label | df9a439f-c2ce-5223-b2d1-91b186dc4fce |  | note | Expoconti - Multiplex- Suppliers inspection of works
label | 4b6a3c6d-0c5b-5fee-a400-b10baaca2ac8 |  | note | Reworks noted and actioned prior to final finish paint coat
holdpoint | ce58fe4a-867d-4fa8-8a58-3cbb2bef03ef |  | signoff | Request Sign Off
checkpoint-status | e244818b-93bd-4fd0-963c-4d87e822d35c |  | checkpoint | DEFECTS
label | 378d7d26-0f1e-518c-97b0-b851d31ba499 |  | note | Multiplex/Client defects closed out via Aconex field
checkpoint-status | 3406495e-d33b-4c30-8008-13bf414c41d0 |  | checkpoint | FINAL INSPECTION/ SIGNOFF
label | 6c963cff-6971-5043-a1c3-acfb82a2e7de |  | note | Conformation that Expoconti representative has reviewed and verifies that all works have been completed and conforms to contract specifications
checklist-flat | 7d30a565-ceb0-4515-a581-62c8b11233e1 |  | checklist | Manufacturer's Inspection Report |  |  |  |  | Yes | Manufacturer's Inspection Report | 2888fa40-3b1e-471c-abb8-caa3871f662e
checkpoint-status | c0f21f58-84e5-4f7b-956c-faad583963a4 |  | checkpoint | Issued Report & Action
checklist-flat | 6687aa8c-9cf7-4f68-a215-10425987c1a3 |  | checklist | Speedpanel |  |  |  |  | Yes | Speedpanel Checklist | 4b372cde-32c1-4075-96fc-bfc653dd9cae
checkpoint-status | 3dec6867-73e6-4d98-9edf-ff5329cc078a |  | checkpoint | Drawing Reference - Latest IFC drawing referenced
checkpoint-status | 45f83804-562a-41b7-be1a-9edb58dc4faf |  | checkpoint | Current revision (Photo of title block with drawing No. and revision)
checkpoint-status | 98473610-ec9a-494a-b0b8-ee426def7b02 |  | checkpoint | Area clean and accessible to start work
checkpoint-status | cf5e7bdd-b64f-4408-8c3e-f2ed13820b83 |  | checkpoint | Confirm panel thickness used - 78mm
checkpoint-status | 782cbb9c-b1e8-472e-a5d9-998f75e96438 |  | checkpoint | Setout of wall location verified
checkpoint-status | f7644916-f7cb-44a0-8bd1-e56fb2f28e32 |  | checkpoint | Apply approved fire rated sealant (Hilti 606) between c-track and structure to entire perimeter (Photo)
checkpoint-status | 0f1a11eb-c9ba-411b-9f0e-eebde9ccc636 |  | checkpoint | Fix c-track to structure using Hiliti Huss anchors at 500mm centres (Photo)
checkpoint-status | 34c94562-4c90-44a3-a6d9-4a1735979354 |  | checkpoint | Apply approved fire rated sealant (Hilti 606) to internal corner ot the c-track (one side) to entire perimeter (Photo)
checkpoint-status | 983baa79-a69e-4f9a-a6c2-3ce08ffde0e9 |  | checkpoint | Verify maximum 20mm gap between speedpanel and top c-track (Photo)
checkpoint-status | 7008d824-f3ef-47b2-b2bf-ab6c524e8696 |  | checkpoint | Panel fixing - Perimeter 500mm centres / Horizontal 250mm centres / Vertical 1000mm centres
checkpoint-status | 7272b27f-1852-4dda-a7d7-4fce8ab25672 |  | checkpoint | If pressurised riser, all joins have been sealed - panel end & perimeter
checkpoint-status | de31aaa5-0d6d-4483-a88b-ed115ab05b9a |  | checkpoint | Install head track protection fixed with 30mm screws at 125mm centres (Photo of completed wall)
checklist-flat | e35e6d43-4ef0-4536-b002-68d5ffb6b996 |  | checklist | Walls |  |  |  |  | Yes | Wall Checklist | 63589c10-2e82-4bf7-9d0c-051fc4b57c5c
checkpoint-status | 91a82b57-abf4-46a8-8761-e7116b0b50fe |  | checkpoint | SAMPLES
label | 6e731246-bf9d-57a3-bc96-220c7a558123 |  | note | Submitted and approved via Multiplex sample register
checkpoint-status | 0c423e75-05fc-4ad5-a4f0-e1541165aa97 |  | checkpoint | MATERIALS
label | 68a66919-db0d-55f7-9237-4dd0694c7355 |  | note | Checked at delivery for compliance to internal material schedule
checkpoint-status | 974ddeb2-76cd-4d2d-a838-8e3d1dee0a48 |  | checkpoint | SET OUT
label | f839f39a-e29e-5629-86aa-7996f8c704e4 |  | note | As per WALL TYPE & INSULATION plans AR-0-140 series
checkpoint-status | cd1892b2-c543-4319-9315-f6e12aefee96 |  | checkpoint | WALL FRAMING
label | cbba3be1-4408-5932-9b9b-38aebe53b364 |  | note | Stud configeration conforms to Wall Types AR-0-230 series
label | 47ff25d0-f4c3-5e75-bbf7-c612bcbf766b |  | note | Conforms to Rondo (building B) / Studco (buildings D/E) seismic designs (Checkpoint - either studco/rondo)
label | 61de5463-195c-58fb-89bf-49f3f8640b9e |  | note | Fixings max 600 centres
label | 116d68c7-024b-5602-b64e-83a92d992047 |  | note | Stud spacings max 600 centres- Noggin track to suit
label | 1b83036d-2ad6-5180-8164-033ecee17881 |  | note | Framing to accommodate for penetrations
checkpoint-status | 59c04d04-38b8-42fb-81be-cfeb7f1e2db8 |  | checkpoint | PENETRATIONS THROUGH SMOKE SEAL
label | 3ab89110-345b-5555-be88-12a5d264a4c4 |  | note | Drilled through smoke seal
label | 68f5375b-e470-59d6-b31c-a5c1ebb98187 |  | note | Vacuum clean
label | 7fa086c2-37a7-5e31-bf92-e593013acc77 |  | note | Pre-filled hole with hilti cp606
label | 8dd37b69-88f5-5121-8473-a47152491cf8 |  | note | Caulking bead full length of bottom track
label | c3fbec38-da17-5902-b004-f1d819b53c09 |  | note | Fixed bottom track with HUSSBOLT 6mm
label | 217cc37d-032c-5a91-9b03-f5e7f81fa77d |  | note | Caulk exposed fixing head with cp606
checkpoint-status | ea163f8f-3dbd-4d20-94ba-a917d8eec0fe |  | checkpoint | DOOR FRAMES
label | 3ab89110-345b-5555-be88-12a5d264a4c4 |  | note | Installed in conjunction with Door Function Schedule AR-0-280 series
label | 68f5375b-e470-59d6-b31c-a5c1ebb98187 |  | note | Installed plumb and square
label | 7fa086c2-37a7-5e31-bf92-e593013acc77 |  | note | Fire rated frames backfilled and caulked
label | 8dd37b69-88f5-5121-8473-a47152491cf8 |  | note | Lead rated frames delivered lined
label | c3fbec38-da17-5902-b004-f1d819b53c09 |  | note | Spreader bars removed
checkpoint-status | 2b89e671-215a-45e7-885f-42c69134f4cc |  | checkpoint | NOGGINS PRESSURE BOXES
label | 5a0ca6be-6263-5bca-8107-4c3b0e92b21b |  | note | Installed as set out and required by service trades
checkpoint-status | 787966c0-a7be-44c9-85f2-387dff79babb |  | checkpoint | HOLDPOINT / INSPECTION
label | 0df09a9c-d597-5acb-bb5b-8e80f88b7b1f |  | note | Expoconti - Multiplex- Suppliers inspection of works
label | acb931b4-b36f-5d0a-a689-bfd7fe5ef7db |  | note | Reworks noted and actioned prior to pre sheet sign off
holdpoint | 0dae3268-ac75-471f-9f0a-98122fe8fee5 |  | signoff | Request Sign Off
checkpoint-status | 70f947b7-1165-4de8-a5e1-8f03e980a42a |  | checkpoint | PRE SHEET SIGN OFF
label | 49fae463-364b-58b5-a48a-229dcbf69aef |  | note | Multiplex sign off system completed and instruction to proceed granted
checkpoint-status | d3ea4356-3af4-4c5c-a380-0701cd6655b0 |  | checkpoint | INSULATION
label | 76318eef-d2b6-50c7-8b99-b5c23fbb3c03 |  | note | Type and location as per Wall Type & Insulation plans AR-0- 230 series (Checkpoint: input insulation type)
label | bdef5cdb-6cda-5d0b-8928-863eb1b60684 |  | note | Installed tight between studs - no gaps
checkpoint-status | a9391b8b-a21e-4435-8690-6599904cf32c |  | checkpoint | LININGS
label | 3a2bf32c-b9f6-5b05-a261-41fd75f74593 |  | note | Conformation type & location AR-0-230 series (Checkpoint: standard / bathroom / Fire)
label | 5cf4e594-01bf-5db7-870f-7a2de61deb11 |  | note | Fire rated board- standard- wet areas- acoustic- impact CSR Red Book
label | 965b2ccf-9f30-5600-ac48-04d5314fbfb7 |  | note | Staggered joins- Screw spacings to Edge (200mm max) field (300mm max)
label | f82c285a-f882-5e0a-8141-60cf32022fe1 |  | note | No gaps - square and plumb
label | 6bbcd215-2912-572d-b34d-0a7b586c311e |  | note | Overlap at corner junctions
label | 1b2a60a5-7da4-55c1-befb-7670691fb10a |  | note | Penetrations stopped/ caulked
checkpoint-status | 6589d930-cdf2-4ec0-8f2b-53f26ae0c28b |  | checkpoint | STOPPING / SANDING
label | 134f024b-92f0-59ab-8114-1f548accbb16 |  | note | Class 4 finish
checkpoint-status | 1b0bfd9d-0d3f-4140-be7c-b38c11c6404b |  | checkpoint | CAULKING /PENETRATIONS
label | 68deef0e-5b41-5cd2-b008-9805d79474f1 |  | note | Acoustic and Fire rated caulk- Hilti 606
label | fb5d727e-6416-535b-b2b1-f01776f77b2e |  | note | Ensure all Fire rated walls fully caulked
label | 82e71732-48bc-5838-bc58-b335d2fa251b |  | note | Gap between plaster & substrate 15mm max
label | 8de164f7-287f-5778-a955-657716398f83 |  | note | All penetrations sealed and caulked
label | 3db1a87c-c6e4-57bd-9467-c65c63911be0 |  | note | All gaps sealed in presurised rooms-perimmitter, pressure boxes
checkpoint-status | defc8b05-a06a-4ab4-87a8-0ff579b1b66f |  | checkpoint | HOLD POINT / INSPECTION
label | f3c7bd2f-bf97-502e-9c05-f446fe525671 |  | note | Expoconti - Multiplex- Suppliers inspection of works
label | bb44b611-fbe9-572c-88ae-a120d1a5a4cc |  | note | Reworks noted and actioned prior to final finish paint coat
holdpoint | d937f66e-d1c9-4ac2-bbf3-f53916d3bfdc |  | signoff | Request Sign Off
checkpoint-status | e426a154-6cbc-4e80-987a-5bbafa87c58d |  | checkpoint | DEFECTS
label | 8affe789-e978-51a0-bd77-0e724566842a |  | note | Multiplex/Client defects closed out via Aconex field
checkpoint-status | be0ea1a5-749c-41dd-870c-5124c921b918 |  | checkpoint | FINAL INSPECTION/ SIGNOFF
label | 227d6390-eb5b-566e-ae59-845bc86a0ddb |  | note | Conformation that Expoconti representative has reviewed and verifies that all works have been completed and conforms to contract specifications
checklist-flat | 660efdb6-1567-4457-acd6-4fd93bf7208a |  | checklist | Delivery Checklist |  |  |  |  | Yes | Delivery Checklist | 9ac09f09-f935-453d-a90b-b2d00f9263e2
checkpoint-status | 419f4ec9-0866-4df0-a1b5-1c6ec3cafd7e |  | checkpoint | Delivery details and docket uploaded below
checklist-flat | 3e2476d8-32cc-4059-88f2-2ff3fa9ab741 |  | checklist | Speedpanel |  |  |  |  | Yes | Speedpanel Checklist (+Door Frames) | bcbcea95-f74a-41a8-a3c6-e4c487353982
checkpoint-status | 7b20406b-d91d-4686-bd9d-814a91d207b1 |  | checkpoint | Drawing Reference - Latest IFC drawing referenced
checkpoint-status | 74a6e418-7c80-41f1-b3f4-0f065c923a53 |  | checkpoint | Current revision (Photo of title block with drawing No. and revision)
checkpoint-status | d247d582-b1e5-4e4f-91d9-ef6aa0ed3ac3 |  | checkpoint | Area clean and accessible to start work
checkpoint-status | e437886b-9fba-4a28-9b1f-34b632103df6 |  | checkpoint | Confirm panel thickness used - 78mm
checkpoint-status | 34082706-5542-43aa-a363-91678f2e9292 |  | checkpoint | Setout of wall location verified
checkpoint-status | 76ac8315-404f-4ee5-b462-965ffafa3e68 |  | checkpoint | Apply approved fire rated sealant (Hilti 606) between c-track and structure to entire perimeter (Photo)
checkpoint-status | 397d6595-dcd3-4fc6-91a6-d515d0df9b0f |  | checkpoint | Fix c-track to structure using Hiliti Huss anchors at 500mm centres (Photo)
checkpoint-status | e5130576-9b73-4e09-b2be-216b549be94b |  | checkpoint | Apply approved fire rated sealant (Hilti 606) to internal corner ot the c-track (one side) to entire perimeter (Photo)
checkpoint-status | cdc489d1-1c84-4806-a224-a6db99476c1b |  | checkpoint | Verify maximum 20mm gap between speedpanel and top c-track (Photo)
checkpoint-status | 5601dbea-a50e-4b82-ab37-955fc4eb09d6 |  | checkpoint | Panel fixing - Perimeter 500mm centres / Horizontal 250mm centres / Vertical 1000mm centres
checkpoint-status | 15fa8667-1278-45e1-8804-7bbead1accf6 |  | checkpoint | If pressurised riser, all joins have been sealed - panel end & perimeter
checkpoint-status | 74ec3d55-4b97-4030-a3a5-27199189dd2d |  | checkpoint | Install head track protection fixed with 30mm screws at 125mm centres (Photo of completed wall)
checkpoint-status | 17e27b35-aaa9-44df-b8b5-12b84859eb2f |  | checkpoint | DOOR FRAMES
label | 0046df1e-7c23-5716-b04c-e034ef96a5a2 |  | note | Installed in conjunction with Door Function Schedule AR-0-280 series
label | 42e9d95a-17e7-5e2b-9bdb-542d6919810b |  | note | Installed plumb and square
label | 2f012a51-3820-583c-8f5d-345c57d2a9f4 |  | note | Fire rated frames backfilled and caulked
label | 25482b9a-ceac-5512-866b-ecc0f0495918 |  | note | Lead rated frames delivered lined
label | 96db60d2-07e6-5187-9104-ee014b60ad60 |  | note | Spreader bars removed