## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
| checklist | AES-NZ1005-STE-ITP-PMT-0030 - EV Charging |  | AES-NZ1005-STE-ITP-PMT-0030 - EV Charging |  | 357f9828-73fa-4c9d-983d-86b8818fba01
| section | MATERIAL COMPLIANCE
| checkpoint | RDM & Consent Approval
272403e8-92f6-58dd-9caf-79f43c5c0f5c | note | Resp. - CPB
939fc292-472b-5c2d-a34f-1b09a139c44e | note | Referenced Documentation - RDM Tracker Consent Tracker
73f5ce68-0453-577e-adfa-2c1bec1fc73f | note | Conformance Criteria - RDM approval tracker Consent approval tracker
3daa43cd-c58a-5548-b888-e05b5f62d85e | note | Method - DR
3ff70af4-8974-5a05-8556-33bcda3b5468 | note | Frequency - By Building/ Site Wide
4b3fd940-9c9d-5bcc-9fc8-00e699bb0aa5 | note | WP - AES
49676dd2-93ab-5a1f-97cb-d4be11042f3b | note | Records - Receipt of Approval by Client
| checkpoint | General
f24b961b-f67d-5da0-bb3b-8305b0cfc7d5 | note | Resp. - SE
795be779-6ecc-5313-85fe-e48453dfc54f | note | Referenced Documentation - NZT5007-STE-ESSP-0001
e69b5f3c-a53f-5323-ae44-d5fdca8a3bb6 | note | Conformance Criteria - For all materials, a certificate of compliance shall be provided to the Client Rep. before the materials are incorporated into the works.
a82c5734-503e-5960-9790-88515c560e66 | note | • Specifications & QA Documents Approved
631dbcc2-1fd8-5af1-9b3e-1c6c64c7614d | note | • Drawings are confirmed.
35e5aba0-0adb-5d16-a54d-2cca261c4b41 | note | • Equipment fit for purpose
b382fe73-3539-5b51-be25-1ccf8df02add | note | Method - DR
78cdd6f2-48be-598c-9db4-e1e906f9d86d | note | Frequency - Each material
9c07482f-f395-554f-b660-9f6ffc33c7fe | note | WP - CPB
b1cf891d-f41e-5d48-b656-1abe4d87c055 | note | Records - Aconex approval
8caf5e90-95e7-5961-91ad-2a3964e78c70 | note | • Incoming Inspection Checklists
4cbf6a37-7af8-52a5-9b51-b5dc96dfc5da | note | • Drawing Register
| signoff | Request Signoff/ Raise Remedial
| section | MSB 3 Installation
| checkpoint | Factory acceptance tests
427725b0-8c3b-52d1-a210-996a7b91264e | note | Resp. - SUP
88cc0e98-df11-5712-a49f-b40b183bd6fd | note | Referenced Documentation - AS/NZS 3000:2007
4b7c632f-eb6d-5035-a573-343bec3526db | note | Conformance Criteria - Confirm FATs complete
b7d5acf1-fc2d-5419-8927-b9127d123794 | note | Method - DR
8e31ea2d-e4bf-5363-a695-95964162b704 | note | Frequency - Once
2ea64359-c7e4-5282-ab5f-764683e44bf6 | note | WP - AES, CPB
79785b13-000c-5b51-98f4-3cb0c17d21ea | note | Records - Check Sheet + CMR
| checkpoint | Location
10181543-e628-516b-8b51-44ca050ed3f9 | note | Resp. - SUP
19e79cb7-b04b-53a0-bc1b-9ad6453e6344 | note | Referenced Documentation - AS/NZS 3000:2007
43f21bb9-3957-57a9-9535-3e6d08ee8ce8 | note | Conformance Criteria - Check MSB is located as per the approved drawings.
66893afc-d263-53d8-8ff9-b1bf2bffa852 | note | • Complies with standards
e8f0135f-7b0c-5990-9d47-eb31f0ad04cd | note | Method - V + FM
29772205-e87c-591f-95a7-e7b26af3ede2 | note | Frequency - Once
482a23e8-2c40-5af9-87bd-e31657dcef24 | note | WP - AES
3aebe157-05a0-55f8-8bc8-8204b2601926 | note | Records - Check Sheet + Photo
| checkpoint | Fixings
d505bd3a-41e2-5b17-89af-5071827e9eef | note | Resp. - SUP
c1037e76-8774-51c6-9765-65959bf78b8c | note | Conformance Criteria - Check seismic fixings comply with approved submission
ced63639-e349-5f74-80c0-7905e6b1f164 | note | Method - V
c1215013-eba9-581b-a68b-1b853ee9e226 | note | Frequency - Once
fed7e844-1eee-5f21-bde4-c6db99ab6e72 | note | WP - AES
74b0eaf5-2fa9-54a8-8cf4-2b30aaec706c | note | Records - Check Sheet
| section | Low Voltage Cable & DB Installation
| checkpoint | Electrical conduits
751139ae-e78d-5af5-af69-6b3b99046acc | note | Resp. - SUP
12e185e1-7348-5a43-9df4-0339f5837ebd | note | Referenced Documentation - Refer AES-NZ1005-STE-ITP-PMT-0019
adf715f6-b41f-5540-9ff3-36a853d9608a | note | Conformance Criteria - Complete as per the referred ITP
5f50b588-b45f-5a9e-88d8-fe26aca1d966 | note | Method - DR
021fb11d-01f4-5375-ba25-3d74c1381e66 | note | Frequency - Once
87f1dc67-ee5a-5c3d-9408-432cc945c551 | note | WP - AES
fb0aa82d-ef2f-536f-9b70-c2c345698d1b | note | Records - Check Sheet + ITP
| checkpoint | Mains & submains Installed & terminated to MSB-3
8051a2ac-2792-5b95-8396-6f15543e4626 | note | Resp. - SUP
d29df31a-fc39-593b-8e41-54577d3aba08 | note | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0002
e346eb22-169c-5665-a615-7f9c6d3f739b | note | • AEC-NZ1005-STE-SCH-ELE-0004
475a3d88-b387-586f-b5c1-31e387b3a661 | note | • AES-NZ1005-STE-ITP-PMT-0022
b977411c-89e0-5b65-ab12-147f4a933372 | note | • AS/NZS 3000:2007
5c835dfc-bd5b-5193-b367-99ba5486b7a7 | note | Conformance Criteria - Installed as per cable schedule on cable tray & inground conduits & pull pits.
979156f9-20dd-5a74-ad28-e0ecdbafbe11 | note | • Installed & terminated.
40af18eb-9424-54f0-b552-b9f0aad8f77c | note | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
9de19714-7bda-5380-996e-c6a2c350dd88 | note | Method - V + FM
648e20d6-33e6-5cde-a443-87996f14de36 | note | Frequency - Once
a1cef41f-a990-51e9-8e01-93de7b6d08a8 | note | WP - AES
bff6cbae-2cca-5cde-ae10-62c50b9b187b | note | Records - Check Sheet + ITP
| checkpoint | Carpark DBs Installed
aa53ad56-9b9a-58d3-ab59-0f308894ba2f | note | • HRO
9ce64755-b6de-5982-8116-e862dc91d370 | note | • UT1
8e91f37f-2e7f-5f7d-adc0-bf6a5502c93b | note | • STA
b74dfcbf-5694-5b3a-8ae6-a245c58bf674 | note | Resp. - SUP
1a3d8ac4-a4c3-5954-870d-55ea219aac07 | note | Conformance Criteria - Location as per drawings
01ad00c4-0326-5903-a163-fa961e109ab8 | note | • Plinths installed & grouted around conduit
55923de1-b9a2-5be0-a3d1-1a1e947b602f | note | • Conduits cut down for DB install
39308be6-32d0-5133-b4cb-3b49c27a4beb | note | • DB placed & fixed to plinth
c4dc44f9-5cbe-5618-ba66-49fe2dfd94b8 | note | Method - V
2421f963-0783-5869-be0d-b0e38ef39fa0 | note | Frequency - Each Location
88831cbf-0cf8-5945-a6e2-f173372ff932 | note | WP - AES
46f09170-4fee-52bd-adf7-728b5097afe8 | note | Records - Check Sheet + Photo
| checkpoint | Submains Terminated to DBs
2431f31e-229b-595b-8e20-3e364d9ecd37 | note | • DB-STE-EV1 (HRO)
3d8c2b90-c856-5698-9108-9287f1979ead | note | • DB-STE-EV2 (UT1)
936a8df6-a408-5bb8-b5a6-4f8e43430f5c | note | • DB-STE-EV3 (STA)
20105c13-d046-5814-9086-b6711decfd7a | note | Resp. - SUP
df302120-29d3-56b7-8976-0559dacf8f30 | note | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0004, AES-NZ1005-STE-ITP-PMT-0022, AS/NZS 3000:2007
99f69dea-1be7-5209-ada6-3ce389f6609d | note | Conformance Criteria - Installed as per cable schedule on cable tray & inground conduits & pull pits.
e9689c69-0fa3-50c5-b40b-049af4727e5a | note | • Installed & Terminated.
9dc73c47-6385-58ac-b3cd-c98a3908fd03 | note | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
6bb9008e-d7ab-5b60-adaa-c1c73c793761 | note | Method - V + FM
6144be71-18af-5291-ab33-a6e8af027c45 | note | Frequency - Each Location
0e3e1fa1-4afe-5bd3-bec9-9bd6a23b33e4 | note | WP - AES
45b78bf4-1ad5-593e-9235-5865c28129d5 | note | Records - Check Sheet
| checkpoint | MSB-3 Pre-Livening Checks Complete - LJE/AES/CPB Hold Point
9d2a40b2-97de-5645-97a7-6063abb90809 | note | Resp. - SUP
71ee5c70-1a9c-5d4a-a5e5-19d582ccfbf1 | note | Referenced Documentation - LJE-UT1 MSB3 AS/NZS 3000:2007
3f3f911f-febb-5a79-a397-6ef29c64d382 | note | Conformance Criteria - As per LJE commissioning Plan
90cd5739-3f11-542c-8c16-e11e0c6426ab | note | • MSB-3 Main Switch & Sub Circuit breakers Isolated
0486dcaa-d2a0-5995-981f-60dd99f15285 | note | • Safe to Liven Mains from TX3 to MSB3
d863698c-c44d-506b-9683-5e4bb253d8f8 | note | Method - V + DR
b44af7ac-8bf3-5825-a812-57c29d97ba43 | note | Frequency - Once
f3274b89-0253-5d47-ae65-c4b6657f1e6d | note | Hold Point - LJE / AES / CPB
20fa5fe1-77ab-5a3e-8373-f769cb780a00 | note | Records - Check Sheet + CMP
| signoff | Request Signoff/ Raise Remedial
| checkpoint | HV Switching TX3 - AES/CPB Hold Point
da94938a-9050-5a5f-a255-9a32b7fb8dc9 | note | Resp. - SUP
45c9918d-5d83-5f6d-a92e-1025280b6dcd | note | Conformance Criteria - HV Switching confirmed by CPB
83da49be-13f8-5ea1-a0d4-174b795e4e4f | note | Method - V
1542a109-8d81-555a-9cff-e7aa8456b496 | note | Frequency - Once
ef298e77-89ae-50b6-b457-806e6dcc9de6 | note | Hold Point - AES / CPB
a663831b-9f9a-5e5a-95a2-fd5ecab321da | note | Records - Check Sheet
| signoff | Request Signoff/ Raise Remedial
| checkpoint | MSB-3 Energisation & Commissioning - CPB Hold Point
f4b12440-1505-553d-9206-2c6e41880c7b | note | Resp. - SUP
1126fd2a-25f3-5048-bb60-c2ae44df627c | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0022, LJE-UT1 MSB3, AS/NZS 3000:2007
aa3ab7ea-2d86-5d7b-9211-7961a249f034 | note | Conformance Criteria - Live cable testing on MSB-3 as per AES-NZ1005-STE-ITP-PMT-0022
e6bf37c8-0a7a-5773-910d-7ece19ecbc4c | note | • Main Switch Isolation removed.
ed2536f0-a119-5647-b5b9-c98ac4ffaa1a | note | • MSB-3 commissioned as per LJE commissioning plan
28d1e227-7e90-524e-90eb-77eecb6565d1 | note | Method - V + FM + DR
7b09b3bb-fdb7-59d6-8790-273a88331bc6 | note | Frequency - Once
154a8b59-70dd-543d-9dae-d4ffdb87ff68 | note | WP - AES
bf658391-9ea1-5361-8e42-f5b38e0bb1ac | note | Hold Point - CPB
c9056da9-de55-57aa-a1e5-7218e05df5da | note | Records - Check Sheet + ITP + CMP + COC
| signoff | Request Signoff/ Raise Remedial
| checkpoint | Site DBs Pre-Livening Checks Complete - LJE/AES/CPB Hold Point
1af9f728-7a3d-5226-a733-1a04d3c36549 | note | Resp. - SUP
5c3e796f-244a-5272-a689-a3c6a8d68f07 | note | Referenced Documentation - LJE-UT1 MSB3 AS/NZS 3000:2007
388658c3-6655-5240-921b-8240546940f9 | note | Conformance Criteria - As per LJE commissioning Plan
811641bf-d060-5c2e-846c-1f108bc1c238 | note | • DB Main Switch & Sub Circuit breakers Isolated
0ecb4587-1235-5fa8-a796-b768deae9c9d | note | • Safe to Liven Mains from MSB-3 to DBs
538f4b5b-f4e7-5149-8a8f-4e55ac2f0a10 | note | Method - V + DR
fa59e841-b85a-5017-b8b7-d7e3049e721e | note | Frequency - Each Location
353ba449-1fca-55aa-930c-98a1ea61616f | note | Hold Point - LJE / AES / CPB
5e6cd20b-711b-5d80-8882-a44373019334 | note | Records - Check Sheet + CMP
| signoff | Request Signoff/ Raise Remedial
| checkpoint | Site DBs Energised & Commissioned - CPB Hold Point
7563456f-ddf4-5c3b-ab55-84c25568db74 | note | • DB-STE-EV1 (HRO)
cca57b80-80f5-5e91-80ff-c8c5ddbecb7e | note | • DB-STE-EV2 (UT1)
1177877e-97e5-5bbb-994b-1a60724a30b9 | note | • DB-STE-EV3 (STA)
3e04888b-8419-5367-b593-e4d889043745 | note | Resp. - SUP
a322d2ca-3caa-5ea9-817a-86bef8f64b02 | note | Referenced Documentation - AES-NZ1005-STE-ITP-PMT-0022 LJE-UT1 MSB3 AS/NZS 3000:2007
8345c941-424c-5722-850b-a3483cd11555 | note | Conformance Criteria - Live cable testing on DBs as per AES-NZ1005-STE-ITP-PMT-0022
5fe4d52f-e7b0-5e54-a8df-272c4365578e | note | • Main Switch Isolation removed.
fb7fef2d-4701-5bfa-930e-8f4b1844b0f0 | note | • DBS commissioned as per LJE commissioning plan
cf307b6b-e64c-5967-aeaa-a86a83d6b10c | note | Method - V + FM + DR
dd6bfe21-4574-577a-a7e6-526ce7c41b0c | note | Frequency - Each Location
4e8185d6-d9d0-5d06-afb4-0e1e00624917 | note | WP - AES
5069f85c-786a-506b-90ad-c0bf180257c7 | note | Hold Point - CPB
91d28c92-6265-543d-9c01-c436f1657c0a | note | Records - Check Sheet + ITP + CMP + COC
| signoff | Request Signoff/ Raise Remedial
| section | Communication Install
| checkpoint | Communications conduits Install
8099d362-622d-5e44-a79c-1824c0d1ac0b | note | Resp. - SUP
5528ded3-8d2c-56df-94bd-26b8510126c3 | note | Referenced Documentation - Refer AES-NZ1005-STE-ITP-PMT-0008
08488f95-c57c-55f5-9403-7066c8c1a960 | note | Conformance Criteria - Complete as per the referred ITPs
a730f5ed-2ddd-536a-b3f8-c0832f71f5cc | note | Method - DR
584a51de-975d-56d1-bc10-428f6912c930 | note | Frequency - Once
76adc419-e923-5cdc-9913-64687eeae122 | note | WP - AES
f7f6b892-1939-5f80-af9d-ca3e40a81ef6 | note | Records - Check Sheet + ITP
| section | EV Charger Plinth Install
| checkpoint | Foundations & Plinths Installed
31cdd244-27c7-5932-83aa-87b4ba839925 | note | Resp. - SUP
fc596384-b03d-5a39-942b-9c049570c9df | note | Referenced Documentation - AES-NZ1005-STE-DSH-ELE-0034
e61dc38f-ea5a-5fbb-a616-d9d285966644 | note | Conformance Criteria - Foundations for ABB wall charger pedestals installed to approved specification.
1e841f67-0f1e-5a71-aabe-e2810480f4b4 | note | • Precast plinths for ABB T54
5ccdafce-8616-562d-8cc4-24bf4499ed13 | note | • Chargers installed at HRO & STA carparks
88171ed9-d7cf-5963-82de-cfea49cb0d8e | note | Method - Each location
4ce42391-c4cb-53fb-a361-a97fb30023d1 | note | Frequency - V
b9d1818e-85c9-5a85-a23e-dff670af28f4 | note | WP - AES
80ad5a22-a327-59c7-a2f6-d3c37551e7da | note | Records - Check Sheet + Photos
| checkpoint | Low Voltage Cables Installed - AES Hold Point
c406ff10-daab-59de-82ba-6645ceb68886 | note | Resp. - SUP
5f1c740e-9047-5148-b293-2a7ea9b8a620 | note | Referenced Documentation - AEC-NZ1005-STE-SCH-ELE-0004, AES-NZ1005-STE-ITP-PMT-0022, AS/NZS 3000:2007
735ced17-fe08-53ef-a9ca-064ee798079e | note | Conformance Criteria - Installed as per cable schedule through inground conduits & pull pits.
d179fd5a-32a6-55a0-bb8f-b082f40a2ccc | note | • Pre-livening tests ONLY as per AES-NZ1005-STE-ITP-PMT-0022
c3d7ea7e-74a2-5943-b615-45d5e1f4b5f5 | note | • Communication & Charger control cables run to each location from DBs
e60ceb28-8648-58ed-88f8-2763eac77222 | note | Method - Each location
91160baf-21b3-5f64-8fdd-90f53daeb06a | note | Frequency - V + DR + FM
57aaf761-8122-5c42-a161-4489d2f92ebd | note | Hold Point - AES
5fc0994b-4ba7-5685-831b-bc4af3e43bed | note | Records - Check Sheet + Photos + ITP
| section | Completion Test & Record
| checkpoint | Works Completion Test WCT 54 - AES/CPB/IR Hold Point
e43633f7-2111-5dfd-830d-643cb3e20027 | note | Resp. - SUP
8e379438-61d6-5e8b-9eb0-055b6f0214bf | note | Referenced Documentation - Schedule 11 WCT 54 (e)(f) AS/NZS 3000:2007
0c40ae5f-0dcd-5c7c-9709-ed16e84558f1 | note | Conformance Criteria - The EIS for the New Waikeria Facility have been installed in accordance with the FDD. This includes EIS testing and satisfactory commissioning (including interfaces with other services) has been completed, recorded and compliance results presented to the Independent Reviewer for the following systems:
89b98e89-bd4a-55f5-9a30-638337d54679 | note | (e) general power;
0cffcf95-5b0c-506b-8cd3-f3b8aa45145d | note | (f) earthing system;
9faf2311-9514-58f1-90fe-3cc1b76b9b6b | note | Method - FTR + V + DR
572e8e1d-d4bd-5293-9b27-33904f6f8dbc | note | Frequency - Once
216f163e-ca57-52ea-922f-8e6aba21a16a | note | WP - AE Smith + LJE
022512fa-c60d-50a0-91f9-b602c5af6882 | note | Hold Point - AES / CPB / IR
92810934-a012-540a-a265-557b8e81efa0 | note | Records - Check Sheet + QA documents + COC
| signoff | Request Signoff/ Raise Remedial
| checkpoint | Works Completion Test WCT 83 - AES/CPB/IR Hold Point
50d7af13-af8b-5e2e-9299-929a3e5e053d | note | Referenced Documentation - Schedule 11 WCT 83 Cable pull pits
5828bfcd-84c1-5ecb-950c-45367e61458a | note | Conformance Criteria - Cable Pull pits inside the primary physical barrier are accessible for maintenance and have locking type bolt down metal covers
7cfb84cc-80f6-562c-9b3d-bf352ff3c222 | note | Method - DR
e947e737-577e-5a11-abb8-5b71664042a7 | note | Frequency - On completion of installation
c157fd59-2f45-5dd1-9b70-987ff387d228 | note | WP - AES / Downer
a9744d89-62cf-5170-b550-123579870f56 | note | Hold Point - AES / CPB / IR
d5027048-cc73-5061-9a3b-f335d5a6f590 | note | Records - Check Sheet
| signoff | Request Signoff/ Raise Remedial
| checkpoint | Conformance records
9801b514-b296-50de-89ac-fc2e621ba28b | note | Resp. - SUP
e1b45a6f-0b8f-5655-8f30-c4468744547d | note | Conformance Criteria - All relevant records will be provided and demonstrate compliance with project requirements
71b6cd10-f038-54d3-bb36-66f4f4263d84 | note | Method - DR
3312f2de-6720-5ab7-a681-4d393a3f0126 | note | Frequency - Each Lot
74ab3cb6-8629-5dd6-a8f7-fe72bfc3cd64 | note | WP - AES
b49ea2fe-0441-57b6-8a06-3502c183a836 | note | Records - Check Sheet
| checkpoint | As-built Survey
3aee5a7e-b4ec-5b02-a6fc-1fe789b073f3 | note | Resp. - SUP
342ed8a9-0597-5f92-bd0e-40c6ba81211a | note | Referenced Documentation - NZT5007-SSS-CSSP-0001
7aef61ac-740e-51d5-8721-a4aa55a7ea5f | note | Conformance Criteria - As Built Completed
eb74a9b6-fe9c-5eaf-a209-e969cef8abd3 | note | Method - DR
224eae8e-2de0-5016-89b5-cb298a1a8e21 | note | Frequency - Each Lot
3a8c1339-f30b-5915-ab0c-460614c1b32e | note | WP - AES
b125e6dd-245c-5346-8657-d14c27eb9bd1 | note | Records - Check Sheet