## ITC 001
ITC 001 - MAIN SWITCHBOARD INSTALLATION CHECKLIST
Pre cable termination
Section 1: Installation inspection checklist
Current approved workshop drawings available on site database | [5 empty] | Yes/ No
Approved factory acceptance testing documents available on site data base | [5 empty] | Yes/ No
Switchboard installed in final location as per approved drawings | [5 empty] | Yes/ No
Switchboard manufacturer Site acceptance testing complete and signed off and available on site data base | [5 empty] | Yes/ No
Confirm labels are correct | [5 empty] | Yes/ No
Confirm Earthing connections are correct | [5 empty] | Yes/ No
Busbar connections: Confirm Connections are torqued to manufacturers specifications and witness marks applied where visible | [5 empty] | Yes/ No
Confirm control wiring is installed as per current approved drawings | [5 empty] | Yes/ No
Confirm each cubicle is from dust and foreign debris | [5 empty] | Yes/ No
Confirm door seals intact | [5 empty] | Yes/ No
Confirm door handles and hinges operate correctly, verify locking | [5 empty] | Yes/ No
Undertake functional testing of all isolators - document results on ITC 019 | [5 empty] | Yes/ No
Undertake functional testing of all circuit breakers -results on ITC 019 | [5 empty] | Yes/ No
Confirm Multiple Earth Neutral Link (where Fitted) | [5 empty] | Yes/ No
All cubicles open/check list signed UNTERMINATED SECTION OF ITC 004 | [5 empty] | Yes/ No
Photos taken of all cubicles | [9 empty] | Photos
Section 2: Busbar insulation testing, all results less than 1MΩ is classed as a fail
L1-EARTH | Text box P/F | MΩ | L2-EARTH | Text box P/F |  | MΩ | L3-EARTH |  | Text box P/F |  | MΩ | NEUTRAL-EARTH |  | Text box P/F | MΩ
L1- L2 | Text box P/F | MΩ | L1-L3 | Text box P/F |  | MΩ | L3-L2 |  | Text box P/F |  | MΩ
L1- NEUTRAL | Text box P/F | MΩ | L2 - NEAUTRAL | Text box P/F |  | MΩ | L3 - NEUTRAL |  | Text box P/F |  | MΩ
Section 3: Switchboard earthing busbar(s) continuity and resistance verification
POINT TO POINT TEST OF SWITCHBOARD |  |  |  |  | SECTION : |  | text box |  |  |  |  | SECTION : | text box
[5 empty] | RESULT Ω : |  | text box |  |  |  |  | RESULT Ω : | text box
Test Equipment Type i.e. Multimeter |  | Brand/Model |  |  | Serial No. |  |  | Calibration Due
text box |  | text box |  |  | text box |  |  | text box
text box |  | text box |  |  | text box |  |  | text box
COMMENTS:
The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
FINAL ACCEPTANCE:
Final Acceptnce - email