## ITC 006
ITC 006 Commissioning of Light and Power Circuits
Referenced Drawing and Revision Number |  | text box
Section 1 :Test and Commissioning Activities as per AS3000 & AS3017
|  | Circuit Destination / Circuit Designation | Number of Points per Circuit | ITC - 20 & ITC - 33 Complete. If not STOP until complete | Visual Inspection to confirm all points are installed | DE-ENERGISED TESTS | [8 empty] | ENERGISED TESTS DE-ENERGISED SECTION TO BE COMPLETED AND SINGED FIRST
RCD Rating | RCD Location |  |  |  |  | Confirmation all labels are installed | Earth Continuity Ω | Polarity/ Phasing |  |  | Insulation Resistance Readings Anything less then 1M ohm is classed as a fail |  |  |  | Voltage Readings |  |  |  | < > | RCD PUSH BUTTON TEST | RCD TRIP TIME TEST mSec |  | Fault Loop Impedance - not required for RCD protected socket outlets | Has a CCEW/CES been completed?
mA | [7 empty] | PH | N | E | MΩ PH - E | MΩ PH - N | MΩ N - E | MΩ PH - PH | PH-N Volts | PH-E Volts | N-E Volts | 3 phase Voltage | Phase Rotation | Pass | 0° | 180° | Ω
text box | DB/ Field | text box | text box | Y/N | Y/N | Y/N | text box | text box | text box | text box | text box | text box | text box | text box | text box | text box | text box | text box | text box | Pass/Fail | text box | text box | text box | Y/N
[11 empty] | P/F | P/F | P/F | P/F
Section 2: Test equipment register
|  | Test Equipment Type | Make/ model |  | Asset Number | Serial No. | Next Calibration due
|  | Text box | text box |  | text box | text box | text box
|  | Text box | text box |  | text box | text box | text box
|  | Text box | text box |  | text box | text box | text box
|  | Text box | text box |  | text box | text box | text box
Comments
The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
Final acceptance email