## Sheet1
ELECTRICAL SERVICES INSPECTION AND TEST RECORD
ITC 010 - INSPECTION AND TEST RECORD FOR: INGROUND CONDUITS
Referenced Drawings and Revision Number
INGROUND CONDUITS AND UNDERGROUND SERVICES INSPECTIONS
Item | Field Type | Hold Point
Description of Work Area | Text box
Attach mark-up of work area | File Upload
Investigation of Existing Services Completed, including review of existing services documentation & BYDA drawings and service scan | Checkbox - Yes / N/A (Please provide comment) Text box
Validation of Imported Material undertaken as per RAP requirements. Upload material validation certificate. | File upload
Set-out inground conduits, pits and any other items in accordance with the IFC documentation ahead of commencing excavation | Checkbox - Yes / N/A (Please provide comment) Text box
Excavate to design levels. Check that minimum cover requirements are achieved (650mm minimum cover for LV & 300 for comms) | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Inspect trench and ensure it is free from sharp materials | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Place bedding sand in bottom of trench. Check that 50mm bedding sand is achieved. | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Place conduits, glue and pull through draw wire | Checkbox - Yes / N/A (Please provide comment) Text box
Verification of correct conduit sizeas per IFC documentation. | Checkbox - Yes / N/A (Please provide comment) Text box
Take photos of conduits prior to backfill. | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Surveyor to survey conduits prior to backfill. | Checkbox - Yes / N/A (Please provide comment) Text box | HOLD POINT - email
Principle contractor to inspect conduits prior to backfill. | Checkbox - Yes / N/A (Please provide comment) Text box | HOLD POINT - email
Place and compact sand to 300mm above the top of conduits. | Checkbox - Yes / N/A (Please provide comment) Text box
Place warning tape. | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Place and compact suitable material to remaining depth of trench. | Checkbox - Yes / N/A (Please provide comment) Text box
Undertake compaction testing per the civil documentation. | Checkbox - Yes / N/A (Please provide comment) Text box | photo
Pits cleaned and free of holes. Refer to ITC 10A | Checkbox - Yes / N/A (Please provide comment) Text box
Attach as-built survey | File Upload & text box (optional comments)
Attach any other relevant items (optional) | File Upload & text box (optional comments)
Grid final acceptance | Checkbox - Yes / N/A (Please provide comment) Text box | HOLD POINT - email
Client to review completed ITC and confirm acceptance | Checkbox - Yes / N/A (Please provide comment) Text box | HOLD POINT - email