## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | CCEW Attachment | [5 empty] | Upload CCEW Attachment
section | Details
checkpoint-no-status | ATTACHMENT:
checklist | ITC 001 - Main Switchboard Installation Checklist
section | Section 1: Installation inspection checklist
checkpoint | Current approved workshop drawings available on site database
checkpoint | Approved factory acceptance testing documents available on site data base
checkpoint | Switchboard installed in final location as per approved drawings
checkpoint | Switchboard manufacturer Site acceptance testing complete and signed off and available on site data base
checkpoint | Confirm labels are correct
checkpoint | Confirm Earthing connections are correct
checkpoint | Busbar connections: Confirm Connections are torqued to manufacturers specifications and witness marks applied where visible
checkpoint | Confirm control wiring is installed as per current approved drawings
checkpoint | Confirm each cubicle is from dust and foreign debris
checkpoint | Confirm door seals intact
checkpoint | Confirm door handles and hinges operate correctly, verify locking
checkpoint | Undertake functional testing of all isolators - document results on ITC 019
checkpoint | Undertake functional testing of all circuit breakers -results on ITC 019
checkpoint | Confirm Multiple Earth Neutral Link (where Fitted)
checkpoint | All cubicles open/check list signed UNTERMINATED SECTION OF ITC 004
checkpoint | Photos taken of all cubicles
section | Section 2: Busbar insulation testing, all results less than 1MΩ is classed as a fail
checkpoint | L1 - EARTH
textbox | MΩ
checkpoint | L2 - EARTH
textbox | MΩ
checkpoint | L3 - EARTH
textbox | MΩ
checkpoint | NEUTRAL - EARTH
textbox | MΩ
checkpoint | L1 - L2
textbox | MΩ
checkpoint | L1 - L3
textbox | MΩ
checkpoint | L3 - L2
textbox | MΩ
checkpoint | L1 - NEUTRAL
textbox | MΩ
checkpoint | L2 - NEUTRAL
textbox | MΩ
checkpoint | L3 - NEUTRAL
textbox | MΩ
section | Section 3: Switchboard earthing busbar(s) continuity and resistance verification
checkpoint | POINT TO POINT TEST OF SWITCHBOARD
textbox | SECTION:
textbox | RESULT Ω:
textbox | SECTION:
textbox | RESULT Ω:
textbox | Test Equipment Type i.e. Multimeter
textbox | Brand/Model
textbox | Serial No.
date | Calibration Due
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 002 - Main Switchboard Pre Energisation Test Report
section | Details
checkpoint | Confirm ITC 001 has been completed and signed off
checkpoint | Confirm section 4 of ITC 005 has been completed and signed off
checkpoint | Confirm ITC - 019 has been completed and signed off
checkpoint | Referenced Drawing Number and Revision
checkpoint | Configuration installed as per approved drawings.
checkpoint | Correct cable glands used.
checkpoint | Cables terminated correctly, Lugs crimped as per manufacturers specifications.
checkpoint | All cable terminations bolted and correctly tensioned according to manufactures specifications, and witness marks applied.
checkpoint | All cables restrained in switchboards
checkpoint | All Cables visually inspected, ensuring cable sheathes are intact and in good condition.
checkpoint | Cables are labelled correctly at origin and destination as per schedule.
checkpoint | Cables are terminated at destination, and made safe.
checkpoint | If cables are not terminated at the destination, remove from breaker and make safe
checkpoint | All Exposed conductors are covered or protected in cubicle or terminal box.
checkpoint | Switchboard is clean and free access is available around the board
checkpoint | All cubilces of the switchboard are sealed
checkpoint | Final Visual Inspection undertaken by Senior GRiD representative.
holdpoint | Signoff
checkpoint | Supply Authority or Regulatory Body inspection completed
date | Date completed:
checkpoint | All works complete in switchboard
checkpoint | All switchboard doors, escutcheons and covers reinstated and locked ready for energisation.
checkpoint | Notice of intent to energise form complete and signed by Principle Contractor
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 004 - Switchboard Cubicle Checklist
section | Section 1: Cubicle Checklist
checkpoint-no-status | CUBCLE REF
textbox | CUBCLE REF #
checkpoint | UN-TERMINATED
button | OPENED | Yes,No
button | FREE OF DEBRIS | Yes,No
checkpoint | TERMINATED
button | CABLES TERMINATED | Yes,No
button | CLEAN/FREE OF DEBRIS | Yes,No
button | SEALED | Yes,No
checkpoint-no-status | COMMENTS:
label | The above Electricians working for GRiD ELECTRICAL SERVICES Pty Ltd Certify the Electrical installation corresponding beside relevant Electrician’s name, has been tested and verified to ensure it is electrically safe and is in accordance with the wiring rules and any other standard applying to the electrical installation under the Electrical Safety Acts of that particular state/Territory at the date that the test was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 005 - Main, Submain & Consumer Main Test Record
section | Details
checkpoint-no-status | Referenced Drawings and Revision Number
textbox | Referenced Drawings and Revision Number:
section | Section 1: Cable details
checkpoint-no-status | Cable details
textbox | Cable Identification
textbox | Cable size and type:
textbox | Cable installation method
textbox | Cable origin:
textbox | Approximate length:
textbox | Cable thermal rating
textbox | Cable destination:
textbox | Number of cores/configuration
textbox | Supplies Life Support Services?
section | Section 2: Cable protection details
checkpoint-no-status | Cable protection details
textbox | Protection type and details
textbox | Breaking Rating (KA)
textbox | Protection device ID
textbox | Short time overload (Short Circuit)
textbox | Protection rating (A)
textbox | Long time overload (Thermal Overload)
section | Section 3: Visual Inspection of Cable according to AS/NZS 3000 and AS/NZS 3017
checkpoint | Confirm that the cable is provided with adequate support and secured across the cables entire length, ensuring the cable does not move under fault conditions and installed according to prescribed methods.
checkpoint | Confirm that the cable used is as per the current cable schedule, confirm if the cable is installed as per drawings current drawings.
checkpoint | Confirm that the cable is protected against mechanical damage, environmental and other external influences.
checkpoint | Confirm cables are correctly labled at requisite points.
checkpoint | Confirm that the cable is terminated at both ends and that exposed parts covered. If this cannot be achieved sub mains are to be removed at both ends and made safe
checkpoint | Confirm that the cable does not impact or interfere with other services.
section | Section 4: Non-Energised testing according to AS/NZS 3000 and AS/NZS 3017
checkpoint | 4.1 MAIN EARTH CONTINUITY & RESISTANCE TEST
textbox | EARTH SIZE |  |  | mm2
textbox | FROM
textbox | TO
textbox | POINT TO POINT READING Ω |  |  | Ω
checkpoint-no-status | 4.2 INSULATION RESISTANCE TEST VALUE MUST BE GREATER THEN 1MΩ AT 500V DC
checkpoint | L1 - EARTH
textbox | MΩ
checkpoint | L2 - EARTH
textbox | MΩ
checkpoint | L3 - EARTH
textbox | MΩ
checkpoint | NEUTRAL - EARTH
textbox | MΩ
checkpoint | L1 - L2
textbox | MΩ
checkpoint | L2 - L3
textbox | MΩ
checkpoint | L1 - L3
textbox | MΩ
checkpoint | L1 - NEUTRAL
textbox | MΩ
checkpoint | L2 - NEUTRAL
textbox | MΩ
checkpoint | L3 - NEUTRAL
textbox | MΩ
checkpoint-no-status | 4.3 Polarity testing measurement of cable origin to end
checkpoint | L1 TO L1
checkpoint | L2 TO L2
checkpoint | L3 TO L3
checkpoint | N TO N
checkpoint | 4.4 Isolation padlock/ tag installed on the main switch of field device i.e distribution board
section | Section 5: ENERGISED testing according to AS/NZS 3000 and AS/NZS 3017
checkpoint | Confirm ITC 002 has been completed
checkpoint | Confirm that all terminations are installed as per the termination specifications, and that connections are torqued to rated specifications with witness marks fitted for future reference.
checkpoint | Known Live source
textbox | V
checkpoint | L1 - Earth
textbox | V
checkpoint | L2 - EARTH
textbox | V
checkpoint | L3 - EARTH
textbox | V
checkpoint | L1 - L2
textbox | V
checkpoint | L1 - L2
textbox | V
checkpoint | L3 - L1
textbox | V
checkpoint | NEUTRAL - EARTH
textbox | V
checkpoint | L1 - NEUTRAL
textbox | V
checkpoint | L2 - NEUTRAL
textbox | V
checkpoint | L3 - NEUTRAL
textbox | V
checkpoint | Known Live source
textbox | V
checkpoint | 5.2 Phase Rotation testing according to AS/NZS 3000 and AS/NZS 3017
button | CLOCK WISE 1-2-3 | Yes,No
button | COUNTER CLOCK WISE 3-2-1 | Yes,No
checkpoint | 5.3 Fault loop Impedance testing according to AS/NZS 3000 and AS/NZS 3017
textbox | MEASURED IMPEDANCE VALUE Ω |  |  | Ω
textbox | CALCULATED MAXIMUM VALUE (Ω) as per the cable schedule report |  |  | Ω
section | Section 6: Test equipment register
checkpoint | Test equipment register (1)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Last Calibration
textbox | Next Calibration due
textbox | Tester
date | Date
checkpoint | Test equipment register (2)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Last Calibration
textbox | Next Calibration due
textbox | Tester
date | Date
checkpoint | Test equipment register (3)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Last Calibration
textbox | Next Calibration due
textbox | Tester
date | Date
checkpoint | Test equipment register (4)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Last Calibration
textbox | Next Calibration due
textbox | Tester
date | Date
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 006 - Commissioning of Light and Power Circuits
section | Section 1: Test and Commissioning Activities as per AS3000 & AS3017
checkpoint-no-status | Details
textbox | RCD Rating |  |  | mA
textbox | RCD Location |  |  | DB/ Field
textbox | Circuit Destination / Circuit Designation
textbox | Number of Points per Circuit
button | ITC - 20 & ITC - 33 Complete. | Yes,No
label | If not STOP until complete
button | Visual Inspection to confirm all points are installed | Yes,No
section | DE-ENERGISED TESTS
checkpoint | Confirmation all labels are installed
textbox | Earth Continuity Ω
checkpoint | Polarity/ Phasing
textbox | PH
textbox | N
textbox | E
checkpoint-no-status | Insulation Resistance Readings
label | Anything less then 1M ohm is classed as a fail
checkpoint | PH - E
textbox | MΩ
checkpoint | PH - N
textbox | MΩ
checkpoint | N - E
textbox | MΩ
checkpoint | PH - PH
textbox | MΩ
section | ENERGISED TESTS (DE-ENERGISED SECTION TO BE COMPLETED AND SIGNED FIRST)
checkpoint-no-status | Voltage Readings
textbox | PH-N |  |  | Volts
textbox | PH-E |  |  | Volts
textbox | N-E |  |  | Volts
textbox | 3 phase |  |  | Voltage
checkpoint | < >
textbox | Phase Rotation
checkpoint | RCD PUSH BUTTON TEST
checkpoint | RCD TRIP TIME TEST
textbox | 0° |  |  | mSec
textbox | 180° |  |  | mSec
checkpoint | Fault Loop Impedance - not required for RCD protected socket outlets
textbox | Ω
checkpoint | Has a CCEW/CES been completed?
section | Section 2: Test equipment register
checkpoint | Test equipment register (1)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Next Calibration due
checkpoint | Test equipment register (2)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Next Calibration due
checkpoint | Test equipment register (3)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Next Calibration due
checkpoint | Test equipment register (4)
textbox | Test Equipment Type
textbox | Make/ model
textbox | Asset Number
textbox | Serial No.
textbox | Next Calibration due
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 007 - Conduits In Slab and Walls
section | Referenced drawings and revision number
checkpoint-no-status | Details
textbox | Referenced drawings and revision number
section | Section 1 - Inspection
checkpoint-no-status | LEVEL / AREA
textbox | LEVEL / AREA
checkpoint | CORRECT DRAWING USED FOR MARKING OUT
checkpoint | CORRECT SIZE AND TYPE OF CONDUIT INSTALLED
checkpoint | APPLICATION OF GLUE TO ALL JOINS AND BOXES
checkpoint | SUFFICIENT TIES & CHAIRS ALONG CONDUIT RUNS
checkpoint | ANY VERTICAL CONDUITS CAPPED OFF
checkpoint | CLEARANCE FROM OTHER SERVICES
checkpoint | CHECK SUFFICIENT SPACING BETWEEN CONDUITS
label | Add photo
checkpoint-no-status | PHOTOS
label | Attach photos
checkpoint | CONFIRM ALL POINTS ARE LOCATED AS PER THE DRAWINGS
checkpoint | CONDUITS INSPECTED FOR BREAKS PRIOR TO CONCRETE POUR
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 010 - Inground Conduits
section | Referenced Drawings and Revision Number
checkpoint-no-status | Details
textbox | Referenced Drawings and Revision Number
section | INGROUND CONDUITS AND UNDERGROUND SERVICES INSPECTIONS
checkpoint-no-status | Description of Work Area
textbox | Description:
checkpoint-no-status | Attach mark-up of work area
checkpoint | Investigation of Existing Services Completed, including review of existing services documentation & BYDA drawings and service scan
checkpoint-no-status | Validation of Imported Material undertaken as per RAP requirements. Upload material validation certificate.
checkpoint | Set-out inground conduits, pits and any other items in accordance with the IFC documentation ahead of commencing excavation
checkpoint | Excavate to design levels. Check that minimum cover requirements are achieved (650mm minimum cover for LV & 300 for comms).
checkpoint | Inspect trench and ensure it is free from sharp materials
checkpoint | Place bedding sand in bottom of trench. Check that 50mm bedding sand is achieved.
checkpoint | Place conduits, glue and pull through draw wire
checkpoint | Verification of correct conduit sizeas per IFC documentation.
checkpoint | Take photos of conduits prior to backfill.
checkpoint | Surveyor to survey conduits prior to backfill.
holdpoint | HOLD POINT
checkpoint | Principle contractor to inspect conduits prior to backfill.
holdpoint | HOLD POINT
checkpoint | Place and compact sand to 300mm above the top of conduits.
checkpoint | Place warning tape.
checkpoint | Place and compact suitable material to remaining depth of trench.
checkpoint | Undertake compaction testing per the civil documentation.
checkpoint | Pits cleaned and free of holes. Refer to ITC 10A
checkpoint-no-status | Attach as-built survey
checkpoint-no-status | Attach any other relevant items (optional)
checkpoint | Grid final acceptance
holdpoint | HOLD POINT
checkpoint | Client to review completed ITC and confirm acceptance
holdpoint | HOLD POINT
checklist | ITC 012a - Earthing & Bonding
section | Referenced Drawing and Revision Number
checkpoint-no-status | Details
textbox | Referenced Drawing and Revision Number
section | INSPECTION RECORD
checkpoint | Approved construction drawings available
textbox | Origin of Earthing Conductor
textbox | Reinforcement bonding point installed to
checkpoint | Earthing cables secure to wall
checkpoint | Size and installation of Earthbar as per design
checkpoint | Earth cables torqued and marked at Connection points
checkpoint | Earth cables labelled at Connection points
checkpoint | Bonding conductor complete throughtout rooms
checkpoint | Bonding of equipment complete throughout room
textbox | Reinforcement bonding testing complete, results recorded
textbox | Bonding complete for earth bar (test results recorded)
checkpoint | Final Test report suppled and available on site data
section | BONDING CONNECTIONS
checkpoint-no-status | Details
textbox | BONDING CONNECTIONS
section | TEST EQUIPMENT USED FOR VERIFICATION
checkpoint | TEST EQUIPMENT USED FOR VERIFICATION
textbox | Test equipment
textbox | Serial No.
textbox | Calibrated on
checkpoint-no-status | COMMENTS:
label | The electricains noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the inspection/ test was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 015 - Cable Containment and Seismic Restraint Systems
section | Referenced Drawings and revision number
checkpoint-no-status | Details
textbox | Referenced Drawings and revision number
section | Section 1 - Visual Inspection
checkpoint-no-status | Details
textbox | LEVEL / AREA
textbox | DRAWINGS USED - REVISION
checkpoint | TRAY/BASKET CORRECT SIZE FOR APPLICATION AS PER DRAWING
checkpoint | CLEARANCE MAINTAINED FROM OTHER SERVICES (IF TRAY MOVED, CONSULTANTS NOTIFIED
checkpoint | SUPPORT HARDWARE SPACING ADEQUATE OR AS SPECIFIED BY THE SUPPLIER
checkpoint | TRAY/BASKET FREE OF SHARP EDGES AND OTHER DEFECTS
checkpoint | EARTHING REQUIREMENTS AS SPECIFIED HAVE BEEN INSTALLED
checkpoint | TRAY/ BASKET READY FOR CABLE INSTALLATION
checkpoint | RESTRAINTS INSTALLED TO SUPPLIER DRAWINGS/ SPECIFICATION
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 018 - Lighting Lux Levels Test
section | LIGHTING LUX LEVEL
checkpoint-no-status | Referenced Drawings and revision number
textbox | Referenced Drawings and revision number:
checkpoint-no-status | LIGHTING LUX LEVEL
textbox | Room Name / No.
textbox | Result Position 1
textbox | Result Position 2
textbox | Result Position 3
textbox | Result Position 4
textbox | Result Position 5
textbox | Average Result
textbox | Required minimum result
textbox | Time Taken
section | Recommended Illumination levels***
checkpoint-no-status | *** Based on measurements taken at the actual working areas, measurements need to be taken at several points and averaged to gain a accurate overall reading.
checkpoint-no-status | (Location) specific location
textbox | (Office) Conference, reception room |  | Min. lux: 320
textbox | (Office) Clerical work areas |  | Min. lux: 320
textbox | (Office) Typical drafting areas |  | Min. lux: 600
textbox | (Hotel) Public room, Cloakroom |  | Min. lux: 160
textbox | (Hotel) Reception, Cashier |  | Min. lux: 160
textbox | (Factory) Packing work, Entrance Passage |  | Min. lux: 160
textbox | (Factory) Visual work at Production line |  | Min. lux: 240
textbox | (Factory) Inspection work |  | Min. lux: 400
textbox | (Factory) Electronic parts assembly lines |  | Min. lux: 600
textbox | (Hospital) Waiting room, Warehouse |  | Min. lux: 160
textbox | (Hospital) Medical examination room and Operating room |  | Min. lux: 320
textbox | (Hospital) Emergency Treatment area |  | Min. lux: 800
textbox | (Schools) Auditorium, Indoor Gymnasium |  | Min. lux: 160
textbox | (Schools) Class room |  | Min. lux: 320
textbox | (Schools) Laboratory, Library, Drafting room |  | Min. lux: 600
section | LUX MEASUREMENT DEVICE DETAILS
checkpoint-no-status | Details
textbox | Make and model
textbox | Serial
textbox | Last Calibration
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 019 - De-Energised Isolator Circuit Breaker Functionality Test Main Switchboard
section | Referenced Drawing and Revision Number
checkpoint-no-status | Details
textbox | Referenced Drawing and Revision Number
section | Inspection Conditions: Ensure all steps are completed in order
checkpoint-no-status | Details
textbox | Equipment number:
textbox | Rating:
textbox | Type:
textbox | Manufacturer:
textbox | Interlock type:
checkpoint | STEP 1 - Open cubicle and undertake a visual inspection
checkpoint | STEP 2 - Verify the settings against the single line and the cubicle door
checkpoint-no-status | STEP 3 - Verification of circuit contacts in Closed Position
textbox | Switch Closed
checkpoint | A to E
checkpoint | B to E
checkpoint | C to E
checkpoint | A to B
checkpoint | A to C
checkpoint | C to B
checkpoint | A to A
checkpoint | B to B
checkpoint | C to C
checkpoint | A to N
checkpoint | B to N
checkpoint | C to N
checkpoint | N to N
checkpoint | STEP 5 - Visually confirm circuit breaker is in the open position
checkpoint | STEP 6 - Visually confirm the door interlock is in the open position and immediately close the cubicle.
checkpoint | STEP 7 - Re-confirm the operating mechanism in the open position.
checkpoint | STEP 8 - Prove operation of the interlocking device.
checkpoint-no-status | STEP 9 - Document the status of circuit breaker.
button | Status: | Open,Closed
checkpoint-no-status | Equipment Details
textbox | Test Equipment Type
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
checkpoint-no-status | COMMENTS:
label | The electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the above inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the inspection/ test was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 020 - Wall and Ceiling Rough in
section | Referenced drawings and revision number
checkpoint-no-status | Details
textbox | Referenced drawings and revision number
section | Section 1 - Inspection
checkpoint-no-status | Number of points on the circuit
number | Number of points on the circuit:
checkpoint | Is the circuit complete
checkpoint | Power cables installed in correct location
checkpoint | General and Emergency lighting cables installed in correct location
checkpoint | Lighting control cabling installed in correct location? i.e. Darley, Cbus
checkpoint | Segregation of services maintained
checkpoint | Penetrations sealed - Fire proofing completed
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 030 - Distribution Switchboard Installation Checklist
section | Section 1: Installation inspection checklist
checkpoint | Current approved workshop drawings available on site database
checkpoint | Switchboard installed in final location as per approved drawings
checkpoint | Confirm labels are correct
checkpoint | Confirm each cubicle is free from dust and foreign debris
checkpoint | Confirm door seals intact as per approved shop drawings
checkpoint | Confirm door handles and hinges operate correctly, confirm locking
checkpoint | Confirm Earthing connections are correct
checkpoint | Busbar connections: confirm connections are torqued to manufacturers specifications and witness marks applied where visible
checkpoint-no-status | (Switch Closed) Undertake functional testing of all isolators:
textbox | Switch Closed
checkpoint | A to E
checkpoint | B to E
checkpoint | C to E
checkpoint | A to B
checkpoint | A to C
checkpoint | C to B
checkpoint | A to A
checkpoint | B to B
checkpoint | C to C
checkpoint | A to N
checkpoint | B to N
checkpoint | C to N
checkpoint | N to N
checkpoint-no-status | (Switch Open) Undertake functional testing of all isolators:
textbox | Switch Open
checkpoint | A to E
checkpoint | B to E
checkpoint | C to E
checkpoint | A to B
checkpoint | A to C
checkpoint | C to B
checkpoint | A to A
checkpoint | B to B
checkpoint | C to C
checkpoint | A to N
checkpoint | B to N
checkpoint | C to N
checkpoint | Terminations are tight and correctly tensioned with witness marks in place
checkpoint | ITC 005 complete and submitted
checkpoint | All subcircuit breakers are securely mounted and installed with locks
checkpoint | All subcircuit cabling is neatly tied and secure in switchboard with no visible damage
checkpoint | Currently terminated subcircuits are tested, verified and labeled with up to date drawings and documented on ITC 006
checkpoint | Photos taken of all cubicles including torque marks
label | Attach photos
section | Section 2: Busbar insulation testing, all results less than 1MΩ is classed as a fail
checkpoint | L1 - EARTH
textbox | MΩ
checkpoint | L2 - EARTH
textbox | MΩ
checkpoint | L3 - EARTH
textbox | MΩ
checkpoint | NEUTRAL - EARTH
textbox | MΩ
checkpoint | L1 - L2
textbox | MΩ
checkpoint | L1 - L3
textbox | MΩ
checkpoint | L3 - L2
textbox | MΩ
checkpoint | L1 - NEUTRAL
textbox | MΩ
checkpoint | L2 - NEAUTRAL
textbox | MΩ
checkpoint | L3 - NEUTRAL
textbox | MΩ
checkpoint-no-status | Equipment Details
textbox | Test Equipment Type
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | ITC 033 - Low Voltage Fit-off of Final Sub-Circuit Equipment
section | Referenced drawings and revision number
checkpoint-no-status | Details
textbox | Referenced drawings and revision number
section | Section 1 - Inspection of electrical equipment and accessories installed
checkpoint-no-status | Fit off inspection
textbox | Number of points
checkpoint | Installed in Correct Location as per drawings
checkpoint | Has lighting control been installled in correct location
checkpoint | Has the correct equipment i.e. gpo, light, been installed as per the drawing
checkpoint | Fit off into Electrical Equipment or Field Device - no unterminated cables
checkpoint | Mounted Correctly
checkpoint | Area left clean and tidy
checkpoint-no-status | COMMENTS:
label | The Electricians noted above, working for Grid Electrical Services Pty Ltd, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation under the Electrical Safety Act of that particular State/ Territory at the date the test/ inspection was completed.
checkpoint | FINAL ACCEPTANCE:
holdpoint | Signoff
checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - 6 Monthly
section | Details
checkpoint-no-status | Details
textbox | Tag Number
textbox | Construction Board Location
textbox | Fed From
section | Section 1: Switchboard/ Load Centre
checkpoint-no-status | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
label | Load Centres
checkpoint | Readily accessible, i.e. not obstructed in any way
label | Load Centres
checkpoint | Robust construction with a minimum IP23 rating
checkpoint | Complete operational checks of all RCD’s i.e. push the test button
label | Load Centres
checkpoint | Spider boards are not exposed to the weather
checkpoint | Live components are effectively protected (check pole fillers)
label | Load Centres
checkpoint | Insulated Tie bar has been fitted for flexible cords
checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
label | Load Centres
checkpoint | Mounting is secure and stable including secured to the floor
label | Load Centres
checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
label | Load Centres
checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
label | Load Centres
checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
label | Load Centres
checkpoint | Visual indicator of periodic test, i.e. current test tag installed
label | Load Centres
checkpoint | Construction DB Register complete
label | Load Centres
section | Construction Wiring
checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
checkpoint | Permanent wiring in vicinity to be marked “live wiring”
checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
checkpoint | Visually inspect each circuit or sub mains entire route length to verify integrity of the installation as is practicable and safe.
section | Lighting
checkpoint | Adequate access lighting provided, minimum 40 lux
checkpoint | Emergency Lighting over switchboard installed
checkpoint | Lamps protected from mechanical damage
checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
section | Emergency Lighting Battery Test – to be completed every six months
checkpoint-no-status | Circuit Breaker Number
textbox | Circuit Breaker Number:
checkpoint | LED charge indicator is working
checkpoint | Battery Operates for 1 hour
checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
holdpoint | Signoff
checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Annual
section | Details
checkpoint-no-status | Details
textbox | Tag Number
textbox | Construction Board Location
textbox | Fed From
section | Section 1: Switchboard/ Load Centre
checkpoint-no-status | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
label | Load Centres
checkpoint | Readily accessible, i.e. not obstructed in any way
label | Load Centres
checkpoint | Robust construction with a minimum IP23 rating
checkpoint | Spider boards are not exposed to the weather
checkpoint | Live components are effectively protected (check pole fillers)
label | Load Centres
checkpoint | Insulated Tie bar has been fitted for flexible cords
checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
label | Load Centres
checkpoint | Mounting is secure and stable including secured to the floor
label | Load Centres
checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
label | Load Centres
checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
label | Load Centres
checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
label | Load Centres
checkpoint | Visual indicator of periodic test, i.e. current test tag installed
label | Load Centres
checkpoint | Construction DB Register complete
label | Load Centres
section | Construction Wiring
checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
checkpoint | Permanent wiring in vicinity to be marked “live wiring”
checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
checkpoint | Visually inspect each circuits or sub mains entire route length to verify integrity of the installation as is practicable and safe
section | Lighting
checkpoint | Adequate access lighting provided, minimum 40 lux
checkpoint | Emergency Lighting over switchboard installed
checkpoint | Lamps protected from mechanical damage
checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
section | Testing Equipment
checkpoint-no-status | Testing Equipment:
textbox | Serial Number:
textbox | Cert Number:
date | Calibrated Date:
date | Calibrated Due Date:
section | Emergency Lighting Battery Test – to be completed every six months
checkpoint-no-status | Circuit Breaker Number
textbox | Circuit Breaker Number:
checkpoint | LED charge indicator is working
checkpoint | Battery Operates for 1 hour
section | RCD Test – trip time and operational check to be completed on initial installation, then Operational Check monthly and trip time every 12 months
checkpoint | RCD Test (1) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (2) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (3) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (4) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (5) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (6) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint-no-status | Comments:
checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
holdpoint | Signoff
checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Initial
section | Details
checkpoint-no-status | Details
textbox | Tag Number
textbox | Construction Board Location
textbox | Fed From
section | Section 1: Switchboard/ Load Centre
checkpoint-no-status | Construction Switchboards complete ALL check points, Load Centres (lunch shed, site offices etc.) complete noted check points only.
checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
label | Load Centres
checkpoint | Readily accessible, i.e. not obstructed in any way
label | Load Centres
checkpoint | Robust construction with a minimum IP23 rating
checkpoint | Spider boards are not exposed to the weather
checkpoint | Live components are effectively protected (check pole fillers)
label | Load Centres
checkpoint | Insulated Tie bar has been fitted for flexible cords
checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
label | Load Centres
checkpoint | Mounting is secure and stable including secured to the floor
label | Load Centres
checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
label | Load Centres
checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
label | Load Centres
checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
label | Load Centres
checkpoint | Visual indicator of periodic test, i.e. current test tag installed
label | Load Centres
checkpoint | Construction DB Register complete
label | Load Centres
section | Construction Wiring
checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
checkpoint | Permanent wiring in vicinity to be marked “live wiring”
checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
checkpoint | Visually inspect each circuit or sub mains entire route length to verify integrity of the installation as is practicable and safe
section | Lighting
checkpoint | Adequate access lighting provided, minimum 40 lux
checkpoint | Emergency Lighting over switchboard installed
checkpoint | Lamps protected from mechanical damage
checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable
section | Testing Equipment
checkpoint-no-status | Testing Equipment:
textbox | Serial Number:
textbox | Cert Number:
date | Calibrated Date:
date | Calibrated Due Date:
section | Test Report - to be completed on initial installation of Construction Board and visually inspected every six months after
checkpoint-no-status | Details
textbox | Earthing system integrity (Ohms)
label | Insulation resistance (Meg Ohms)
textbox | A-B
textbox | A-C
textbox | A-N
textbox | B-C
textbox | B-N
textbox | C-N
checkpoint | Polarity
checkpoint | Correct Circuit Connections
checkpoint | Suitable for connection to supply
section | Emergency Lighting Battery Test – to be completed every six months
checkpoint-no-status | Circuit Breaker Number
textbox | Circuit Breaker Number:
checkpoint | LED charge indicator is working
checkpoint | Battery Operates for 1 hour
section | RCD Test – trip time and operational check to be completed on initial installation
checkpoint | RCD Test (1) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (2) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (3) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (4) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (5) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint | RCD Test (6) - Operational Check (push button test)
textbox | ID No.
textbox | Description
label | Trip time
textbox | 0*
textbox | 180*
textbox | Sensitivity
checkpoint-no-status | Comments:
checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
holdpoint | Signoff
checklist | WHS-PRO-041 F-03 Construction Switchboard and Wiring Checklist - Monthly
section | Details
checkpoint-no-status | Details
textbox | Tag Number
textbox | Construction Board Location
textbox | Fed From
section | Section 1: Switchboard/ Load Centre
checkpoint | All electrical equipment and lighting/ power supplied from a 30mA RCBO
label | Load Centres
checkpoint | Readily accessible, i.e. not obstructed in any way
label | Load Centres
checkpoint | Robust construction with a minimum IP23 rating
checkpoint | Complete operational checks of all RCD’s i.e. push the test button
label | Load Centres
checkpoint | Spider boards are not exposed to the weather
checkpoint | Live components are effectively protected (check pole fillers)
label | Load Centres
checkpoint | Insulated Tie bar has been fitted for flexible cords
checkpoint | Switchboard/ Load centre door is lockable, non-removable without a tool and fitted with a retention device to stay in the open position
label | Load Centres
checkpoint | Mounting is secure and stable including secured to the floor
label | Load Centres
checkpoint | Where there is more than one breaker, marking provided by means of number, letters or both to distinguish one from the other (unique ID)
label | Load Centres
checkpoint | Marked with appropriate signage such as “danger 240V / 415V”, “lightning bolt”, “source of supply is identified” and” Keep Closed- Run all leads through the bottom”.
label | Load Centres
checkpoint | Main isolator installed capable of isolating all downstream circuits, is labelled appropriately i.e. MAIN SWITCH and is capable of being locked or within a lockable space.
label | Load Centres
checkpoint | Visual indicator of periodic test, i.e. current test tag installed
label | Load Centres
checkpoint | Construction DB Register complete
label | Load Centres
section | Construction Wiring
checkpoint | Confirm wiring is not tied or bundled with permanent wiring system
checkpoint | Marker tape (yellow “construction wiring”) installed at intervals not exceeding 5 meters (unless cable is readily distinguishable colour from permanent installation)
checkpoint | Permanent wiring in vicinity to be marked “live wiring”
checkpoint | Mechanical protection installed as required including the use of plain screw adaptors (glands are not to be used)
checkpoint | Visually inspect each circuit and/ or sub mains entire route length to verify integrity of the installation as is practicable and safe
section | Lighting
checkpoint | Adequate access lighting provided, minimum 40 lux
checkpoint | Emergency Lighting over switchboard installed
checkpoint | Lamps protected from mechanical damage
checkpoint | Emergency lighting (when required) adequate for safe egress – minimum 20 lux average
checkpoint | Emergency Lighting Register complete, site plan marked up accordingly
checkpoint | Visually inspect each circuit entire route length to verify integrity of the installation as practicable and safe.
checkpoint | The Electricians noted above, working for Grid Electrical Services, certify that the inspections/ tests beside their name, has been verified/ tested to ensure it is electrically safe and in accordance with the relevant wiring rules and any other standard applying to the electrical installation un der the electrical safety act of that particular state/ territory at the date the test/ inspection was completed, in particular AS3000 & AS3012.
holdpoint | Signoff