## Table 1
Abbreviations
Third Party |  |  | TP |  |  | RSA Contractors |  | RSA |  |  | Nominated Project Personnel |  |  |  |  | NPP | Principle Contractor |  |  |  | PC
Surveyor |  |  | SUR |  |  | RPEQ |  | RPEQ |  |  | Supervisor |  |  |  |  | SUP | Inspect |  |  |  | INS
Test |  |  | TST |  |  | Project Engineer |  | PE |  |  | Witness Point |  |  |  |  | WP | Hold Point |  |  |  | HP
Visual |  |  | VIS |  |  | Check |  | CHK |  |  | Written |  |  |  |  | WRI | Monitor |  |  |  | M
Milestone |  |  | MST |  |  | Review |  | R
Inspection and Test Plan Details | [16 empty] | Contractor |  |  |  | Client
Item | Inspection Activity |  |  | Work By |  | Standard / Spec |  |  | Criteria |  |  |  |  | Frequency |  | Record | Resp |  | Type | Signoff | Resp | Type | Signoff
1 | Lot Identification |  |  | Contractor |  | Technical Specification |  |  | Location of Works identified in accordance with project technical specification |  |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot Map | RSA |  | CHK |  | Senex | CHK
2 | Underlying Lot Conforms |  |  | Contractor |  | Technical Specification |  |  | Foundation preparation works completed in underlying lot. |  |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot Map | RSA |  | CHK |  | Senex | CHK
3 | General Fill Material Requirement |  |  | Contractor |  | Technical Specification |  |  | Grading Requirements 75mm sieve –100% passing 37.5mm Sieve – 90 to 100% passing 19mm Sieve – 80 to 100% passing 4.75mm Sieve - 60 to 100% passing 2.36mm sieve - 40 to 95 % passing 0.075mm Sieve –15 to 90% passing Indicator requirements Plasticity Index – 10 to 40% Liquid Limit – 20 to 60% Emerson Class 2 (minimum) Organic content 2% (maximum) |  |  |  |  | Refer to Table 11 SPE |  | Laboratory test Certificate | RSA |  | HP |  | Senex | HP
4 | Fill placement |  |  | Contractor |  | Technical Specification |  |  | General Fill Placed in continuous, approximately horizontal layers for the full width of the area, having a compacted thickness of not more than 300 mm or less than 75 mm. If the surface of any layer is smooth, it must be scarified to a depth of approximately 30 to 50 mm prior to the placement of the next layer. |  |  |  |  | Each Lot |  | ITP Verification Checklist/Lot Map | RSA |  | WP |  | Senex | WP
5 | General Fill Testing |  |  | Contractor |  | Technical Specification |  |  | ≥ 96 % standard MDD. NOTE: ≥ 98% standard MDD for the Earthen Ring Beam General Fill Section. -2% to +2% of OMC |  |  |  |  | Table 10 Technical specification |  | Laboratory test Certificate | RSA |  | HP |  | Senex | HP
6 | ERB Inspection |  |  | Contractor |  | Technical Specification |  |  | Verification of RLs/Elevations filed controls for the ERB |  |  |  |  | Progressive During Fill Placement |  | Survey Data | RSA |  | CHK |  | Senex | CHK
7 | Survey |  |  | Contractor |  | Technical Specification |  |  | RSA shall submit 25%, 50%, 75%, 100% tank pad foundation fill placement completion survey to the superintendent within 48 hours of each milestone achievement |  |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot Map | RSA |  | HP |  | Senex | HP
Test Details | [9 empty] | Normal Testing Level | [7 empty] | Required Result(s)
Item | Test |  |  |  | Description |  |  |  |  | Max Lot Size/Area/ |  |  | Min Test Frequency |  | Min No of tests |  |  | Criteria
1 | AS 1289 .2.22, AS1289.5.1.1, AS 1289.5.4.1, AS1289.5.8.1 |  |  |  | General Fill Standard Dry density ratio, Moisture Content |  |  |  |  | 17,970 m3 |  |  | 1/ 500 m3 |  | 36 |  |  | -2% dry to +2% wet OMC SDDR 96%
2 | AS 1289 .2.22, AS1289.5.1.1, AS 1289.5.4.1, AS1289.5.8.1 |  |  |  | General Fill -Earth Ring Beam Standard Dry density ratio, Moisture Content |  |  |  |  | 320 m3 |  |  | 1/ 50 LM |  | 11 |  |  | -2% dry to +2% wet OMC SDDR 98%
3 | AS 1289.3.6.1, AS1289.3.3.1, AS1289.3.2.2 |  |  |  | PSD and Atterberg limits |  |  |  |  | 17,970 m3 |  |  | 1/1500m3 |  | 12 |  |  | Table 6 Technical Specification
4 | AS 1289.3.8.1 |  |  |  | Emerson Class |  |  |  |  | 17,970 m3 |  |  | 5 Evenly distributed test around the Tank |  | 5 |  |  | >=2
Contractor Construction Manager:
[7 empty] | (Print Name) |  |  |  |  | (Signature) | [6 empty] | (Date)
Client Superintendent:
[7 empty] | (Print Name) |  |  |  |  | (Signature) | [6 empty] | (Date)
Document Status
Revision Status |  | Responsible Person |  |  |  | Signed |  | Dated |  |  | Revision
Draft By: |  | Madhu Achana | [8 empty] | Rev1
Reviewed By:
Submitted By:
Approved By: