## Table 1
Abbreviations
Third Party |  |  | TP |  | RSA Contractors |  | RSA |  | Nominated Project Personnel |  |  |  |  | NPP | Principle Contractor | [5 empty] | PC
Surveyor |  |  | SUR |  | RPEQ |  | RPEQ |  | Supervisor |  |  |  |  | SUP | Inspect | [5 empty] | INS
Test |  |  | TST |  | Project Engineer |  | PE |  | Witness Point |  |  |  |  | WP | Hold Point | [5 empty] | HP
Visual |  |  | VIS |  | Check |  | CHK |  | Written |  |  |  |  | WRI | Monitor | [5 empty] | M
Milestone |  |  | MST |  | Review |  | R
Inspection and Test Plan Details | [14 empty] | Contractor |  |  |  |  | Client
Item | Inspection Activity |  | Work By |  | Standard / Spec |  |  | Criteria |  |  |  | Frequency |  | Record | Resp |  | Type |  | Signoff | Resp | Type | Signoff
1 | Lot Identification |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Location of works identified as per IFC drawings |  |  |  | 1/Lot |  | ITP Verification Checklist/Lot drawing | RSA |  | CHK |  |  | Senex | CHK
2 | Survey control and Setout |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Confirm centres of both sump and tank locations |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | HP |  |  | Senex | HP
3 | Excavation of sump |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Located at 3m outside from the hinge point of the tank pad. To be trenched to a depth of 3.17 m (to be confirmed on site) Sump excavated to correct dimensions in line with Concept Tanks 0.8m diameter excavation to design depth. Sump pit depth to be determined onsite ensuring sufficient fall from tank centre to sump |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | WP
4 | Installation of HDPE sump base and chamber at correct height and level |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Poly sump base to be installed at 200mm below leak detection pipe. Sump chamber installed plumb to correct height minimum 150mm above top of tank |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | WP
5 | Backfill - Sump |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Backfill in accordance with CT requirements. Compaction testing in line with Earthworks specification |  |  |  | 1/Lot |  | ITP Verification Checklist / Test | RSA |  | CHK |  |  | Senex | HP
6 | Leakage pipe trench excavation |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Trench excavated to correct lines and levels in line with CES drawings. 1:100 fall to sump Sufficient excavation width to facilitate installation. |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | WP
7 | Installation of 50mm HDPE leakage pipe |  | Contractor |  | Technical Specification/IFC Drawings |  |  | 50mm HDPE pipe and bends installed in accordance with CT and manufacturer requirements. Minimum 150mm cover at centre of tank Pipe installed on 50mm sand bedding (optional) as per CT recommendations HDPE pipe riser installed 300mm above FSL at centre of tank, temporary seal to prevent sediment ingress. Pipe to be left exposed at centre of sump pit |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | WP
8 | Surface Water Runoff |  | Contractor |  | Technical Specification/IFC Drawings |  |  | DN110 HDPE pipe for construction surface water runoff to be installed 1:100 fall to swale drain |  |  |  | 1/Lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | WP
9 | Backfill - Trench |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Backfill in accordance with CES requirements and general earthworks specifications 98% +/-2% moisture (Ring beam area) 96% +/-2% moisture (All other areas) |  |  |  | Min 2 tests per lot |  | ITP Verification Checklist / Test Report | RSA |  | CHK |  |  | Senex | WP
10 | Acceptance of work |  | Contractor |  | Technical Specification/IFC Drawings |  |  | Work completed in accordance with CES requirements. Compaction reports received and meeting specification As-constructed survey data obtained |  |  |  | Once per lot |  | ITP Verification Checklist | RSA |  | CHK |  |  | Senex | HP
Test Details | [7 empty] | Normal Testing Level | [7 empty] | Required Result(s)
Item | Test |  |  | Description |  |  |  | Max Lot Size |  | Min Test Frequency |  |  | Min No of tests |  |  | Criteria
1 | AS 1289 .2.22, AS1289.5.1.1, |  |  | General Fill |  |  |  | 1 |  | 2/LOT |  |  | 2 |  |  | -2% dry to +2% wet OMC SDDR 96%
| AS 1289.5.4.1, AS1289.5.8.1 |  |  | Standard Dry density ratio,
Moisture Content
Contractor Construction Manager:
[6 empty] | (Print Name) |  |  |  |  | (Signature) | [6 empty] | (Date)
Client Superintendent:
[6 empty] | (Print Name) |  |  |  |  | (Signature) | [6 empty] | (Date)
Document Status
Revision Status |  | Responsible Person |  |  | Signed |  | Dated |  | Revision
Draft By: Reviewed By: Submitted By: Approved By: |  | Madhu Achana | [6 empty] | Rev0