## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP025 - AGL Conduit and Boring Installation | itp |  |  |  |  | FH-ZU2-QU-ITP025 - AGL Conduit and Boring Installation - Rev 0
section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are:
label | ○ Using the correct and complete set of drawings.
label | ○ All drawings are the latest revision.
label | Reference Documents - Drawings / Aconex Register
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings and drawing registers
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.3 - Definition of the work area (survey)
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Work area has been cleared and surveyed (marked on site). Limits of excavation clearly defined.
label | Reference Documents - Drawings
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 1.4 - Check conduit compliance
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that uPVC conduits comply with AS 1477 or equivalent AS 2053. Shall be heavy duty, orange for electrical services and white for communication services.
label | ○ Ensure that pipe diameter is correct as per the drawings.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.4 AS 1477 AS 2053
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference This ITP signed
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.5 - Check bedding material compliance
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Ensure that conduit bedding material is non- plastic granitic sand complying with Table 3-1 and 3-2 under cl. 3.8.3.3 of the Works Specification.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.3
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference
label | TP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.6 - Locate and prove existing services
label | Frequency - Prior to commencing activity
label | Acceptance Criteria - Location of services to be found and marked on the ground within the works;
label | ○ Contractor to obtain excavation permit from APAM prior to any demolition works.
label | ○ Services located within the works area to be exposed/proven, recorded as survey data and also on a service plan which is to be attached to the Excavation Permit.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.15
label | Inspection/Test Method - Verify
label | Record of conformity - Melbourne Airport Excavation Permit
label | HP*
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
section | 2.0 - Construction
checkpoint | 2.1 - Excavate trenches for conduits
label | Frequency - Each lot
label | Acceptance Criteria - Trenches for conduits shall be excavated to the width and depth required enabling construction of the conduits to the requirements specified on the drawings.
label | ○ The level at the bottom of the trench shall not be above the required level at any point.
label | ○ Any over excavation under pavements shall be restored using 5MPa lean mix concrete in conjunction with the embedment.
label | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.6
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 2.2 - Existing services crossing new conduits
label | Frequency - Each lot
label | Acceptance Criteria - Only approved methods of excavation that has been approved by the Principal’s Representative shall be used.
label | ○ Location, level and configuration of existing service crossing to be recorded in as built documentation prior to backfill (including CAD model file)
label | Reference Documents - WMS002 – Working Near Existing Services
label | Inspection/Test Method - Visual inspection
label | Record of conformity - As-built survey report
label | SCP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 2.3 - Laying and jointing of conduits
label | Frequency - Each lot
label | Acceptance Criteria - All conduits shall be rigidly supported and positioned by concrete or plastic spacer blocks so that no displacement occurs during backfill.
label | ○ Where conduit ends are not open to a pit, UPVC end caps shall be temporarily fitted to each end.
label | ○ Number of conduits and duct route to be confirmed for conformity with design.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.7
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 2.4 - Survey as-built
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - Surveyor to pick up completed conduit runs before backfill
label | Reference Documents - FH QMP
label | Inspection/Test Method - Verify / Inspection
label | Record of conformity - Survey report
label | SCP / IP
label | Responsibility - Project Engineer / Surveyor
date | Date Completed:
checkpoint | 2.5 - Pre-pour inspection
label | Frequency - Prior to backfilling each lot
label | Acceptance Criteria - WITNESS POINT
label | ○ The Contractor must provide the Principal’s Representative notice of the Contractor’s intention to backfill trenches within a Lot. This must include details of the date, time and location of the proposed work.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.1
label | Inspection/Test Method - Inspection
label | Record of conformity - This ITP signed
label | WP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
checkpoint | 2.6 - Backfilling conduits under pavement
label | Frequency - Each lot
label | Acceptance Criteria - Concrete encasement of conduits: Conduits to be encased in 5MPa lean mix concrete as per drawings.
label | ○ Trenches in existing pavement: Surface shall be reinstated to match surrounding pavement. Unless noted otherwise, reinstate asphalt pavement surfaces to a minimum of 70mm (or to match existing depth (whichever is greater)).
label | ○ Trenches in new pavement: Pavement shall be constructed as per the drawings and specification.
label | Reference Documents - Drawings ZULU-BECA- 001-SPC-00004 cl. 3.8.2.1, cl. 3.8.2.2
label | Inspection/Test Method - Verify
label | Record of conformity - Delivery docket This ITP signed
label | IP
label | Responsibility - Project Engineer/Foreman
date | Date Completed:
checkpoint | 2.7 - Backfilling conduits in grassed areas
label | Frequency - Each Lot
label | Acceptance Criteria - HOLD POINT
label | Conduits to be encased in compacted sand bedding. The material shall be non-plastic and comply with properties specified in Table 3-1 & 3-2 of the specification. Details of the proposed sand shall be submitted to the Principal’s Representative.
label | ○ Backfill layers:
label | – Not exceeding 300mm compacted thickness.
label | – Not less than 90% maximum dry density (test no. 5.1.1).
label | – Not less than 70% of density index (test E6.1).
label | ○ Compaction testing carried out at a rate of not less than:
label | – Bedding: 1 test per 400m of conduit laid (min. 3x).
label | – Backfill: 1 test per 400m of conduit laid per 0.5m of backfill depth (min. 3x).
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.8.3.1 cl. 3.8.3.2 cl. 3.8.3.3, AS 1289 Test no. 5.1.1 Test no. E6.1
label | Inspection/Test Method - Verify
label | Record of conformity - Test report Aconex reference This ITP signed
label | HP / TP / IP
label | Responsibility - Project Engineer / Principal’s Representative / Foreman
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.8 - Conduit markers & warning tape
label | Frequency - Each lot
label | Acceptance Criteria - Pavement edge duct markers shall be installed at the edge of pavements immediately over the centreline of duct banks.
label | ○ Warning tape shall be to AS 2648.1, and coloured orange for electrical/white for communications conduits.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.11 cl. 3.12 AS 2648.1
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | 2.9 - Checking of conduit lines
label | Frequency - Each lot
label | Acceptance Criteria - HOLD POINT
label | ○ Following installation, the conduit shall be checked by passing a mandrel (not less than 300mm long and having a diameter of not more than 6mm less than the diameter of the conduit) through each way, followed by a brush with stiff bristles to clean the conduit of any foreign materials.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.9
label | Inspection/Test Method - Visual inspection
label | Record of conformity - This ITP signed, Avionics Primary Trenching Checklist
label | HP
label | Responsibility - Project Engineer / Principal’s Representative
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.10 - Conduit draw cord
label | Frequency - Each lot
label | Acceptance Criteria - Each duct way in each duct bank shall be fitted with a single unjointed length of draw cord of a length equal to the length of the duct plus 4m. The draw cord shall be nylon rope and be 6mm in diameter, blue in colour. The ends of the rope shall be coiled at the bottom of each pit or wound around a stake.
label | Reference Documents - ZULU-BECA- 001-SPC-00004 cl. 3.10
label | Inspection/Test Method - Visual
label | Record of conformity - This ITP signed, Avionics Primary/Secondary Trenching Checklist
label | IP
label | Responsibility - Project Engineer / Foreman
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
date | Work Completed On:
date | Date: