## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP028 - AGL Luminaires | itp |  |  |  |  | FH-ZU2-QU-ITP028 - AGL Luminaires - Rev 0
section | 1.0 - Preliminary Works
checkpoint | 1.1 - Check for correct documentation
label | Frequency - Prior to commencing any activity
label | Acceptance Criteria - Ensure that all employees and subcontractors are using the latest and complete set of drawings
label | Reference Documents - IFC Drawings
label | Inspection/Test Method - Verify
label | Record of conformity - Drawings
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
label | Frequency - Prior to commencing any activities
label | Acceptance Criteria - All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
label | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
label | Inspection/Test Method - Verify
label | Record of conformity - Site and office Inspection
label | HP*
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
checkpoint | 1.3 - Material/Equipment Approvals
label | Frequency - Prior to start
label | Acceptance Criteria - All materials shall be proven to meet contractual requirements prior to acceptance.
label | – MAGS shall be from ATG Airfield guidance signs range
label | – Taxiway centre lights shall be from the ADB Safegate range only
label | – Runway guard lights shall be from ADB Safegate only.
label | – Intermediate hold position lights shall be from the ADB Safegate range only
label | – Stop Bar Lights shall be from the ADB Safegate
label | – IWDI shall be from ALS
label | ○ Any deviation from the above suppliers shall be submitted to the Contract Administrator for approval prior to ordering.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 2.3
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference(s)
label | HP*
label | Responsibility - Project Engineer
date | Date Completed:
section | 2.0 - Installation of AGL Base
checkpoint | 2.1 - MAG Sign Base
label | Frequency - Each lot
label | Acceptance Criteria - Position of rectangular base to be as per set out coordinated listed in MAGS schedules.
label | ○ 150mm thick class 2 crushed rock base layer compacted to 98% STD on prepared subgrade
label | ○ 50mm blinding concrete between subgrade and foundation
label | ○ Slab thickness to be 300mm for all
label | ○ H<900mm signs (signage outside this range will require additional design)
label | ○ N12-200 top and bottom reinforcing bars with minimum 50mm cover from edge of concrete.
label | ○ Sign mounting brackets and frangible coupling as per manufacturers guidelines
label | Reference Documents - ZULU-BECA-023- DWG-07502
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.2 - Inset Luminaire Base
label | Frequency - Each lot
label | Acceptance Criteria - Installed and backfilled in accordance with drawings.
label | ○ Reinstatement in Flexible Pavement
label | – 500mm deep circular concrete block (500mm diameter for 8” cans, 600mm diameter for 12” cans).
label | – Core depth and pavement embedment for can as per can/fitting manufacturers recommendation.
label | – Epoxy sealant as per can/fitting manufacturer’s specifications
label | – DOWSIL 890SL to gap between AGL can and pavement.
label | ○ Deep Can Installation for Rigid Pavement
label | – Concrete encasement for electrical conduit shall have 75mm minimum cover
label | – 700mm diameter concrete foundation
label | – Minimum 200mm from bottom of can to bottom of foundation
label | – Concrete for deep base can foundation to be strength grade N32
label | – N12 reinforcement cage to be installed as per AGL details
label | – Epoxy to manufacturers specifications
label | Reference Documents - ZULU- BECA-024- DWG- 07501, ZULU- BECA-024- DWG- 07506-8
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Shallow Canister Installation checklist / Avionics Base Canister Installation checklist / Avionics Top Canister Installation checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 2.3 - Elevated Luminaire Base
label | Frequency - Each lot
label | Acceptance Criteria - Installed and backfilled in accordance with drawings.
label | ○ One-piece L867 can to be installed
label | ○ Min 500mm cover from finished surface to top of conduit
label | ○ Can to be fitted with frangible coupling and FAA type/secondary socket retaining arrangement plug and socket
label | ○ Foundation and reinforcement installation to match Deep Can Installation for Rigid Pavement
label | Reference Documents - ZULU- BECA-024- DWG- 07507
label | Inspection/Test Method - Visual Inspection
label | Record of conformity - This ITP signed, Avionics Base Canister Installation checklist
label | IP
label | Responsibility - Project Engineer / Site Supervisor
date | Date Completed:
section | 3.0 - Installation of AGL Luminaires
checkpoint | 3.1 - Setting out for Airfield Luminaires
label | Frequency - Each Lot
label | Acceptance Criteria - The Contractor shall survey the proposed light locations in conjunction with the new and existing linemarking to set out the proposed lights. A schedule of the proposed lights shall be produced by the
label | ○ Contractor with the following details:
label | – Surveyed location, with coordinates to the APAM database system.
label | – Orientation including any additional deviation angle from any tangents.
label | – Colour
label | – Circuitry
label | – Labelling
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 5.4
label | Inspection/Test Method - Verify
label | Record of conformity - Aconex reference
label | HP
label | Responsibility - Project Engineer / Beca
date | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Elevated Light Installation
label | Frequency - Each lot
label | Acceptance Criteria - Components of elevated lights shall:
label | ○ Be less than 360mm above the pavement level including the frangible coupling.
label | ○ Be suitable for installation on a threaded connection when installed.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.4.4.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.3 - Inset Light Installation
label | Frequency - Each lot
label | Acceptance Criteria - Components of inset lights shall:
label | ○ Be less than 13mm height above the surrounding surface.
label | ○ Have a slope of surface of the unit to be less than 20º (not including any recesses).
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.4.4.3
label | Inspection/Test Method - Verify
label | Record of conformity - This signed ITP, ADBSG Installation of Inset Light Fittings checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.4 - Series Isolation transformer
label | Frequency - Each lot
label | Acceptance Criteria - SITs shall be installed in specified deep base cans or pits.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.3
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, ADBSG Installation of Series Isolating Transformer (SIT)
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.5 - Luminaire Circuit
label | Frequency - Each lot
label | Acceptance Criteria - Each luminaire fitting shall be installed on the appropriate circuit as specified in the AGL schedule.
label | Reference Documents - ZULU- BECA-024- DWG- 09001-16
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, As-Built Documentation
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | 3.7 - MAG Sign Face
label | Frequency - Each lot
label | Acceptance Criteria - The proposed location for MAGS are to be as indicated on the Drawings.
label | ○ All MAGS that are to be mounted on frangible couplings. The provision of internal illumination of the MAGS shall be as detailed on the Drawings.
label | ○ Where multiple panels are required, the inscription shall appear continuous over any joint and shall only include a bar if the bar is part of the inscription.
label | Reference Documents - ZULU- BECA-001- SPC-00003 cl 4.7.1
label | Inspection/Test Method - Verify
label | Record of conformity - This ITP signed, Avionics Installation of New MAG Slab and Sign checklist
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
section | 4.0 - Post Construction
checkpoint | 4.1 - As-Built
label | Frequency - Each lot
label | Acceptance Criteria - Submission of surveyed luminaire position to superintendent prior to practical completion
label | Reference Documents - WP-001-09
label | Inspection/Test Method - Verify
label | Record of conformity - SCP
label | IP
label | Responsibility - Project Engineer
date | Date Completed:
checkpoint | Final Inspection
label | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
text | Print Name:
text | Position:
date | Work Completed On:
date | Date: