## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-flat |  |  | checklist | Drains: Greasy Waste - Underslung, Stacks & Vents |  |  |  |  | Yes | (LATEST) Drains: Greasy Waste - Underslung, Stacks & Vents | 002cd025-2125-4b42-be87-ee6fe238e405
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for underslung/suspended drains for greasy waste
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status |  |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status |  |  | checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Expansion correctly clipped
checkpoint-status |  |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status |  |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status |  |  | checkpoint | Peno has been caulked (top and underside of slab)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint-status |  |  | checkpoint | Greasy waste/pumpline has been water tested (include photos)
checklist-flat |  |  | checklist | Comm/HO - Apartment Final Commissioning - Fixture Group |  |  |  |  | Yes | (LATEST) Comm/HO - Apartment Final Commissioning - Fixture Group | 01646f6f-0460-47da-ba53-a238df9b3bdf
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for final commissioning of all installed fixtures
checkpoint-no-status |  |  | checkpoint | Bathroom/WC Area
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery does not exceed 50degC on any fixtures
checkpoint-status |  |  | checkpoint | For SDA or DDA areas only, hot water delivery does not exceed 45degC on any fixtures
checkpoint-status |  |  | checkpoint | WC toilet seat and lid secured and fastened with soft close function operating
checkpoint-status |  |  | checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Wet area grated outlets are installed correctly
checkpoint-status |  |  | checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status |  |  | checkpoint | Laundry Area
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Mini stops/trivalve have been securely capped for future washing machine connection by others
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery does not exceed 65degC
checkpoint-status |  |  | checkpoint | Trough tap has been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | Trough tap has been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Wet area grated outlets are installed correctly
checkpoint-status |  |  | checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status |  |  | checkpoint | Kitchen
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Pullout mixer function has been checked and has clear
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint-status |  |  | checkpoint | All fixtures have been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Dishwasher has been run through a short cycle
checkpoint-no-status |  |  | checkpoint | Kitchen - Gas
checkpoint-status |  |  | checkpoint | Gas appliance connections have been checked for any damage or leaks
checkpoint-status |  |  | checkpoint | Gas valves & regulator flow direction have been checked
checkpoint-status |  |  | checkpoint | All gas burners function correctly and consistently
checkpoint-status |  |  | checkpoint | Check balcony hose tap & NRV are installed correctly
checkpoint-status |  |  | checkpoint | Check balcony floor grate & downpipe are installed correctly
checklist-flat | 8fc28b2c-6c1d-421b-ab41-3f08c172330c |  | checklist | HW Hot Water Meters |  |  |  |  | Yes | HW Hot Water Meters | 02769bc8-0090-441f-a113-1a427ce9862d
checkpoint-status | 802155b8-2bfd-4e2f-a54f-b7f2cc6fddee |  | checkpoint | Water Meter Details:
text | 7a8f0fa3-09ff-5386-aea8-5c554e27b47a |  | textbox | Meter No:
text | da1827b2-c38d-5a27-a9d3-b2bb4a6ce9c5 |  | textbox | Level:
text | 084adfeb-a922-5893-96f0-36a4e95634eb |  | textbox | Meter Size:
checkpoint-status | 865686b3-7f20-4819-b1f8-618084362348 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 233baefe-8f17-45e4-b43c-5a5383cbfe79 |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | b49f6498-3324-496c-8d70-dec8df4d4a69 |  | checkpoint | Meter bracketed
checkpoint-status | b374331c-ceee-4c56-82dc-4c9c250b5df0 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | ab99a934-d9c6-4984-9efe-0ceb8f0f9754 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | b7e5fe72-a082-437d-a24a-d14605e79293 |  | checkpoint | Pulse rate value is correct
checkpoint-status | eab3f7ae-5e5b-48d3-813f-9de02805b0bf |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | d724a9a7-4279-4880-91c9-245d5f4bff46 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | d01b471e-96b2-42f9-a72f-a048c7453090 |  | checkpoint | Flow direction is correct
checkpoint-status | 444a473e-e2e1-4600-a2f2-40657adee01d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 36b8d63c-3ef9-467a-8f18-3ac985c4d44e |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 5416713a-3295-40ea-ba3e-151726e35bb5 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Plant & Equipment Install - Stormwater Treatment System/Filter |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Stormwater Treatment System/Filter | 071f003a-bf41-4769-8a5a-da85753e424c
checkpoint-status |  |  | checkpoint | Stormwater treatment system/filter has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all supply lines has been undertaken
checkpoint-status |  |  | checkpoint | Filter lid has been lifted and all formwork has been stripped
checkpoint-status |  |  | checkpoint | Rails and lifting chains are in place
text | a0dc9e57-16b5-5b75-94b0-f1449a5212f0 |  | textbox | Stormwater treatment system/filter is generally a SPEL/ Gross Pollutant Trap/First Flush/Rain Garden
checkpoint-status |  |  | checkpoint | Stormwater treatment/filter is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | Pumpwell lid has been resecured and lid fixings resecured
checklist-flat | 27ad5f32-a25f-4e86-be79-14d9a7ae076c |  | checklist | RW Rough-in (High Level) |  |  |  |  | Yes | RW Rough-in (High Level) | 09f16d52-3839-47c6-8057-7ecfee02b604
checkpoint-status | 12ba887c-ea5f-45e1-9ea4-1dbdf9cb192b |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 6e202e1b-2ed8-4777-b21c-5ce293311c2e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | b758d218-d16a-4ab4-83d5-d7b2512577bf |  | checkpoint | Pipe materials are correct for application
checkpoint-status | abebe7fc-d0f8-4ae3-8875-0ef10fb2db34 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | fe2e0211-52c6-4512-937f-f0771519e166 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 801c705b-cf4e-40aa-9585-41a418787815 |  | checkpoint | Check for possible cross connections
checkpoint-status | ad2837f4-62c2-4fb6-8007-9b5e12ec6dbd |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 0dc25855-7d1f-4841-a0cf-722314d2f096 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 88fa9e07-d745-4d56-a645-dbcfe3bcf33b |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e8371e92-d6a3-471b-9994-8685c63eb53c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | b5b7a32c-8b08-495c-be0b-df5b8d0ca721 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 30dc31fa-9827-4860-8979-076aa2ba6102 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 0df79968-e9eb-4ced-bf29-456c837f9860 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Rough In - CW Design Components |  |  |  |  | Yes | (LATEST) Rough In - CW Design Components | 0ba74e8b-9d0d-4c09-b704-5914175027af
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for specific design requirements for CW
checkpoint-status |  |  | checkpoint | CW tank bypass has been roughed in
checkpoint-status |  |  | checkpoint | CW backup to RW system has been roughed in
checkpoint-status |  |  | checkpoint | Check meter installed
checkpoint-status |  |  | checkpoint | RPZD/ back flow prevention device installed
checkpoint-status |  |  | checkpoint | Isolation valves installed
checkpoint-status |  |  | checkpoint | Pressure reducing valves installed
checkpoint-status |  |  | checkpoint | Future provision for connection to BMS
checkpoint-status |  |  | checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist-flat | 2c955d87-c17d-4214-93b2-71ecca366047 |  | checklist | RW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | RW Risers (Pumped or Mains Pressure Risers) | 0d50bbf2-fe47-485b-8440-ecc796691b71
checkpoint-status | 83480c04-bfcd-481c-8262-0fd484a537c5 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 84f8d95f-3095-4847-bb12-259dbedd1cd8 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 85d5da0f-2d08-4568-a428-e9ff0d623e26 |  | checkpoint | Penetrations are installed
checkpoint-status | 7c7c6d42-99d5-46d7-892c-67f3ae1d8c1c |  | checkpoint | Pipe materials are correct for application
checkpoint-status | afd38a27-0eba-43eb-8920-7cd28c001133 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7c354e53-633b-43ae-847d-d9bb16c47423 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 1dda99b1-4649-420f-81db-8e849f126760 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | b712ca53-996a-44fe-a62f-1e9bc08fbe5f |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | d4c4e7f5-ad4b-4678-9a74-4a73cbc7f701 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 88a3bf3a-8c4e-4437-9ac4-e609df66e0a5 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 34f18272-db06-4a70-a20a-b6d858e7ea89 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 464bc64e-42f8-43b8-8593-da910f1725fa |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 6cd8e533-35d5-4e98-b41b-ce8e9f387dea |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 6615a1d7-deb8-41ef-85f3-e24625997920 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 49b51fa2-fed5-4cf7-9d31-f280b7575b01 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 961ccab6-2b7f-48b2-a544-3437991c0d79 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | caabce3d-bb48-43f3-bb70-b0eb6e8d9c17 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 5d858f45-e4ee-4767-a2b6-839789adfd55 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d91e437c-017b-4837-a0d9-437a1c546ae0 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 40fc0389-d486-4290-88f4-3ec61c375874 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 56c18991-2bc6-4eb0-bb63-dfeff55a54d7 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 8d882aa4-56ab-4fba-ad4b-b615a6360341 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | fae1b1ef-b42a-431e-9b07-ebaa9781b6a4 |  | checklist | HW High Level/Corridors |  |  |  |  | Yes | HW High Level/Corridors | 0d9ada3b-543e-4463-bea8-a5ff876c577d
checkpoint-status | 35ab1971-da0e-43d0-a541-9ccdf8017500 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 898312af-4045-4f02-aa4e-1310b2680d5d |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | e9516ffc-ef1c-48c8-bd09-719dffef3992 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 2e0b053b-571c-4a91-94ed-45398344ee84 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 5afee796-a94a-4ac7-a58b-30d625094c7b |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 7c45c6e9-2c74-4faa-9737-80e667fd3de7 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 6f28991a-1e5e-4857-8a35-8055aece7599 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | af16468e-310f-4796-9201-583e0d35528b |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | e33a78be-938d-4f3a-8501-38140621d09c |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 6834cc92-c14e-4ac8-b25c-00b6a1d6213f |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | 474a608d-878a-4a8c-8db3-236ecea8e5a6 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 052db33a-1f32-477f-8459-358600901ed6 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 01c5f481-e0ea-4e3c-b4be-cbb9338c9b11 |  | checkpoint | Balancing valves are installed & flow correct
checkpoint-status | 5af5ae73-ed0e-488d-a16c-8500390369d6 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e95f5a71-be5d-49bc-88a8-661d275f5cc5 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7461b8f8-e850-4162-8e54-beeb121c436d |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | dae9297f-25fc-4610-98a8-3b24c9d2a19e |  | checkpoint | Heat trace installed if required
checkpoint-status | 360af0a5-f1d9-4030-affa-0cc293a1fe65 |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 3f8d7357-5c89-4eea-ac29-da3cf2751a45 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9f6f35b9-36a5-4619-a29c-438cde20398f |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 96110f71-4c63-4e1e-9e96-1549a3bb285d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bc7a3210-ff76-4a24-a7cb-4860c3aefc3f |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | FINAL Commissioning - Hot Water Plant |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Hot Water Plant | 10b5933e-e791-414c-b5c0-3ef10ea60716
checkpoint-status |  |  | checkpoint | Hot water plant commissioning report to be uploaded here
checkpoint-status |  |  | checkpoint | Hot water plant final install photos to be uploaded here (show temperature on plant setting)
checklist-flat | 69e6bca9-15ed-42f8-8d9d-d6111c697916 |  | checklist | 10.6 NG Purging of Consumer Fitting Line |  |  |  |  | Yes | 10.6 NG Purging of Consumer Fitting Line | 1614960e-9aad-4867-ac7c-0cc1d443029d
checkpoint-status | 66278665-796c-415d-8c12-2e5303fc5afc |  | checkpoint | Complies with requirements of either AS3500 and AS5600.1
checkpoint-status | 88029b1d-440e-45d4-8150-6a968185503f |  | checkpoint | Complies with the latest IFC specifications & drawings
checkpoint-status | cdaf51e8-01ba-4d92-9968-5347b10525f5 |  | checkpoint | A "Tool Box" meeting to be held on the morning of the meter installation date to define personnel rolls & responsibilities
checkpoint-status | 08fd0aef-9c95-4d9b-914f-585494546b6a |  | checkpoint | Select the purge areas and ensure no ignition sources are within these areas
checkpoint-status | 3a9154ca-4b13-47f2-89b6-144dec01ed77 |  | checkpoint | Prominently display warning signs surrounding the purge areas
checkpoint-status | ebc03ad5-12ee-4548-9775-89e376a2b482 |  | checkpoint | A purge stack or purge bucket must be available and operated by one designated team member
checkpoint-status | 2908574d-94de-448e-bdc7-c196efc963d0 |  | checkpoint | Provide suitable fire-extinguishers within the purge venting areas
checkpoint-status | c0397de5-ea6e-4543-9c50-9d82099f3359 |  | checkpoint | Nitrogen and connection equipment is available for the purge
checkpoint-status | 48997309-917c-4606-a6b5-1604c4aee5e0 |  | checkpoint | Ensure personnel are familiar with operation of the fire-extinguishers
checkpoint-status | b6c87043-e0a6-4c38-922e-eb3cc3951c1b |  | checkpoint | All electronic equipment to be used in the purge area must be rated as "electromagnetically safe"
checkpoint-status | 2da4e964-42ad-44c7-8200-d3b6d6535bfa |  | checkpoint | The team leader is to remain in the gas meter room to control & oversee proceedings
checkpoint-status | 7d18d79b-bd59-4923-96fc-b47e21472be5 |  | checkpoint | Reliable two-way radio devices are to be issued to all personnel as the means of primary communication
checkpoint-status | dde21088-993d-49eb-bb96-d59c48e56b92 |  | checkpoint | Hydraulic Services contractor to purge all air from the consumer line using nitrogen until air is displaced with a nitrogen plug
checkpoint-status | 0a87032a-10ba-4dc3-8fdf-d33a4263d107 |  | checkpoint | ESVs' meter contractor is instructed that all is in readiness for the commencement of his works
checkpoint-status | 0a32d802-8a49-46a1-8c61-d9b4dd6845d9 |  | checkpoint | ESVs' meter contractor fits the meter in position and immediately commences the purging & calibration of his meter
checkpoint-status | 8631ff9d-585e-4d9a-9744-1dfc6eb020b2 |  | checkpoint | At this stage only a minor amount of nitrogen gas will be displaced for venting in the purge areas
checkpoint-status | c5278c56-34c5-4794-8dd5-4afdc2d39b57 |  | checkpoint | Following the successful installation & calibration of the meter, the ESV contractors' engagement is complete
checkpoint-status | 0b1bc146-01e4-46c3-88f4-2d71614aaee0 |  | checkpoint | The Hydraulic Services team now takes over and commences the consumer fitting line primary purge
checkpoint-status | c4d923e3-a4c2-4d31-ad61-4bea1ffc6fda |  | checkpoint | Calculate the volume of the main run of pipe before commencing the purge (Re: ESV GIS No: 14 - Table 1 and the example in Appendix 2). Observing the volume passing through the meter will indicate when gas is expected to flow through the purge stack or the purge bucket.
checkpoint-status | 78ad7dc7-7b07-4ced-bd62-ff6dd8411acb |  | checkpoint | Note the gas meter test dial position for indication of the flow rate
checkpoint-status | da86de99-8c39-4558-b21e-d73e3324e842 |  | checkpoint | A purge stack or purge bucket has previously been connected to the further most point of the consumer fitting line
checkpoint-status | a2093032-9c4d-4680-859d-e5832da0e3e2 |  | checkpoint | Carefully open the primary gas control valve & commence the purging process
checkpoint-status | 36664ca5-1cab-4faf-b33b-9c32088fc11e |  | checkpoint | Ensure the maximum purge pressure is not exceeded (Pressure is labelled on fitting line)
checkpoint-status | 39e12e45-b44b-40ea-808f-67f8908d91b8 |  | checkpoint | Continue to purge through the purge stack or purge bucket until natural gas is commences being presented
checkpoint-status | 63771ff4-1bdf-46fa-93d2-89eab44336ae |  | checkpoint | Take a sample from the purge stack or purge bucket sampling point using a suitable gas detector (minimum acceptable reading 95% gas).
checkpoint-status | c13f46f9-78b7-43ea-85b7-200e4f6fcf14 |  | checkpoint | An indication that the purging of natural gas is nearing completion is seen when mass gas aeration evacuates from the purge bucket and proceeds to disperses.
checkpoint-status | 8f220191-fa88-4756-8a9a-808ec4e95e9c |  | checkpoint | Continue purging & testing until an acceptable reading on the gas detector is obtained
checkpoint-status | a9f7ae77-0e37-4ce0-95c3-5bf3efd0052a |  | checkpoint | When the correct test result is obtained, purging of this section will be complete.
checkpoint-status | 5889495a-8583-4f46-bf05-8e91dbf38ebb |  | checkpoint | Relieve the pressure in the purge hose by opening the purge stack main valve.
checkpoint-status | f7cba317-6de5-4625-ad0b-89fcf3b04cca |  | checkpoint | Disconnect the purge hose and the hose inlet valve from the installation. Cap & seal the fitting line immediately to avoid gas escaping and air re-entering the line.
checkpoint-status | ff5ea3a6-40af-47a0-95a7-0f9c0162f20c |  | checkpoint | Transfer the purge stack or purge bucket and hose to the end of the branch nearest the meter and repeat the procedure.
checkpoint-status | 6c223fc1-a108-4af5-a545-14939a78b766 |  | checkpoint | Continue purging all branches, moving away from the meter, until the whole installation is filled with gas.
checklist-flat | c3a7dd80-2927-4b59-97ca-b03a30e3b4f4 |  | checklist | FO Clothes Washing Machine Stops |  |  |  |  | Yes | FO Clothes Washing Machine Stops | 1753a8a2-a079-4c29-81a0-0bef92891b2e
checkpoint-status | a67d194b-7cee-4ccf-b55a-1b6aae535de0 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d07b1e29-307c-4c98-acf8-c5aebd2b2fd8 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | d986add7-f0fd-4406-9141-062b8f0bbce2 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | e0df35a7-9a68-4587-b0fc-ef2b90a0efa2 |  | checkpoint | Check flood stoppers
checkpoint-status | 42386290-2820-49b8-92d1-da8657c938e0 |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | bdad37b4-fe57-47fb-b9f0-08fa6d005c4d |  | checkpoint | Check cover plates are installed
checkpoint-status | 98d2016c-4c87-4079-9aa0-91dfb77efdc0 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | c471711d-5860-4740-8a65-e436a4b2821b |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat | 756f5eed-9b56-49ae-ac0a-7a5f28d35eea |  | checklist | CW Reduced Pressure Zone Device(RPZD) Rough-in |  |  |  |  | Yes | CW Reduced Pressure Zone Device(RPZD) Rough-in | 1a36c7e5-426e-4d6a-93ab-0ab84aeac9c0
checkpoint-status | 6d905ef1-ca5d-4fd9-8ac8-9c473b9f7de9 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 9394911b-7031-4d4b-9d57-caee71612d78 |  | checkpoint | General finish & alignment both level & center of valve assembly
checkpoint-status | bd91f412-1afa-4c50-93fe-759b7c0a04e3 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 1e973406-b6c1-45f0-8ae5-81c59ccdaf3e |  | checkpoint | Check silicone applied to studs
checkpoint-status | ae31f4c0-a4d6-41a4-9037-64069de414ad |  | checkpoint | Wall box is installed if required
checkpoint-status | 5acddc14-9446-419d-b235-08ec4b5bac89 |  | checkpoint | Check RPZD correct location
checkpoint-status | 5f2bd211-e33d-4e99-9372-b2fc93279c98 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 7bf47135-3a55-46ad-95c8-90df0f1bd3b3 |  | checkpoint | Flow direction is correct
checkpoint-status | 0ef73ab8-36b9-48c0-bc2c-9306be70b6c6 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | d34d4410-adf4-476c-b66c-bfddc615dbf2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bb0e2004-0610-451d-95c5-11b452505121 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | ae050eda-6d39-4b74-a32c-eec68a2c5ed5 |  | checklist | FO Cleaners Sinks |  |  |  |  | Yes | FO Cleaners Sinks | 1a7a356b-963b-4ced-82dd-6b58294285c5
checkpoint-status | 18d56098-ffbc-4aaf-8d64-041bea23e5c7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 3e35c924-bcff-447a-833c-8b4894bd4cf2 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 2a0d0f15-d2cd-478e-9d7d-2f0585cec41f |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | a6e2cc42-0755-4734-9bed-b02ec3460956 |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status | a8539c52-f518-4e17-8790-25614d841abc |  | checkpoint | Wall brackets are well fitted & secure
checkpoint-status | 2339c138-6ef1-4a92-b299-cf70051bf0c6 |  | checkpoint | Bucket grate is well fitted & secure
checkpoint-status | 3d6ee26b-900c-43b6-b877-bc79807c4276 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 35936f24-88b4-46a0-94d2-e2246d2995e7 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | e730e844-7b64-4c57-8ae4-50ae5a1c20cb |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | f251752a-e1c0-4e03-bf44-e4fa776916fb |  | checkpoint | Check cover plates are installed
checkpoint-status | 723affb0-d3b0-4e49-9477-4868a6cd3767 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 485c592a-69c6-4bd7-b395-c6b4ae44e24a |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | c504deee-4f1c-4dbd-ab18-2b7d7db9996f |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status | 0342bfa4-1b09-4426-ac32-c7e3ed19af48 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 50cc1f86-8ebd-452c-894c-f1e39f32bc5c |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 9ba23a94-2501-4494-a627-d153a04b1731 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | a14e491d-3a56-4ee2-a67c-4e6122d3b667 |  | checkpoint | Check caulking is correct
checklist-flat | e90358ad-fa55-4908-99da-474dcd4c31a2 |  | checklist | RW Rough-in (Low Level) |  |  |  |  | Yes | RW Rough-in (Low Level) | 1b44c508-4a1e-43dd-92c7-c18649fce351
checkpoint-status | ec58e273-0f1b-4873-be78-bca889d504d3 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 13e53228-edc4-4538-a5bf-c2cc4f761ad0 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | d5bff27a-48c6-48b8-8b63-7129991804f2 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 70cc5d5e-ee3a-4b96-8610-559da6155e98 |  | checkpoint | Check silicone applied to studs
checkpoint-status | df4bd6fe-ccd8-4fab-951e-73b8e48a242a |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 101b8a32-5de1-460a-8814-ce987e04a091 |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status | f1fd2ac7-5410-49e4-8772-0819442055cb |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status | 980e60c6-e7b4-4f20-83db-fa80568510f0 |  | checkpoint | Check for possible cross connections
checkpoint-status | 6fee58df-cac7-42fe-825c-c11a71f59b94 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | f27e117a-a252-4484-aa70-59952f55e7b3 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 573abe61-ad8d-41c3-a180-6a8fd9e8a29a |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 83e9c7b2-f0e2-4996-87f8-31bb40860471 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c05a85f9-a635-48d5-9703-c35835f2045a |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | f29d7d99-f2cb-4f2b-a0cd-1692a42e2e0b |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | eb515d00-3b84-4940-937e-6c99e16647e1 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Testing - Air Test - Sewer |  |  |  |  | Yes | (LATEST) Testing - Air Test - Sewer | 1def256f-f26a-4835-b7d0-f99574a8aa70
checkpoint-no-status |  |  | checkpoint | Test Phase
checkpoint-status |  |  | checkpoint | The sewer drainage pipe has been filled with air as per section 15.3 of AS3500.2.2021
checkpoint-status |  |  | checkpoint | Pressure of approx 15 kPa has been applied to the drain. When approx 15 kPa has been reached, the compressor has been shut off
checkpoint-status |  |  | checkpoint | Air pressure has been stablised for not less than 3 min while checking for leaks
checkpoint-status |  |  | checkpoint | After the pressure has stablised, commence the test when the pressure has fallen to 10 kPa
checkpoint-status |  |  | checkpoint | Record the time and drop in pressure over the minimum test duration depending on pipe size (eg, 100DN = 2min test)
text | 50618bb2-d6e0-53a2-8c09-de9081092d43 |  | textbox | Start of test: Note start time and include photo of include photo of calibrated gauge at the start of test
text | 3f10bd97-cd26-5725-893c-a7584752c05c |  | textbox | End of test: Note end time and include photo of include photo of calibrated gauge at the end of test
checkpoint-status |  |  | checkpoint | The test has been deemed successful if the pressure does not drop more than 3 kPa over the test duration
checklist-flat |  |  | checklist | Testing - Water Hold - Sewer & Stormwater Underslung |  |  |  |  | Yes | (LATEST) Testing - Water Hold - Sewer & Stormwater Underslung | 207acaa9-457d-41df-8585-380caa082701
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for water hold test of underslung sewer & stormwater drainage
checkpoint-status |  |  | checkpoint | Pipe has been checked and is clear of blockage
checkpoint-status |  |  | checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint-status |  |  | checkpoint | Open ends have been sealed
checkpoint-status |  |  | checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint-status |  |  | checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint-status |  |  | checkpoint | Water was drained from the pipe at the end of the test
text | 775dfe1b-8aa7-5b73-b44e-a00cb567b3d8 |  | textbox | Water level photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat |  |  | checklist | Drains: Syphonic - Underslung |  |  |  |  | Yes | (LATEST) Drains: Syphonic - Underslung | 20ed241a-4a01-42a1-bb24-233a2746a930
checkpoint-no-status |  |  | checkpoint | Syphonic underslung drains have been installed as outlined below
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status |  |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status |  |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status |  |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checklist-flat | 6959891d-0b92-44ae-b087-8b8411faa2f9 |  | checklist | Enter Level/Apartment/Description |  |  |  |  | Yes | Record Hold-Up | 21beb992-20d6-4dc5-8a0a-6161b6f1629b
checkpoint-status | 29c1ce54-3941-416f-970e-71384848811e |  | checkpoint | Decription of Hold Up
label | 2e3c3582-73df-5fa8-9088-8e2c74dbcf06 |  | note | (See Photos & Comments Attached Below)
checklist-flat |  |  | checklist | Comm/HO - Commercial Final Commissioning - Fixture Group |  |  |  |  | Yes | (LATEST) Comm/HO - Commercial Final Commissioning - Fixture Group | 21f14d2b-a003-484f-a350-ee22f896cb73
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for final commissioning of all installed fixtures
checkpoint-no-status |  |  | checkpoint | Bathroom/WC Area
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery does not exceed 50degC on any fixtures
checkpoint-status |  |  | checkpoint | For SDA or DDA areas only, hot water delivery does not exceed 45degC on any fixtures
checkpoint-status |  |  | checkpoint | WC toilet seat and lid secured and fastened with soft close function operating
checkpoint-status |  |  | checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Wet area grated outlets are installed correctly
checkpoint-status |  |  | checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status |  |  | checkpoint | Cleaners Sink
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint-status |  |  | checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Wet area grated outlets are installed correctly
checkpoint-status |  |  | checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status |  |  | checkpoint | Kitchen
checkpoint-status |  |  | checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint-status |  |  | checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint-status |  |  | checkpoint | Pullout mixer function has been checked and has clear
checkpoint-status |  |  | checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint-status |  |  | checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint-status |  |  | checkpoint | All fixtures have been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint-status |  |  | checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint-status |  |  | checkpoint | Dishwasher has been run through a short cycle
checklist-flat | 1b169243-dc68-43ce-b405-664d74a27b8f |  | checklist | RW Re-Cycled Water Meters |  |  |  |  | Yes | RW Re-Cycled Water Meters | 29a09817-efe8-4756-976b-5d8a933e50f1
checkpoint-status | 68567258-f241-468e-9da2-4a6a240990dd |  | checkpoint | Water Meter Details:
text | 1bf0a78f-c1c5-5d33-a2b6-21766dd8e902 |  | textbox | Meter No:
text | d9333858-2bd7-50bc-acf2-4f936820fcfb |  | textbox | Level:
text | 8523f3d8-97e0-51ae-90ae-9301724d8b73 |  | textbox | Meter Size:
checkpoint-status | 59b77962-09bf-4630-a7c9-567c16bba5b2 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ce60ab8a-39ee-4e19-bf63-bfd726813a5a |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 63c79889-40d8-4667-8d98-ee69e8e64d03 |  | checkpoint | Meter bracketed
checkpoint-status | 4675ee96-af85-4fc8-926a-6457b5706530 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 19ca28be-68a1-433a-9382-74036e4af81e |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 0dd40b27-76bf-4008-9190-c6d42772d2a2 |  | checkpoint | Pulse rate value is correct
checkpoint-status | 2c346f9a-33e8-4681-8bf0-a4cd30eae8b8 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 87be5c84-3fc9-4775-bbdb-8191f27ae3f2 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | a1b5d034-e3e1-47f8-b04d-238316441540 |  | checkpoint | Flow direction is correct
checkpoint-status | ae5e9c9f-3701-4c8c-85fa-e394467bd765 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 35c8c864-ee82-4cc9-b1a2-910fa9f0c9a8 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 50fd5e50-683f-4cbe-8389-08df4164f490 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Risers (CW, HWF & HWR, Rainwater/Non Potable) |  |  |  |  | Yes | (LATEST) Risers (CW, HWF & HWR, Rainwater/Non Potable) | 29d6faa3-99db-40aa-8543-c39ddbce6f53
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for install of all risers
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint-status |  |  | checkpoint | Any v-hose, victaulic joints are watermarked and installed correctly
checkpoint-status |  |  | checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Branch junctions & off-set levels are correct
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct
checkpoint-status |  |  | checkpoint | Checked for damage prior to install
checkpoint-status |  |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint-status |  |  | checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint-status |  |  | checkpoint | All risers are ready for testing
checklist-flat |  |  | checklist | Plant & Equipment Install - Cold Water Pumpset |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Cold Water Pumpset | 2ae3fd14-896d-4530-a2e7-9aad55940435
checkpoint-status |  |  | checkpoint | Cold water pumpset has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all supply lines have been undertaken
checkpoint-status |  |  | checkpoint | Cold water pumpset is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | Photos of installed cold water pumpset have been included
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Toilets & Cisterns |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Toilets & Cisterns | 2dc2ffde-6290-4243-a7db-80c175c0bae4
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for fit off of toilet and cistern (this is not a commissioning ITP)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | Installation is aligned, level and secure
checkpoint-status |  |  | checkpoint | Flush pipe has been measured to suit the pan prior to being cut to size
checkpoint-status |  |  | checkpoint | Button flush plate is in working order and not damaged/scratched
checkpoint-status |  |  | checkpoint | Seat and accessories are secure and correct
checkpoint-status |  |  | checkpoint | DDA suite back rest installed correctly
checkpoint-status |  |  | checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint-status |  |  | checkpoint | Pan trap is clear of debris
checkpoint-status |  |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status |  |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 3257ceca-046f-469b-9a21-c62013da22e6 |  | checklist | CW High Level/Corridors |  |  |  |  | Yes | CW High Level/Corridors | 33c7b06e-5695-42a6-b157-de7b4655a322
checkpoint-status | ca9e237c-ea53-4bb2-82f6-1289473d79f9 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 378603b0-9083-4646-aa48-4673f5e6821b |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 8a50e4bb-cad2-4dd0-803f-3229e98a83df |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a3b2ccb8-1c60-4814-97cd-69c38fc75103 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c1ef2aea-c83b-41ba-999b-b8588269f97a |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 82aba98d-5a49-4f87-af71-8c2bbb969938 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | bf5750c7-9f60-40fc-a13e-f9f1d35e1f8e |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 0ccf37c6-2e2f-41e3-8704-7d193fea19db |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | f7d362a1-4e98-4320-ac99-ba35b952538e |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 16bc3443-ac8b-47e2-b161-90cd04741c50 |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | 65368135-71fb-4e3c-b694-260368d60575 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 55e46df0-c061-4d99-a0ad-f3bf0284658f |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | f6f5cd47-cfef-4307-a251-7987b3e73562 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 47c9960c-0afe-47a2-aeee-8e61f78fe0d8 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | f24fa30e-0b56-49d7-9834-cc9709240b68 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 1e014d01-a3cc-47b3-8686-cf9df3c29e2e |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7e0dfe69-cd2e-44c3-85e7-75216469332a |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 8b9f3da8-9687-421f-b961-1f3df40191bf |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 07611780-9a10-4b68-ad6a-10d9325bb014 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 67aac4f5-f36a-4a2b-85f8-75bbb3dd5270 |  | checklist | PE Above-Ground Potable Cold Water Pump Package |  |  |  |  | Yes | PE Above-Ground Potable Cold Water Pump Package | 34229ed9-33a1-49fc-8e7d-38defa7dfe4d
checkpoint-status | 7dc86013-3e22-4315-b52b-17683ed4a578 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | eb3079ae-3e4b-451f-8d09-e2e63bffb3a2 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | ad3d4f7e-6b02-441f-a49f-994d9e85958d |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | e955bf79-2365-48cd-8d86-766bb38227f9 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 7b04d0b6-6440-4abb-a644-fba2c3d283da |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | 7dc00e14-1993-4fe4-9b6a-76eede4b7deb |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 8ff43dec-4f84-4fe0-9ae4-9b051a5c8c04 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 4ebb2173-29f3-4664-8a9f-43861243b149 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | 63d4fa66-02b0-4abb-b822-366b9b75f96f |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | ce958cb1-da47-4cfc-9a11-ab3d059edbba |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 89e68855-7a55-4efa-a7d1-be071333fdbe |  | checkpoint | Electrical cable is installed
checkpoint-status | 23253fda-8b9e-4e3b-bc9f-c819024f4e54 |  | checkpoint | Control panel is installed
checkpoint-status | d35db932-fb2b-4b97-a23c-e41e671ea646 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | c9bc9e29-061b-46a8-982d-c5e969cfdc87 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | d8edb78a-de3b-4eb3-9e3c-8cdf20fe7cf9 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | e592beb4-8a20-4674-b319-629b8ac6d55a |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 9808fb6c-3ec9-47fd-9766-12d8ab608720 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 73330255-2be7-426c-bcd1-39504c298c85 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Drains: Trade Waste - Underslung, Stacks & Vents |  |  |  |  | Yes | (LATEST) Drains: Trade Waste - Underslung, Stacks & Vents | 3566a708-5c2c-41e3-81cc-3b1a45d3f818
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status |  |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status |  |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status |  |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status |  |  | checkpoint | Tradewaste pipes have been tested with water (include photos of test)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | 5d75f097-83af-49b4-bf26-17806731d374 |  | checklist | PE In-Ground Grease Arresting Tank |  |  |  |  | Yes | PE In-Ground Grease Arresting Tank | 3610fdc7-e1c8-4afd-911e-ba71fa814825
checkpoint-status | 86bc1298-2e7f-4340-a246-a03b5f45e4da |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | cde537a2-b5d8-491f-a8a1-8cc17ebd0e76 |  | checkpoint | Authority applications & start work notices accepted
checkpoint-status | 8553dc35-7a68-435d-9639-9140fcfcc201 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 1c275509-8043-4248-b0a5-bc023d5aadea |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 0c9dc1fe-77f9-49f9-8c9c-895f039133df |  | checkpoint | General visual check for damage, etc
checkpoint-status | e2d3ad6e-7ff1-4e07-82eb-4da247d5ebf9 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | ee13ab41-d2e3-41b5-886f-3c9994302c36 |  | checkpoint | Vents are installed if required
checkpoint-status | 501327ba-c0da-4bb1-b657-81d8a16aff95 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 6d9d01e0-700a-4548-bb2d-17ee96cd9d79 |  | checkpoint | Spoil is removed
checkpoint-status | 44bad9f3-a08b-42b6-8189-9812c7bf6f65 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 04f5b1ef-a561-470e-b056-b34895bfc5b7 |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | 6580f9dd-5584-4ef7-ad13-44413e4da7bf |  | checkpoint | Disconnector trap is installed & connected
checkpoint-status | 8e68e923-613e-48a4-9088-da3f4881c6e9 |  | checkpoint | Vacuum-line installed & connected
checkpoint-status | c8e5af29-fd97-4e36-aa10-2aa174c79c10 |  | checkpoint | Vacuum-line stortz couplings & caps are installed
checkpoint-status | ef18c647-bb05-4623-8c2d-a0b54ac05382 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 5a3c8bb1-58d6-4679-8b45-3cd7ac05cda8 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Hose Taps |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Hose Taps | 36317add-56f9-4a40-8f2f-e69d16a0d83f
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for fit off of laundry hose taps (this is not a commissioning ITP)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | Hose Taps have been installed aligned, level and secure
checkpoint-status |  |  | checkpoint | Backflow prevention device has been installed
checkpoint-status |  |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 87be32f1-f680-47cb-9f45-c4d7043286bb |  | checklist | MT Natural Gas Meters |  |  |  |  | Yes | MT Natural Gas Meters | 3784e5ea-4e76-410d-a494-d44ba47bb392
checkpoint-status | eb0aa058-3929-44ac-a60a-b0f4916ae5ee |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 3547cc79-bfa8-433c-aef8-f726173cc618 |  | checkpoint | Natural Gas Meter Details:
text | a89b7158-e638-5e52-a4f2-dac5be2ea6a4 |  | textbox | Meter No:
text | 26a0a29d-e5d0-5d6e-9bac-19662f28e2f9 |  | textbox | Meter Location:
text | ad1b815f-a712-5058-a4dd-62528b1ea0e6 |  | textbox | Meter Size:
checkpoint-status | bee4c451-6e86-4f8c-a244-090f6b80a65a |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 4d768b32-e863-425d-959f-322076c2c90d |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | bb71efa5-fd0b-4cd7-a91c-4132e38824eb |  | checkpoint | Meter bracketed
checkpoint-status | a8f8cc3d-bcb2-451d-b8a2-d672736532be |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 7164cf45-73f8-49b2-8208-e7f7f9de201c |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 2992908b-6f33-4913-a233-891c733edee0 |  | checkpoint | Pulse rate value is correct
checkpoint-status | 2bed7e83-0078-4f89-8621-f20366413711 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 841242d2-556d-4d54-8229-9097d8078448 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | e85ac9d3-31c8-4bdf-93b4-cca2d4397341 |  | checkpoint | Flow direction is correct
checkpoint-status | 7ef96c22-0cc0-4e87-a0a6-2d414433e2e2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 9c361f2f-4def-49ba-b61a-0180c3028bfd |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 33026a99-4b86-438c-9778-3cf342b19409 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Ingrounds - Sewer BT Authority Connection |  |  |  |  | Yes | (LATEST) Ingrounds - Sewer BT Authority Connection | 37b750a1-6c6f-4cbf-b41a-eaa32d13f190
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - Sewer BT Authority Connection
checkpoint-status |  |  | checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | Installation meets water authority requirements
checkpoint-status |  |  | checkpoint | All pipe elements free of damage prior to install
checkpoint-status |  |  | checkpoint | Boundary trap is installed and supported correctly
checkpoint-status |  |  | checkpoint | Reflux valve is installed and supported correctly
checkpoint-status |  |  | checkpoint | Access riser to surface level is installed
checklist-flat |  |  | checklist | FINAL Commissioning - Stormwater Pumpwell/s |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Stormwater Pumpwell/s | 39f1c9ed-f0f1-4d93-9480-3b4618964265
checkpoint-status |  |  | checkpoint | Stormwater pumpwell/s commissioning report/s to be uploaded here
checkpoint-status |  |  | checkpoint | Stormwater pumpwell final install photos to be uploaded here (show connection to active board)
checklist-flat | 34dc9509-59f5-480d-8b6e-046389a4d85d |  | checklist | RW High Level/Corridors |  |  |  |  | Yes | RW High Level/Corridors | 3a570b5f-cbf4-4923-a16a-070a74aca063
checkpoint-status | 0a5c5113-5c0a-4e1b-8655-bcbf5f6bee15 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ade914e9-49d8-4480-a27c-1207ad8d9eb9 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 3f425dfd-6c09-4f30-82dd-0bcba740b9d5 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a7a8d9aa-41ea-44df-bfdb-b88cbe9b95fe |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c7126ea5-2202-48cf-9268-7f81006cc7ed |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 72ec79a7-ba17-47f8-99bb-6ce34c18e1d4 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 149eb114-29f7-4942-a935-16c820f2bd7e |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 69fa57be-4d3a-47f5-98d0-b36cc87669b1 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | b42aeca5-906d-41e9-9c0b-ca67d0d28ee3 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 7227d359-858e-4de6-a7da-0b30341d8f99 |  | checkpoint | Meter manifolds & frames are firmly bracketed & installed in sizes, quantities & locations as per design
checkpoint-status | ec7e2c16-1197-4d48-93b0-a7bdcba7ae0c |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 6bb8421a-7f75-408b-8c93-f1f94ce1d128 |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | e0a10e9f-6615-4a06-a534-9a6b9cdcb835 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e2660bb1-9f15-494e-b881-e8e98b221c5e |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7c5e38de-25d0-4694-b393-7700b9ec0979 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 52e1e0eb-4ce7-43e9-8152-67ee582e05af |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | cc295f97-b04b-485e-8c42-3c6582ef6da4 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | ef48e7a9-5a28-4e11-81aa-eb9a684fa0a8 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | e6981bcb-0101-424c-aef7-1ba1e3887eb4 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Ingrounds - Pumpwells/Tanks/Pits |  |  |  |  | Yes | (LATEST) Ingrounds - Pumpwells/Tanks/Pits | 3a9d0f82-7df7-4c34-92a0-fe2a7509889b
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - Installation of pumpwells/tanks/pits
text | 4c7c7d03-9685-5e7f-9f62-bda5246363ea |  | textbox | Description of work zone (e. location/drawing grid reference)
checkpoint-status |  |  | checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint-status |  |  | checkpoint | Installation methods & materials are in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Invert levels for inlets, outlets and cover levels have been checked against current IFC drawings
checkpoint-status |  |  | checkpoint | Connection of drainage to pumpwell/tank/pit has been sealed/caulked/grouted both inside and outside
checkpoint-status |  |  | checkpoint | Cast in conduits to pump control panels are correctly sized and in accordance with current IFC drawings
checklist-flat | d0d2d4f7-a322-46ca-b655-3aa486473641 |  | checklist | TST Testing Roof Downpipes (Water Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Water Test) | 3ae5ae58-4b45-49aa-ab11-0d8ce68c679b
checkpoint-status | 62cf6ab6-07d4-4313-8f3f-ca1f83e7cc1d |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status | 5d067915-1e4f-4c9d-9ff9-7324d9532676 |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 23f8695d-6562-48b2-9942-2153a289596b |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | eb00178f-c2c1-4098-acc5-419f8124b901 |  | checkpoint | Temporarily plug & seal any open ends below the test point
checkpoint-status | 80f868c1-e15e-4bff-b642-a5bea1348e8a |  | checkpoint | Choke test to a head of 10 metres or if the downpipe if shorter, fill to its limit
checkpoint-status | e693062a-712d-4409-ae97-2ad5e645e3d6 |  | checkpoint | Slowly fill the test riser with water until full and hold for 30 minutes
checkpoint-status | 1b59040f-5b2f-4390-97f4-ff1b46eaeab1 |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 30 minutes
checkpoint-status | 976febd3-d471-49f4-8c23-94f0a77c58e6 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | f7a291a6-a5d2-4488-8a93-84854f099c7b |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | 18efd130-a386-40ab-9c6b-3c59ad8e71e5 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | ac8b7088-aee6-4e92-b0e2-7e8dc834aa0d |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 79ebb149-5ca5-452b-b160-298152fe4d59 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | Main Run Rough In (Gas) |  |  |  |  | Yes | (LATEST) Main Run Rough In (Gas) | 3b8e5a7d-1da5-4282-aa9a-8d6a20d24315
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for the main gas run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status |  |  | checkpoint | Clips and fixings are correct
checkpoint-status |  |  | checkpoint | Pipe run position & levels are correct
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status |  |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status |  |  | checkpoint | Flexible connections are correct
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Rough in is ready for a gas test
checklist-flat | 4bb74aca-b76e-48ed-8a77-24fbf39d4ca3 |  | checklist | SW Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SW Downpipes/Overflows (Main Droppers) | 3c3c4b4e-9a07-4d71-ac02-cfd29c43a3c9
checkpoint-status | 090dbbba-de07-4bdf-a051-225a017f90c5 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ac128060-1ed4-4f8f-b458-34c35f890dd9 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 68d36df3-fbaf-42d5-bb07-61f98ff72c5d |  | checkpoint | Pipe materials are correct for application
checkpoint-status | e8c112b8-74e4-421b-bb98-488764ba36b6 |  | checkpoint | Downpipes are installed
checkpoint-status | a5aa4868-45ea-47e1-9663-515be2480cb4 |  | checkpoint | Overflows are installed
checkpoint-status | 24aa1744-ab54-4ddf-9ef1-db2fc9d4cf8c |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | dbbfba4f-6fb7-40cc-a3de-7d047d385ae2 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 76ac9ab9-77b4-4bad-9244-f931f4484b1e |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | e68c0790-5d45-4ab7-9dfa-f95228f678f6 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | e848d0b7-201d-41f3-b8a8-726e41b44869 |  | checkpoint | Penetrations are installed
checkpoint-status | 1d3ba217-9783-4e89-beb9-8674f9e56deb |  | checkpoint | Drain penetrations are caulked
checkpoint-status | cf4f4e6f-c5df-4df3-91a8-8022504d1b23 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 4e0eeea1-fe49-406b-b998-3e001ca25fa8 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7422bb29-72e3-47e9-88cc-b10ca70dd039 |  | checkpoint | Roof/overflow outlets installed
checkpoint-status | 10396ee0-fd57-45e8-ac75-bd7668cbc5a6 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 2c0c558d-6e77-4a12-848c-3d526cad06ac |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 2fc73862-9b33-43de-84de-3cf637608c12 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 49225b1e-ede8-4ddf-9457-51b0292658c6 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 542ab373-3401-48cc-8f78-49f3ac378cc9 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c0966762-f057-4c2c-bf19-3c19611042a1 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 109c880a-f42c-47c6-b6e7-a66c4211e643 |  | checklist | PE Hot Water Generating Packaged Plant |  |  |  |  | Yes | PE Hot Water Generating Packaged Plant | 3c3d15e3-c785-44e6-a676-e0cc6a3a7c0a
checkpoint-status | 65ae2020-5caa-4f8c-addb-f2b3cb816ffb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 6d721781-f5b3-4cf4-b74a-4da1e8b61965 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | fcfe837d-0985-4d76-91d6-83647c87d735 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 8ebe4a23-7a1a-48bf-855f-de0e4c032490 |  | checkpoint | General visual check for damage, etc
checkpoint-status | a6a68229-4c6f-41e0-b884-89e295a29cd0 |  | checkpoint | Visual check for water leakage
checkpoint-status | 743f3cd2-0bdf-4c79-ae4c-143eaa7af602 |  | checkpoint | Perform natural gas leak detection procedure
checkpoint-status | dba89218-7d6f-49a1-8315-38a9d1077ea8 |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 9df29ef3-3d9d-4cf8-a919-4ce5f588937a |  | checkpoint | Cold water check meter is installed & connected
checkpoint-status | a0d3f634-e59c-4b10-a13c-276de7338af8 |  | checkpoint | Natural gas check meter is installed & connected
checkpoint-status | b83e2c01-707c-4824-826a-9627d2ba7423 |  | checkpoint | Cold water inlet pipework is installed & connected
checkpoint-status | 7d49f697-f012-4abf-afb4-144cbfd38e9c |  | checkpoint | Hot water outlet pipework is installed & connected
checkpoint-status | 6ab72879-bd4c-4f86-b97e-30c32758b27a |  | checkpoint | Hot water return pipework is installed & connected
checkpoint-status | f11efb5f-5529-4a4d-8441-e33f1d647afe |  | checkpoint | Hot water pipework is thermally insulated & correct weight as designed
checkpoint-status | 5b8ec57e-5e7f-4ddb-94aa-eb214f67f2f1 |  | checkpoint | Exposed hot water pipework is completely sheaved & weather proofed
checkpoint-status | 2f6d0bf0-c656-4861-8e47-b3ea87f3e082 |  | checkpoint | Natural gas inlet pipework is installed & connected
checkpoint-status | 7135d68f-7814-4bea-855c-1d46c32c1a71 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 8207582f-b793-42ee-b4f0-e3b9d727f39f |  | checkpoint | Hot water exhaust pipework discharges over dedicated hot water tolerant drain point
checkpoint-status | 201ab46c-cae7-4f27-ae5d-085973aa4c42 |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 3b8d192d-7c91-4c78-9394-e6a02e9bb836 |  | checkpoint | Electrical cable is installed
checkpoint-status | 877dc67d-748f-400c-a7c8-3a1509670075 |  | checkpoint | Power flue is installed & terminated as per design
checkpoint-status | 6e3fa903-0307-4b09-9be2-fea50da9b5c0 |  | checkpoint | Control panel is installed
checkpoint-status | ff3d7b9c-2165-4b07-a2eb-543efd6bb8b0 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | ea6e582e-ece0-4bfa-b18a-cb7b0f9e63bc |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | a5742d57-5e4b-4009-8973-ac83baf6b3a8 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | 1ea9ac52-ac20-4fce-85e5-0a4682a7e729 |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 4a716abb-5d9e-467a-aa0b-fa0c22525223 |  | checkpoint | Flow & return temperature gauges installed & running within operating limits
checkpoint-status | 725aefa4-8c49-4fce-a929-1b3cda21da69 |  | checkpoint | Hot water plant provider has fully commissioned & certified the plant
checkpoint-status | 54b8e18f-3dea-4c82-b4e2-3745c987f3f7 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 6f55e169-c52a-4921-8e67-54cd5a82f098 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Gas Cooktop |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Gas Cooktop | 3cc4b419-12dd-44a8-91a1-1bfe2786c39c
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | Cooktop has been installed aligned, level and secure
checkpoint-status |  |  | checkpoint | Surrounding wall material is fire rated and complies with manufacturer specs
checkpoint-status |  |  | checkpoint | Distance from cooktop flame to underside of overhead joinery/rangehood complies with manufacturer specs
checkpoint-status |  |  | checkpoint | Isolation valve has been installed
checkpoint-status |  |  | checkpoint | Gas regulator has been installed
checkpoint-status |  |  | checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint-status |  |  | checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint-status |  |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat |  |  | checklist | FINAL Commissioning - Diversion Valve |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Diversion Valve | 3fb987ec-f18f-4651-a582-5cf63d74a0ba
checkpoint-status |  |  | checkpoint | Diversion Valve commissioning report to be uploaded here
checklist-flat |  |  | checklist | Plant & Equipment Install - GIT |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - GIT | 3fe11a75-b868-4069-b2fd-bdfc5475a460
checkpoint-status |  |  | checkpoint | GIT has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all suction lines have been undertaken
checkpoint-status |  |  | checkpoint | GIT lid has been lifted and all formwork has been stripped
checkpoint-status |  |  | checkpoint | Camlocks cap have bene fitted off
checkpoint-status |  |  | checkpoint | Drop pipe installed inside tank
checkpoint-status |  |  | checkpoint | Lid has been resecured and lid fixings resecured
checklist-flat |  |  | checklist | Main Run Rough In (Hot Water) |  |  |  |  | Yes | (LATEST) Main Run Rough In (Hot Water) | 42cdd028-87dd-4c02-b434-873a011cfc2d
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for the main HWF & HWR run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status |  |  | checkpoint | Clips, fixings & furrel blocks are correct
checkpoint-status |  |  | checkpoint | Pipe run position & levels are correct
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status |  |  | checkpoint | Hot water meter has been installed
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status |  |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint-status |  |  | checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat |  |  | checklist | FINAL Commissioning - Cold Water Pumpset |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Cold Water Pumpset | 45439cee-db1e-4fea-b3b5-d060b66bbb63
checkpoint-status |  |  | checkpoint | Cold water pumpset commissioning report to be uploaded here
text | 2ac9af7c-722d-5b0c-b06d-6a95830910fc |  | textbox | Cold water pumpset has been commissioned to achieve a set working pressure of |  |  | kPa
checkpoint-status |  |  | checkpoint | Cold Water pumpset final install photos to be uploaded here (show connection to active board)
checklist-flat | f9709404-465a-48b5-b950-71373bb3a405 |  | checklist | SYP Syphonic Downpipes/Overflows (High Level) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (High Level) | 472a7e11-ef99-440e-b155-9b67a53f35dd
checkpoint-status | f4e732ed-c454-401b-9dc5-9cc9ce88c7a4 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c2fad174-caa0-4487-9f87-68ea239eaee3 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 5ade3f39-f302-4328-b817-4ab7f816bb3e |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 0784520c-9c8b-4fde-9311-859defb01a36 |  | checkpoint | Downpipes are installed
checkpoint-status | ab5d95dc-8970-4792-8b81-de924f5fb323 |  | checkpoint | Overflows are installed
checkpoint-status | d883d41f-5994-4546-a7cc-530b859239db |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | b31b764f-7daf-44b3-a7a6-b67af8b2acc6 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 426b48a9-4ba9-4d51-807f-c9aad037680d |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | fceb4029-20e0-4b1a-af77-c4fabd113364 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 52b9d3ce-cdfe-437b-91c7-d4e0a3a56198 |  | checkpoint | Penetrations are installed
checkpoint-status | 4c320c3d-d9ba-4cba-be9b-2c4ccb386862 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | b9fec945-25e9-44e7-bc19-42d00819d237 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | f027b6b8-22ef-4e97-8351-e99c9517760b |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 398e76be-05df-40b1-baab-b2535dac0860 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 965d9777-6ed3-421f-96a0-30bcdbe290bd |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | b38ece19-cd13-44d2-98cd-6f8f270fec76 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 36681eb3-9df9-48d2-8596-7671d65fb205 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 5bd487b5-35d3-48b9-8645-b355791a93c9 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | d3b5d811-570b-455d-abae-716a8af4acd0 |  | checklist | TMP Temporary Plumbing Services |  |  |  |  | Yes | TMP Temporary Plumbing Services | 48df5bce-c777-4429-aeb7-32b99db12d94
checkpoint-status | 7172c8f1-a2af-40c7-b399-43fb1cef56ce |  | checkpoint | Work Completed (As per below)
label | d89903d8-a81e-5065-a488-4e1d9425de71 |  | note | Add Comments/Photos below as applicable
button | 08ac1e61-f6d2-5a70-99c6-fcac632c8420 |  | button | Installer is a Registered Plumber/Apprentice (VIC) | N/A, No,Yes
button | 7074cdb8-d8b9-5cac-a3fe-b3c70a653e9c |  | button | Installer clearly understands the task to be undertaken | N/A, No,Yes
button | 97332af3-ca1c-5eba-b425-24cb7c04fe83 |  | button | Ensure installation materials are used in accordance with manufacturer instructions | N/A, No,Yes
button | 3d946780-3170-5168-9f50-1cf01a6f43ae |  | button | Check for damage or leaks to the installation | N/A, No,Yes
button | 599bfe0d-30db-5484-8a4e-b33e6095939c |  | button | Check pressure pipe joints are installed correctly | N/A, No,Yes
button | 782d0596-8257-5689-9bb3-27bb6c302aa8 |  | button | Check PVC joints are cleaned & glued (no duct tape) | N/A, No,Yes
button | 7e65ee57-9f11-5f14-8671-abedf4d8da32 |  | button | Ensure all waste/rain water discharges to a live drainage system | N/A, No,Yes
button | 1d7377b7-c206-56ab-bb7a-5817064ec75d |  | button | Ensure all pipe & fittings are not reused | N/A, No,Yes
button | fcb86749-abc2-544c-bf1f-e5fcf798858c |  | button | Check cross connections between reused & potable water | N/A, No,Yes
button | 6e45d6ec-29fc-51cf-a410-84dff12224b8 |  | button | Check Jump Form temp connection when jacking | N/A, No,Yes
button | ef9afda6-ad31-54ab-ba05-5354d03d046d |  | button | Check any open ends are sealed and/or capped | N/A, No,Yes
checkpoint-status | 9af164ea-ed50-40a6-938d-1d990f92b789 |  | checkpoint | Final sign off - Pass when Work completed to specifications/drawings (Any issues please comment & Add photo's below)
boolean | 0d562912-1ca9-5e36-b904-908d04bce234 |  | tickbox | Area clean
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Cleaners Sink |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Cleaners Sink | 493e9b80-3fce-4c0f-a457-d49819113627
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for fit off of cleaners sink (this is not a commissioning ITP)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Sink & tapware has been checked for damage. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | sink & taps have been installed aligned, level and secure
checkpoint-status |  |  | checkpoint | Trap connection is clear of debris
checkpoint-status |  |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat | 32181fcd-e9c1-405b-b901-4accd0270fe3 |  | checklist | New Task: |  |  |  |  | Yes | Add New Task | 4bd67ba7-cb35-4dbe-ac34-a9e285fdc741
checkpoint-status | 911e3ad2-9021-413c-a5f3-9fb56f1c6d17 |  | checkpoint | Task completed
checklist-flat | a5446e89-e336-4519-ba5d-d2f74fdff81e |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) High Pressure | 4ee9e62f-162e-4b71-b551-d3947c7c5df6
checkpoint-status | 9ae54806-6e4c-4a5f-a793-f066b7aae094 |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status | dd006164-76d3-41a2-854a-4b9fcc5810fa |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 5732ed7b-2182-4522-b797-1fb67065e2a6 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 52b9de8c-d781-4c26-bd5a-790a4dcb4205 |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status | 1da7d467-b365-499b-9992-7e359935498d |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 8049cae8-a08d-420f-994a-33bef2e45664 |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 34204d52-c908-4637-9106-d17867612369 |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status | b23a7543-2d7e-4650-b94e-40464c15b08a |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | e184d6b8-e1bd-4930-945c-e6c6515874f9 |  | checkpoint | Shut off the gas feeder valve
checkpoint-status | 7e82d984-b77a-41a6-babe-ca79713d84f6 |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status | b837191f-a3fd-4ece-9582-86770107f157 |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status | 45405978-ed7d-4721-855f-4da2cf4b7eae |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 2cb5b463-2c27-44a6-906a-1fcd0045b797 |  | checkpoint | Test sticker in visible location
checkpoint-status | a18db677-d18c-4e54-852d-4b86ea2b6cfa |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 5c18bd07-f729-41bc-8dfb-91add8fdf872 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 27b7a3ae-b039-4103-84b0-f7f3b93db87d |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | Testing Potable Water - (1.5 times maximum working pressure) |  |  |  |  | Yes | (LATEST) Testing Potable Water - (1.5 times maximum working pressure) | 4f100c47-3237-447f-950d-a64359132b79
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for water test on fittings that can not be tested to 1500 kPa as per manufacturer's guidelines
checkpoint-status |  |  | checkpoint | Water test is being conducted on material that is rated to withstand BELOW 1500kpa
checkpoint-status |  |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status |  |  | checkpoint | Air purging valve point has been nominated
checkpoint-status |  |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint-status |  |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status |  |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status |  |  | checkpoint | Test consisted of slowly increasing the pressure to one a half times the working pressure and the pressure held for not less than 30mins
checkpoint-status |  |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | 8d2e6bb0-8fda-55cd-83fb-476b59b1bdb3 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | 23a97c24-fdf6-446f-8b09-551205beeb53 |  | checklist | TST Testing Sewer Drainage (Water Test) |  |  |  |  | Yes | TST Testing Sewer Drainage (Water Test) | 4f1fb02d-3e69-48d0-ae0d-a774c03c1115
checkpoint-status | df073688-d844-4380-99ab-eb7c3ea313fb |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.2 (2018)
checkpoint-status | 6a4e53ee-896d-4cd6-983c-f43748b1fe5a |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 5934a0a9-4aae-472e-a682-2bba74de1a8a |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | 1bb5a494-f36c-4b85-ae57-fa7703f4fc72 |  | checkpoint | Temporarily plug & seal any open ends below the test point (i.e. floor or shower wastes)
checkpoint-status | abb14718-e199-47d8-b657-3e4eebae900f |  | checkpoint | Extend a temporary test point riser to a height of 1 metre above the highest overflow point
checkpoint-status | 24bddb2c-b26a-423d-8a49-1ad12c3d24aa |  | checkpoint | Slowly fill the test riser with water until full and hold for at least 15 minutes
checkpoint-status | 85b5f8a5-b96e-45e3-b3ff-04106b6ed1e6 |  | checkpoint | Testing is deemed successful if the water level remains unchanged after 15 minutes
checkpoint-status | 8859a627-9973-4b25-9c12-1b24b7171501 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | a979dbc0-32d4-4405-9c98-dedc442b6793 |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | b35f3e95-ef7b-484f-bb89-576bbc4674fe |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | fac3671f-ddf5-45d1-bd3d-83509aac5bdc |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 03865c12-6c85-496c-bf68-43764919b4d1 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 57a61d17-1a49-4c34-962c-8f8467dcf4a3 |  | checklist | CW Cold Water Meters |  |  |  |  | Yes | CW Cold Water Meters | 506027ec-32c3-4c58-a7ce-78e61bf82948
checkpoint-status | 57665d3a-08f3-4230-85b3-651cec68f2ee |  | checkpoint | Water Meter Details:
text | 4d1a8338-3dce-5266-9b5d-c8672d970b56 |  | textbox | Meter No:
text | a426ba8d-c781-5e2d-b2dd-e4c5664dafd6 |  | textbox | Level:
text | b940cbec-f7ec-5034-a7cf-006ae60238d1 |  | textbox | Meter Size:
checkpoint-status | f4aadea4-0035-4b73-a049-bd3be07a34be |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 475f3f7e-60dc-4d99-9b19-f0a6073b7cbc |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 077b4a6b-f7da-4d8a-89f5-1f6bb8972b74 |  | checkpoint | Meter bracketed
checkpoint-status | 988e8c9a-14a9-4164-954d-07815091d69d |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 802fdd79-12a9-45d7-bc22-802b7152f075 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 13f42ef4-bf74-4a74-94bd-f6a3718fd17e |  | checkpoint | Pulse rate value is correct
checkpoint-status | 66aa9461-c9a9-46d7-a818-738e4f04e581 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | fc8f00de-12f1-479c-bff8-7a13f7371d39 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 21e016ff-bb59-4a5d-b753-65b6db121e60 |  | checkpoint | Flow direction is correct
checkpoint-status | 6594e313-c788-43fc-b48e-b7d11cb4f12b |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 63f8c1d7-3423-4eca-81f3-9b084193436c |  | checkpoint | Record installation by photo & time/date
checkpoint-status | af245b03-147a-40bd-b9e9-111cc8582088 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Plant & Equipment Install - Rainwater Tank |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Rainwater Tank | 52a58c6b-cfd8-490e-a980-e62a1413b3c9
checkpoint-status |  |  | checkpoint | Rainwater tank has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all pumplines has been undertaken
checkpoint-status |  |  | checkpoint | If underground, tank lid has been lifted and all formwork has been stripped
checkpoint-status |  |  | checkpoint | Flow control valve (eg Bermad) has been installed and is watermarked
checkpoint-status |  |  | checkpoint | Ensure float connection is secure and will be part of the commissioning by supplier (note, if the float comes off, it will lead to overfow issues)
checkpoint-status |  |  | checkpoint | Overflow is positioned 50mm above highest float setting (this is critical)
checkpoint-status |  |  | checkpoint | There is a physical air break from the tank-fill pipe height to the height of the overflow
checkpoint-status |  |  | checkpoint | Float is connected to the diversion valve
checkpoint-status |  |  | checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint-status |  |  | checkpoint | Rainwater tank & pump is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | Lid has been resecured and lid fixings resecured
checklist-flat | 83f1e51f-5ec1-40c2-84ef-07130760427c |  | checklist | COM Commission Fixture Groups |  |  |  |  | Yes | COM Commission Fixture Groups | 54b93f12-9632-4f80-b6c9-aa51086a31ae
checkpoint-status | 99519f19-a9a1-479b-b8e4-9cc9d6ba7dcd |  | checkpoint | Confirm the installer is qualified & trained to carry out the task as assigned
checkpoint-status | 2156416a-6fec-4668-8df8-d71ad6d2cc6c |  | checkpoint | Ensure all sewer drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status | 08d40142-fa77-4a90-9e6b-9a5e44731b66 |  | checkpoint | Ensure all down-pipe drainage pressure tests have been successfully carried out & recorded previously
checkpoint-status | 6f9b681f-4521-4c79-8390-b957bc1bd231 |  | checkpoint | Ensure all water pressure tests have been successfully carried out & recorded previously
checkpoint-status | 8e05253d-d5aa-4d76-b051-88422fe94ca9 |  | checkpoint | Ensure all natural gas pressure tests have been successfully carried out & recorded previously
checkpoint-status | 6b318466-30c8-4fd0-a894-2da03f9fb09a |  | checkpoint | Confirm the fixtures/tapware/appliances installed conform with the contract & specification docs
checkpoint-status | 3cdc1e5d-b712-484c-b12c-dc16b4ab15eb |  | checkpoint | Ensure the fixtures/tapware/appliances installed are un-blemished & fit for hand over
checkpoint-status | e0170610-c4c6-4478-b5ef-41b3cc231429 |  | checkpoint | Ensure the fixtures/tapware/appliances are installed level, square & centre of position
checkpoint-status | 75ef2068-1af7-4af6-a56f-37f621a5df35 |  | checkpoint | Ensure the fixtures/tapware/appliances are neatly & firmly fitted
checkpoint-status | ed918126-74fe-4cd1-b5b6-4344c2ba8f75 |  | checkpoint | Ensure the wall/splash-back materials & clearances conform with AS-5601
checkpoint-status | 7759a974-d729-4b43-a551-dd4d60f169bc |  | checkpoint | Ensure the range-hood height clearance conforms with AS-5601 & manufacturer tolerances
checkpoint-status | be7b2264-e601-46b9-87f7-b1e5fcf2eb8f |  | checkpoint | Check gas appliance burner operation for functionality & complete combustion
checkpoint-status | 39107580-bb5b-412f-b70a-4831c2d7c6f4 |  | checkpoint | Check installation of correct pressure reduction valves on dish washers, fridges, etc.
checkpoint-status | 9b2a8a37-3d34-4e17-9f82-55799abcb8ca |  | checkpoint | Check all valves, unions & regulators are fit for purpose & not leaking
checkpoint-status | 71ed4f68-1945-4981-8500-d56093b27b83 |  | checkpoint | Check for installation debris, glue, cleaner & set-out marks. (remove if necessary)
checkpoint-status | 6fc05388-1964-4ac0-887f-a2326f82c938 |  | checkpoint | General visual check for signs of water leakage
checkpoint-status | 676d76a6-0871-4773-8897-c7489d162b45 |  | checkpoint | Check cover plates have been installed
checkpoint-status | c560a844-56e7-4b7a-bd92-f4d7a3a0593d |  | checkpoint | Check mini stops have been installed
checkpoint-status | c726a584-6824-4737-9ecf-470cce321ee0 |  | checkpoint | Check flexible water/gas connections are fit for purpose with no twisting or kinks
checkpoint-status | ee22a489-3ee5-478d-9c62-40d2a4310bf3 |  | checkpoint | Check dishwasher hose for connection with no twists or kinks
checkpoint-status | 7fc22857-4abf-4c5a-b665-011291348360 |  | checkpoint | Check waste trap & associated connectors are installed with nuts firmly tightened
checkpoint-status | 53404143-c07a-406d-9cc8-ca2355577036 |  | checkpoint | Check all fixture & floor waste traps are clear of debris & free flowing
checkpoint-status | 49bab921-553f-4b49-bb20-c211840e1b6c |  | checkpoint | Check all balcony rain water outlets & overflows are clear of debris & free flowing
checkpoint-status | 3febeccf-388b-48ef-b268-70d5b22e4741 |  | checkpoint | AAV location & height is code compliant
checkpoint-status | 883a4067-e5d1-49de-822a-f8c79f97045e |  | checkpoint | Operate each fixture/tapware/appliance through its operation & functionality sequence
checkpoint-status | 3451652c-ef4e-4b8d-b24f-3876d75938a5 |  | checkpoint | Check hot water delivery time & temperature against contract specification requirements
checkpoint-status | 98545afb-63ff-4bf6-af25-c752f5bbe4a2 |  | checkpoint | Visually check inside traps & floor wastes for possible debris & ensure free flow of waste water
checkpoint-status | 7092a259-c3ba-4041-a79f-d097a57b87c9 |  | checkpoint | Check hot water thermostatic control valves (TMV) for correct function & delivery temps ≤ 43°C
checkpoint-status | 2c2d3372-d5d5-4c68-be93-c9c7b124ac4a |  | checkpoint | Check hot water temperature control valves (TCV) for correct function & delivery temps ≤ 50°C
checkpoint-status | 55ff24ca-37af-4c11-953d-83a7a4a6262a |  | checkpoint | Check location & functionality of any balancing or straining valves
checkpoint-status | a6479e2b-4488-4bc9-a0c9-1c639b723888 |  | checkpoint | Check correct operation & connections to all tundishes
checkpoint-status | 708eade8-e5c2-4626-9b46-5d40f2c47c73 |  | checkpoint | Check RPZD fitting is installed on balcony tap if required
checkpoint-status | 7d078610-c762-4986-ba6e-d95fca07d6f9 |  | checkpoint | Check quality & application of caulking is fit for purpose
checkpoint-status | 85124822-9ea8-469d-8749-c051d62b8905 |  | checkpoint | Check flood stoppers if in use on CWM stops
checkpoint-status | 9dd76828-d939-4993-9ec0-2f13c878c157 |  | checkpoint | Seal or cap off any open ends if required i.e. CWM stops
checkpoint-status | 487ec06d-9d44-470d-838d-e2fb18caadfd |  | checkpoint | Check valve tag numbers match their allocated location.
checkpoint-status | c2e2d075-ed2a-43ab-af4e-8ad4d9842af5 |  | checkpoint | Check flow meter numbers match their allocated location.
checkpoint-status | d05104d5-d816-4065-9c0b-1e02e52b0721 |  | checkpoint | Test sticker in visible location
checkpoint-status | cf3f5216-0a0b-4dc1-b426-82863a88f40a |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 54504cc7-5905-4e42-bc74-43a398f3e39a |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checklist-flat | 2d05a7ac-03f9-4758-91a4-40c29c0b309c |  | checklist | FO Irrigation/Hose Taps |  |  |  |  | Yes | FO Irrigation/Hose Taps | 55096593-54cf-4fd9-a8aa-2776a2a7cdd8
checkpoint-status | 277b4a6d-9980-4a82-8d03-a909c5581784 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d61db411-8673-46fd-b29b-f055ecac7d02 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | a151dc5c-4ba1-469f-bfc3-cf9ad9108a49 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | c09d263c-6684-422a-9a78-816c2d4f570c |  | checkpoint | Screw-on RPZD fitting installed if required
checkpoint-status | e1286726-1437-4eae-9580-963e12a2feba |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | bda86704-3717-485d-9bcc-469b7c5a009f |  | checkpoint | Check cover plates are installed
checkpoint-status | d8906a42-6bae-4d6c-8c78-4f2252f92221 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 3d43ac0b-934c-4383-b81f-828c12028474 |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 6ca4d82c-46f1-44ca-87f6-47e9490fdee8 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 67afe977-be65-40b3-8bbc-a8e26c99d903 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | Risers (Gas) |  |  |  |  | Yes | (LATEST) Risers (Gas) | 55199a23-f9b4-4a08-9c76-12d6bcf9b996
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for install of all risers
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint-status |  |  | checkpoint | Any v-hose, are AGA compliant and installed correctly
checkpoint-status |  |  | checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Branch junctions & off-set levels are correct
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct
checkpoint-status |  |  | checkpoint | Checked for damage prior to install
checkpoint-status |  |  | checkpoint | Disconnection unions are correct to allow for future maintenance
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Gas authority labels have been applied with working pressure noted
checkpoint-status |  |  | checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint-status |  |  | checkpoint | Gas riser/s are ready for testing
checklist-flat | 75b264d2-d29f-41bd-8963-8a5749362ca9 |  | checklist | CW Rough-in (Low Level) |  |  |  |  | Yes | CW Rough-in (Low Level) | 565c3967-c77c-4e41-8622-2037b0e97b30
checkpoint-status | 42eb4eb1-4f56-4818-a2a4-d20ecfb9867d |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c0e69a6e-bb96-4e00-ba16-7231204c5c9c |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 4014d8a5-e39c-43a5-b90e-6c7ea97f5f73 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 65751e39-1161-4104-b7a2-2daf27a52b70 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 7c4e17be-9eea-4ace-9dec-3433f75e17fb |  | checkpoint | Check TCV/TMV in wall box correct location & securely clipped
checkpoint-status | c89a5a8c-5036-4860-affd-8487a5a14a10 |  | checkpoint | Check RPZD in wall box correct location & securely clipped
checkpoint-status | ba03eb0a-2e88-437c-b0aa-d9504f71e741 |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | b9fd2279-8361-48ef-a7f7-5d6792a1c604 |  | checkpoint | Check In-wall mixer bodies & lugged elbows are installed to correct locations
checkpoint-status | 7ea716f2-1e3a-474d-8d5d-cf430aa42aec |  | checkpoint | Check in-wall pan/cistern brackets are installed to correct locations
checkpoint-status | 939441e4-1a24-489f-b126-73b2b9ddb181 |  | checkpoint | Check for possible cross connections
checkpoint-status | 4594c1f1-f504-454a-a823-1bb055669dac |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 1bf3433d-5ca3-4ac6-a709-04274e2efba8 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 44e4211c-0ab2-4614-95cf-67861a9e8191 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | f29a1c18-5a5e-4df2-8082-d650896ef3fe |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 85129786-e004-4352-ae61-16e4d3951011 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 294bb7c6-91aa-4352-a5b9-55d637203801 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 2546b2bd-5dcb-47f4-ae8e-dc48247d2a05 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 0b8dabc8-34bf-44a5-b0dd-a4f61842fe4e |  | checklist | FO Tempering Valve (TV's) |  |  |  |  | Yes | FO Tempering Valve (TV's) | 589a0933-6774-4c79-b4f2-ea69905bab56
checkpoint-status | 01b7c9d8-0b3c-4826-b9d3-71035fe4cd9e |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | cd34427f-b83d-4bf5-8ff5-83adec32bdc0 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 714f0bd4-613e-47c1-8ef6-69a0f6344ec0 |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | 020d7a5b-b93d-47d1-b28b-6c141c3d9a2e |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | 30a5f0b1-2d13-4bc9-8b36-b5770f781106 |  | checkpoint | Check cover plates are installed
checkpoint-status | cbe50f0e-3f04-498c-886b-b432f49d91da |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | f45f6889-6a26-4bc4-acf3-fd046e996c5f |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 45dd5fe8-22e5-4072-bbe5-c0c27da88161 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | d371c445-3b39-481f-acb8-e83b0fabe804 |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status | 15a2d69f-6efc-46a8-b5da-d5a26e37cc8f |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 9f8985c7-c516-4c46-8575-91d05497b337 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 67d6e940-5733-46d1-b994-8a56b01031b3 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | Drains: Pumpline - Underslung & Stacks |  |  |  |  | Yes | (LATEST) Drains: Pumpline - Underslung & Stacks | 58cee4b6-019a-46e6-a04d-17052d2dab6d
checkpoint-no-status |  |  | checkpoint | Underslung & stack pumpline drains have been installed as outlined below
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status |  |  | checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct with secure fixings to reduce pipe movement (eg thrust bracing)
checkpoint-status |  |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status |  |  | checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status |  |  | checkpoint | Pumplines have been tested with water (include photos of test)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | 170272e9-ea3b-42ef-90f9-23f16c3b6141 |  | checklist | FO Install Cold Water RPZD |  |  |  |  | Yes | FO Install Cold Water RPZD | 59c4c234-45e0-48a7-83a1-c27e2d0f4096
checkpoint-status | 071d129b-eb5a-48c0-b6d7-653bba0291c1 |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status | a5f66cac-fc70-4dfe-a9a3-ff6c45684998 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 3599d17a-c800-452f-894d-301aaaba638a |  | checkpoint | General visual check for damage, etc
checkpoint-status | e14b3ff9-3390-4e87-b66b-74f063ac668e |  | checkpoint | Visual check for water leakage
checkpoint-status | 6d246c39-815f-4782-825c-1235bddbc444 |  | checkpoint | Mountings fixed & torqued down
checkpoint-status | 9cb177ab-1ef3-4e02-b975-d65c9ddaaaaa |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 1fb60340-fb23-4551-a8df-218e76b274d3 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | cbcd6499-4e9d-46fd-a6ac-f5cdd6d3f36f |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | e17c449d-7947-4923-a8e3-dfadeb80d49c |  | checkpoint | RPZD tested & certified buy qualified practitioner
checkpoint-status | dbe04a42-cddb-4a02-86b2-01b475508b03 |  | checkpoint | Testing by pressurized Water or Air as per RSG procedure is completed
checkpoint-status | 5d2cf724-2c41-4573-a33d-64e44ad385b7 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat |  |  | checklist | Plant & Equipment Install - Diversion Valve |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Diversion Valve | 5b5e355a-d41d-429b-a8b6-0c485cfbf909
checkpoint-status |  |  | checkpoint | Diversion valve has been installed as per IFC drawings and as per MPS Design instructions
checkpoint-status |  |  | checkpoint | Connection to panel board is ready for commissioning
checkpoint-status |  |  | checkpoint | Ensure diversion valve is installed as close as possible to the diversion point to ensure debris is diverted out to the street
checkpoint-status |  |  | checkpoint | Diversion valve is ready for commissioning by supplier/manufacturer
checklist-flat | 92ace3b4-d13a-4cdb-ac0e-02597502dd6c |  | checklist | SD Sewer Drainage (In-Ground) |  |  |  |  | Yes | SD Sewer Drainage (In-Ground) | 5c05c3eb-bd40-4d3e-a6d7-e7cef120d9fd
checkpoint-status | b1d3dd73-ba1c-46c0-879a-fd56b9b253aa |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 07e87e26-da9e-49ca-8e2d-0cb76644e37d |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | d7d230ac-6f82-4412-a10c-f66cfd4f8370 |  | checkpoint | Authority sewer drainage applications & start work notices accepted
checkpoint-status | 29ba736b-b628-44f7-ba79-11106da404d8 |  | checkpoint | Authority connections installed by certified contractors
checkpoint-status | 190680df-46d1-455f-bd13-9d9320f03d70 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | f4385bcd-8c55-4b53-be70-19f15ba9814d |  | checkpoint | Sewer instection chambers are installed in sizes & locations as per design
checkpoint-status | 26a3a95f-e55e-4eae-b12b-8c7c12053bf2 |  | checkpoint | Sewer Boundary Traps are installed in sizes & locations as per design
checkpoint-status | 6056fa37-14ae-4825-9a05-740beebc76ac |  | checkpoint | Sewer reflux valves are installed in sixes & locations as per design
checkpoint-status | 39a6790a-85c5-446d-8efd-0c1c1a0bc0c9 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 9271ad58-918f-455b-92ec-5d396b957886 |  | checkpoint | Ensure all grades are correct
checkpoint-status | 08d5a3f8-fcbd-49c0-a8ea-62b3bab2307a |  | checkpoint | Ensure all invert levels are correct
checkpoint-status | c38f099a-d9ba-441a-86b5-b8a5247c06cf |  | checkpoint | Sewer vents are installed
checkpoint-status | 97a9c6d6-a7a3-489d-a5af-14e7add76ada |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 195cc7f5-c3a6-45da-a02e-851bdf3432b5 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 826ab118-0f38-43b4-a53c-520e91207d0a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 420be83d-6944-402a-a2a1-fcf3b38c4422 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | f704e963-c796-4243-ae62-40c3ccbed253 |  | checkpoint | Spoil is removed
checkpoint-status | 87ad58d9-db00-448c-b27c-4005e2696f50 |  | checkpoint | Vents are installed compliant with AS3500
checkpoint-status | 9b42e580-2543-45f9-bb1c-37fcbc6b2953 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 570aa84d-b73a-41c8-9787-76e402fec88d |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 727eee80-1afd-4aaa-bf3f-89ebe5f727bb |  | checkpoint | Check traps are correct locations & clear of debris
checkpoint-status | ab22ca06-7b3e-4b8d-955e-e0fd1e92cb2e |  | checkpoint | Check trap grates are at correct finished heights
checkpoint-status | cc6da2d7-c2b5-4393-8e37-b3a8c47488d6 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | ffcfb893-13cc-4481-a6d4-ff4e7e666bbd |  | checkpoint | Marking tape installed
checkpoint-status | 52537a18-9943-4630-8043-c82803b96526 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | f98b488f-9e26-4035-a01d-89151bc63f4f |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7261a2ac-228e-41ef-b8b5-ddc1118cca64 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | b63cd8e1-c17d-4646-aa34-6c22273e2ce8 |  | checklist | FO Wall Tundishes |  |  |  |  | Yes | FO Wall Tundishes | 5d79e369-c6ed-4035-86c6-b584c456a477
checkpoint-status | 0c4a5705-d7ef-42e2-9d13-b7f13cc04379 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 89f1f112-b341-4444-ac88-7247f67464c8 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 309b64d8-8c38-402e-8703-9d62ead0a431 |  | checkpoint | General finish & alignment both level & centre of tundish
checkpoint-status | 3bb70134-0eb4-46a5-bd02-b06e567e4d7f |  | checkpoint | Solid installation & mounting of tundish
checkpoint-status | 21585d77-e1e8-48ae-bf5a-d5c55816268d |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checklist-flat | 298a6c3d-5436-4b50-95e6-87034de06869 |  | checklist | HW Rough-in (High Level) |  |  |  |  | Yes | HW Rough-in (High Level) | 5eebadc7-7084-4f8a-87af-3fe395aac5df
checkpoint-status | d6249d97-e714-44f5-9e7b-9a7eff558384 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 1f177dd8-c7e7-4945-be36-f5d9eacbb613 |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 855e0bfb-607d-4930-99b7-b5439c24b6b5 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | a2cef182-6397-419f-8dee-51aa33b58d87 |  | checkpoint | Check silicone applied to studs
checkpoint-status | b8cb8694-6184-4c5d-bb47-aba1b99d7c5c |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | 308cf113-f1aa-4a50-be4e-77ff80f737e0 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 5691c747-2996-4091-acbd-8a219c651a05 |  | checkpoint | Check for possible cross connections
checkpoint-status | 7f655edb-2c0d-4d60-979b-b0e46ce7705b |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 2a036e99-cbc4-4492-b390-5bb4d7ca9729 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 2da43c4b-ae18-483d-b23c-16b83325c07f |  | checkpoint | Heat trace installed if required
checkpoint-status | 8b5dcc99-dfd3-42a7-ac09-6bac22ab512d |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 2e64e8c8-9378-47be-b35c-710e90e46ef5 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d81e844b-c63c-4971-a7b2-33c027842142 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | a6b32ae7-425a-4fdb-9c34-d738b1ce0272 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 3e8d6bc3-701d-4909-9056-3587f9f922ab |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | d15ce357-1c66-4b30-a1f2-f455a4362019 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | def1af9d-395e-47cf-888a-77d5a79adc6f |  | checklist | FO Dishwashers |  |  |  |  | Yes | FO Dishwashers | 644607bd-534f-42d5-b8c9-a00d8fd8d0b5
checkpoint-status | 8b0d876b-188d-4c7f-a5dd-a23ffb1123b7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 9f6d09de-183c-46ff-856a-7dc02e3ead61 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | d95ea681-8444-4d6a-9df6-ae9949ff8a92 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 4ea31663-cf27-4072-8451-4a145d69657e |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | d525a8d2-b700-4cde-bd84-9ca569d056ef |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | ea17893c-4b2b-46eb-a03d-36e919153c75 |  | checkpoint | Check pressure reduction valve if required
checkpoint-status | fa48fdbd-4125-4f31-8fe9-140ef079d0a8 |  | checkpoint | Check flexible CW connection for kinks or twisting
checkpoint-status | 2e511908-6faa-48ba-8973-12a7c6f54afa |  | checkpoint | Check flexible waste connections for kinks or twisting
checkpoint-status | 818331dc-ff52-4003-845d-2117f2d161b2 |  | checkpoint | Check dishwasher cycle
checkpoint-status | 2cac0c53-5dbb-4c4b-97cb-199e9ef7bafd |  | checkpoint | Check for evidence of leakage
checkpoint-status | 785d2cd4-87e5-4e83-a17d-43f2d79fb77f |  | checkpoint | Check flexible waste connection to trap is tight
checklist-flat |  |  | checklist | Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test) |  |  |  |  | Yes | (LATEST) Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test) | 6a1e1e91-5587-45e0-95ab-dc54bbe043f5
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for undertaking a hydrostatic test to 500kPa to accommodate pressure sensitive fittings
checkpoint-status |  |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status |  |  | checkpoint | Air purging valve point has been nominated
checkpoint-status |  |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status |  |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status |  |  | checkpoint | Test consisted of slowly increasing the pressure to 500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint-status |  |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | 2f11b6f3-3f1a-5ce4-849e-198db1cd2694 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | 7608ada5-6b63-4100-8dcc-2bd94bf04961 |  | checklist | TST Testing Thermostatic Mixing Valve (TMV) |  |  |  |  | Yes | TST Testing Thermostatic Mixing Valve (TMV) | 6b214445-af23-4274-b4ea-065236e670b6
checkpoint-status | 5b37c52b-0a40-4c7e-a483-5999c499b60f |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.4 (2018)
checkpoint-status | a5aa4118-ab8e-4768-9aa7-df3f5a22e85b |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status | d5e0ee52-3ff0-4f34-a9b5-f6492d03bb9f |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status | e32c6bd7-77a4-49dd-951f-8f921dd739da |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status | 84a37fd6-5d9c-4786-a362-a642ee0d2f8c |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 1af3f868-b3e2-4d28-8e8e-f5ad98d5231f |  | checkpoint | Test sticker in visible location
checkpoint-status | c15d4090-c83a-4c98-a23b-7031bab39a58 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | d9330416-555a-4de8-9d57-4d480b4067f0 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 7bc34e42-02c5-4bf4-864a-eccd9a4961b4 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 602924f9-b6ed-440c-934a-91337137d69b |  | checklist | HW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | HW Risers (Pumped or Mains Pressure Risers) | 6d3948fd-3723-474d-8f7d-9470b2ee034e
checkpoint-status | 0ab25228-abed-4b1f-ab40-b1b673659abc |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 9bea115d-600c-43fe-8eb3-742ca5927106 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ab2198b7-1ad3-4f4e-8703-4c43bcec7467 |  | checkpoint | Penetrations are installed
checkpoint-status | 61199243-d00c-4112-a80c-b7dd3a735813 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | d443c1a1-73a8-4514-8831-a26577288236 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 4c7c2317-90f0-43ba-a3c9-66bde2c29711 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 15515f46-ec98-4cb1-9ecf-0f87e8f35fe3 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 95aaf836-e6d5-4f06-9631-1d35714c8d0e |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | e06c42d2-0d8a-4a0c-86c2-ddc903f17f6a |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 0b6485dd-9f08-4832-95c3-89944b95f360 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | c7b9bf2c-cc70-4337-8802-9ead705b7882 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 320fa33c-af42-4c8b-b1ac-5c5f89a759fc |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 2f04bda6-f66b-40b3-8e33-fb2d1fb0bb5b |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | fb8f09d5-62b1-4199-aefe-f2a102992af9 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | f661dad1-43ae-4024-b581-6f4a27923dfa |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | ef1d7044-88d3-4dad-8ea5-b059f1d4a976 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 5841ebad-66ef-45fd-939d-61dec9677f8d |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 49b62134-f984-47c7-9328-c12cf3adaf19 |  | checkpoint | Heat trace installed if required
checkpoint-status | a1ca2685-a85b-4cb3-ab0f-28b988881396 |  | checkpoint | Thermal insulation installed & correct weight as designed
checkpoint-status | 2da5efed-b9c9-4815-9f77-578235a0522b |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9ab7176e-9e53-421a-afc3-425e7959385c |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 82cc12bf-96ee-4f58-9245-970400b16a18 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 536e0972-1e09-47d0-9501-993b0579f63f |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 304c881b-d2ec-4a29-93f8-22284147212f |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Rough In - RW Design Components |  |  |  |  | Yes | (LATEST) Rough In - RW Design Components | 6eca16cc-2787-4b40-b5da-89fbd8603480
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for specific design requirements for CW
checkpoint-status |  |  | checkpoint | CW backup to RW system has been roughed in
checkpoint-status |  |  | checkpoint | Check meter installed
checkpoint-status |  |  | checkpoint | Isolation valves installed
checkpoint-status |  |  | checkpoint | Future provision for connection to BMS
checkpoint-status |  |  | checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Wall Tundish |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Wall Tundish | 735402c0-b2bb-41d4-b1c1-e35892166ad3
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for fit off of laundry in wall tundish (this is not a commissioning ITP)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | Tundish has been installed aligned, level and secure
checkpoint-status |  |  | checkpoint | Trap connection is clear of debris
checkpoint-status |  |  | checkpoint | Fixture has been left covered and protected and the area is clean
checklist-flat |  |  | checklist | Plant & Equipment Install - Rainwater Filtration System |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Rainwater Filtration System | 7368512f-fbae-4cd3-83c1-f9f294b9c6b2
checkpoint-status |  |  | checkpoint | Rrainwater treatment system/filter has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all supply lines has been undertaken
checkpoint-status |  |  | checkpoint | Rainwater treatment/filter is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | If specified, provision for BMS connection
checklist-flat | 00800e05-f67d-4146-8011-3201bc6e6a5d |  | checklist | FO Flood Stop Valve |  |  |  |  | Yes | FO Flood Stop Valve | 7509bb4c-8eee-47b8-8413-2649f598d36b
checkpoint-status | 75bef93a-4aef-4ad7-b239-92b541ccef63 |  | checkpoint | Pipe-work installed & sized as per current documentation
checkpoint-status | 628c5639-9eaa-4119-88b4-051d216ad5c7 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | ffea3703-51bf-4828-8bd3-8089b4022a90 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 9ffcfa3e-4052-4b92-8d04-ebdb35ac82dc |  | checkpoint | Clipped & mounted securely
checkpoint-status | 57723551-1880-4192-9db5-306d29d88683 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 75d149c3-dcad-4290-a759-0dd1fa7a211b |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | 7b257c82-dcad-47c5-9f89-c9b6e42e268e |  | checkpoint | Batteries are installed correctly
checkpoint-status | 60bebb01-78b7-49d8-b4a0-e9f5a16e77ac |  | checkpoint | Control LED lights are all in the Green
checkpoint-status | a13f281f-a96a-4521-914a-caa6deed4053 |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checklist-flat |  |  | checklist | Comm/HO - TMV |  |  |  |  | Yes | (LATEST) Comm/HO - TMV | 760735d2-2664-489b-aeb0-3393f800da0f
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for commissioning TMV and temp testing each tap/mixer
text | a052901c-e61c-593e-a33c-bd063adb8cde |  | textbox | Hot water delivery time from cold to stable hot to be logged |  |  | secs
text | f1045bff-70f5-50b4-8057-2f87f63641bb |  | textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint-status |  |  | checkpoint | Test has been conducted to fully isolate CW supply to demonstrate HW is not delivered through TMV
checkpoint-status |  |  | checkpoint | System has been returned to working conditions
text | aa959dea-f85f-56fa-9fda-bb792d22ae05 |  | textbox | Temp and Time reading photos from each fitting must be taken at start & finish of test
checklist-flat |  |  | checklist | Plant & Equipment Install - Hot Water Plant |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Hot Water Plant | 765c5cb1-7bf5-43f8-8acb-2e8713dce1c2
checkpoint-status |  |  | checkpoint | Hot water plant has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all supply lines upto the hot water plant have been undertaken
checkpoint-status |  |  | checkpoint | All pumps have been installed
checkpoint-status |  |  | checkpoint | Hot water plant is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | Photos of installed hot water plant have been included
checklist-flat | 904f2be2-5959-4181-8636-4b5e8d5734d0 |  | checklist | MT Hot Water Meters |  |  |  |  | Yes | MT Hot Water Meters | 7fbdf2da-f292-4246-83a5-195bc504a247
checkpoint-status | b949901a-9165-49df-846a-ba05bf451e86 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c2358fa1-c83e-4c23-9225-347395791821 |  | checkpoint | Water Meter Details:
text | 03dffddc-6315-5771-99e7-14e12461fce2 |  | textbox | Meter No:
text | 36d6298d-9acf-5553-a167-0cbe179add4a |  | textbox | Meter Location:
text | 1e3d8c62-66db-5893-85e8-8d789a604d16 |  | textbox | Meter Size:
checkpoint-status | 3812f87e-a1ec-420e-8ada-eca40b61efad |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 79bf6613-027e-4923-b253-59339871512d |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 6b124238-dfb8-4c16-88f0-f3fe78101ff1 |  | checkpoint | Meter bracketed
checkpoint-status | 5314eb3c-2334-404b-8cea-6fdfcf45c9fb |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | a47a0584-c451-4665-8c95-0963755a374f |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 6986e591-9477-4930-bca7-c0e9d59c446a |  | checkpoint | Pulse rate value is correct
checkpoint-status | a7116d4d-8655-44fb-ac8b-64f5b6666e62 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 50f611f7-6b9e-4722-8a28-252dfaca7314 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 4014a84c-bebe-4ef5-99fb-f414eb30d161 |  | checkpoint | Flow direction is correct
checkpoint-status | 83d417ef-be8e-48b0-8051-c98730f14cdc |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | d61c252e-eab2-414a-af6e-174084c280b7 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c7836cad-8660-434c-bc95-c1799c5050c8 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 29bad66a-930a-4480-b2e1-77ae0050e3cb |  | checklist | AU Notification to Commence Works in Vicinity |  |  |  |  | Yes | AU Notification to Commence Works in Vicinity | 817d9713-ab21-4f96-af90-e2f1b2264f39
checkpoint-status | 3a2338b1-f4a9-413c-ba6c-4f9c54320e08 |  | checkpoint | Dial Before You Dig
checkpoint-status | 3ecbc806-6e54-4bcd-b18b-0c30efcaac5b |  | checkpoint | Council/Municipality
checkpoint-status | 3ed5914e-22eb-4993-b6b4-cd536631a845 |  | checkpoint | Storm Water Drainage
checkpoint-status | 67d19618-18c1-4826-b1f0-ff1a199cc36c |  | checkpoint | Sewer Drainage
checkpoint-status | 52086a10-5748-4100-aeb6-dace6cddd825 |  | checkpoint | Water Supply
checkpoint-status | 04dc7c3c-83b8-460f-8454-e61524acaf7a |  | checkpoint | Natural Gas Supply
checkpoint-status | 1ed27e9a-0e77-425c-ade2-3f770f92f293 |  | checkpoint | Communications & Data
checkpoint-status | 15f39f5a-257d-479e-bd54-5168565aa16d |  | checkpoint | Electrical Power
checkpoint-status | 19f163a7-bfcf-4962-8722-40d583a17502 |  | checkpoint | Metro Rail
checkpoint-status | b26d2139-a763-4547-b52b-a4c588eef5f4 |  | checkpoint | Metro Trams
checkpoint-status | fb4fbdcb-9240-4dd9-82fa-6264f1f23b82 |  | checkpoint | VIC Roads
checklist-flat | 9af6b9d3-d39c-4fa0-a639-bb4000f8c6cc |  | checklist | NG High Level/Corridors |  |  |  |  | Yes | NG High Level/Corridors | 82d12fd3-f0b2-45c9-a262-eb29b47f8464
checkpoint-status | 05399499-554f-4835-809e-9f3ce745d215 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 775a2f70-a3d9-427c-884c-fd440eedaca2 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 862f2275-510b-4f94-9870-1775083e5127 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | aaa4c0f4-6803-4559-bfeb-5512033a1366 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 7a727447-3230-49f7-ad28-ac7256587561 |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | f5ffeab5-eebe-490b-a6f4-727025559201 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | f91de869-2ffa-475e-89a6-599b60194899 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 73cbd02b-8a81-41a3-9a78-7cc77fe0d146 |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 8ccc52b5-f7d8-46c9-88ef-0806529f2a5c |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | 7d06afc3-7d78-4b2a-aab7-cd4b46e60518 |  | checkpoint | Meter assemblies correct & bracketed
checkpoint-status | 3bd29a4f-5fbb-4372-b6b1-6040b835d4a2 |  | checkpoint | PR valves are installed. Pressure rate & flow correct
checkpoint-status | 81289f3f-6dba-4a9c-9d45-78331f0f4e2d |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 1e596d8d-f5ee-4eb4-af14-00daefededf8 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 199449af-b42b-405e-ae92-dfa90f1cb1d1 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 82a6b89e-6a08-41ab-8d94-7622a3bcb247 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | c0c71c2c-74c3-4626-8288-2ed146259971 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 6587befd-91ca-4b0a-ac48-2407e6dea113 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c3ea197c-8bb7-4833-8529-e2865d8a9c17 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | a10d9803-7494-412d-800d-d7a8a8781e06 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-sectioned |  |  | checklist | Toolbox Meeting Checklist |  |  |  |  | Yes | Toolbox Meeting Checklist | 846da54e-8571-4f5b-a09b-97c444e7c580
checkpoint-group |  |  | section | Attendance
checkpoint-status |  |  | checkpoint | Attendance - list of attendees added below
checkpoint-status |  |  | checkpoint | Apologies - list of non-attendees added below
checkpoint-group |  |  | section | Minutes
checkpoint-status |  |  | checkpoint | Actions from last meeting
checkpoint-status |  |  | checkpoint | Administration
checkpoint-status |  |  | checkpoint | HR
label | 269f6fea-8e79-5950-99a3-8c4971c94584 |  | note | e.g - Site recognition, any HR issues?
checkpoint-status |  |  | checkpoint | Safety: (including hazards / near misses / controls / site specific)
label | 242ed23c-3da4-5af5-8675-c54da4b54efb |  | note | Discussed recent incidents
label | e7af3d9d-039f-595c-8044-e5986f2190c8 |  | note | HSE Monthly Reports
label | a5571467-47f4-58c9-a2b6-c57019b1195b |  | note | SDS – Of the week (list which SDS you have reviewed)
checkpoint-status |  |  | checkpoint | Environment: (including hazards / controls / incidents / impacts)
checkpoint-status |  |  | checkpoint | Training
label | d9dddba9-ca81-5a0c-8829-9087aeff249e |  | note | Competency Assessment Guides (Apprentices) if applicable – are they up to date?
checkpoint-status |  |  | checkpoint | Plant & Equipment
checkpoint-status |  |  | checkpoint | Issues & Customer Feedback
checkpoint-status |  |  | checkpoint | Client/Job specific information:
checkpoint-status |  |  | checkpoint | HSE Committee: (key points from minutes / questions / feedback to be raised at next meeting)
label | be786a12-1fd4-55bb-8c92-22a9d5173a50 |  | note | Discuss recent HSE Committee Minutes
checkpoint-status |  |  | checkpoint | Memo’s and other office correspondence
checkpoint-group |  |  | section | Document Review
checkpoint-status |  |  | checkpoint | Document uploaded below if applicable
checkpoint-group |  |  | section | New Business / Other
checkpoint-status |  |  | checkpoint | Any new business / other comments added below
checkpoint-group |  |  | section | Meeting Closure
checkpoint-status |  |  | checkpoint | Meeting Closed
text | ffec8ea0-8527-5f0a-b4ef-2343fd2a2f92 |  | textbox | Meeting Closed time
text | dacdadd8-b1b5-5dfa-8879-5a684bb615f2 |  | textbox | Date for next meeting
text | 5b0c939f-7fe6-5216-b691-241eafd40728 |  | textbox | Minutes taken by (Name)
checklist-flat | f2beab3f-9826-423d-8419-16b1dedb6532 |  | checklist | FO Gas Appliances |  |  |  |  | Yes | FO Gas Appliances | 860cf017-7028-4207-880c-333a63960678
checkpoint-status | 0b545e84-c894-40fc-a825-0e13cd5ff979 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 989b3b51-4c07-498e-b77f-5834992813a2 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 859937c4-60c0-45c3-af74-8621a8d21879 |  | checkpoint | General finish & alignment both level & centre of cook top
checkpoint-status | 73e7bdbb-a33b-461f-9042-96abcb21d93b |  | checkpoint | Ensure wall & surrounding joinery material is fire rated & compliant with AS-5601
checkpoint-status | fcc21e33-34c0-4d85-ae0a-ce9bb365f688 |  | checkpoint | Solid installation & mounting of cook top
checkpoint-status | 224e1c05-b1c1-4e8b-856a-d59df78b8af5 |  | checkpoint | Check in cupboard for signs of gas leakage
checkpoint-status | 7c440baa-cecf-46db-bcce-82038cc312fb |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | 85a276d6-a571-4907-94f2-ad4174c3c6c3 |  | checkpoint | Check cover plates are installed
checkpoint-status | 9a0e8b42-6543-423f-a160-591ecc856236 |  | checkpoint | Check gas valve for operation & leaks
checkpoint-status | 6bddb163-ab61-4b9d-96f0-4fc7be099855 |  | checkpoint | Check gas regulator for operation & leaks
checkpoint-status | c433cca9-fa44-4ec5-8363-a99868e7f482 |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status | f01edac7-fdc5-44d8-955d-35d458c9504c |  | checkpoint | Test operation of all burners from low to full to off
checkpoint-status | 9884ecdc-6fdb-4f3b-bd8c-1724e46e283b |  | checkpoint | Test flame for complete combustion
checkpoint-status | a26d7b63-9fbb-4978-a93f-db5ee0931982 |  | checkpoint | Range hood height is compliant with manufacturer recommendation
checkpoint-status | 63e8acb2-6dd5-468e-9cb0-8495438becf7 |  | checkpoint | Test sticker to be adhered to pipe inside cabinet in a visible position
checkpoint-status | dca5bdb2-4884-4cc6-9eaf-212469ca7c35 |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | Rough In: Commercial (High & Low Level Rough In) Water Services |  |  |  |  | Yes | (LATEST) Rough In: Commercial (High & Low Level Rough In) Water Services | 86c49294-7a57-4e91-bdf7-d53a270e87c3
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for rough in of high level and low level water services to specific areas (tea point/bathrooms/EOT etc)
checkpoint-status |  |  | checkpoint | Pressure Pipework (for high & low level rough-in) checked off as below
checkpoint-no-status |  |  | checkpoint | Install Phase
checkpoint-status |  |  | checkpoint | If pex is being insulated with armaflex, a barrier of duct tape has been applied to all pex crimp fittings
checkpoint-status |  |  | checkpoint | All joints have been crimped correctly and to manufacturers spec
checkpoint-status |  |  | checkpoint | Spacing of clips and fixings for WaterPex as per AS3500.1.2021
checkpoint-status |  |  | checkpoint | Any pex through metal studs is entirely protected from sharp edges (achieve through additional oversized sleeving or suitable grommets)
checkpoint-status |  |  | checkpoint | Check has been undertaken to ensure no cross connections
checkpoint-status |  |  | checkpoint | All pex fittings are crimped and ready for 1500 kPa bump test
checkpoint-no-status |  |  | checkpoint | Rough In Fitting Install
checkpoint-status |  |  | checkpoint | Installation and location of tempering valve or T.M.V is correct (must be within access panel area)
checkpoint-status |  |  | checkpoint | Location of shower mixer is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of lugged elbow is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of WC water point is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of vanity water points are as per latest IFC
checklist-flat |  |  | checklist | Ingrounds - Authority connection to meter room |  |  |  |  | Yes | (LATEST) Ingrounds - Authority connection to meter room | 86d694c6-71d2-433e-b0f8-37da150e9675
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - Authority connection to meter room
checkpoint-status |  |  | checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | Installation meets water authority requirements
checkpoint-status |  |  | checkpoint | All pipe elements free of damage prior to install
checkpoint-status |  |  | checkpoint | Pipework is connected to water meter assemblies
checkpoint-status |  |  | checkpoint | Pipes have been wrapped in plastic (or denso wrap)
checkpoint-status |  |  | checkpoint | Pipe bedding is correct
checkpoint-status |  |  | checkpoint | Pipes are labelled
checkpoint-status |  |  | checkpoint | Any open ends have been sealed
checkpoint-status |  |  | checkpoint | All mechanical joints are correct and have been checked
checkpoint-status |  |  | checkpoint | Access riser from sluice valves to surface level installed
checklist-flat | 04cb4105-4a38-4c9b-ae0d-27b5cfa7229a |  | checklist | PE SW Downpipe/Syphonic Diversion Valve |  |  |  |  | Yes | PE SW Downpipe/Syphonic Diversion Valve | 88d3d32e-35a2-49e7-b524-c6ec662d3142
checkpoint-status | 8afdfdf0-4f78-4b85-ad25-dfd641dd86ff |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | e87ea839-15da-48b4-a028-59f324802726 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 4bfb7185-6fd2-43f7-a9c9-8a52298d767e |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | b366df14-be46-45c2-b2d8-d3e83559a0e6 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 4a47d353-0411-499a-8f7d-50e194ce01e8 |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | a8452c84-08b5-46b0-95b2-10a0327e6f0a |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | f43b2941-ab26-4160-8ff4-fd69c90a0acc |  | checkpoint | Inlet pipework is installed & connected as per design
checkpoint-status | d6255960-b54c-4c75-8b2b-465e36e21a90 |  | checkpoint | Outlet pipework is installed & connected as per design
checkpoint-status | 88645359-e678-4258-9816-524c98cb5c5b |  | checkpoint | Diversion pipework is installed & connected as per design
checkpoint-status | f5ad01e6-8e0f-4ed8-ad1c-9b19080ebcca |  | checkpoint | Connection flanges fixed to manufacturer specification
checkpoint-status | 7f189098-fee6-45d1-b1c1-493d8f515b5e |  | checkpoint | Ensure data wiring is connected between control panels & operating to the manufacturers specification
checkpoint-status | 75715d57-7368-4489-b08f-fdf79a8d4f0f |  | checkpoint | Ensure electrical connection have been completed & certified by a licenced electrician
checkpoint-status | cd2586ec-ebc7-43e1-aa3f-82656abd9835 |  | checkpoint | Ensure the pnuematic pump is installed & operates to the manufacturers specification
checkpoint-status | 46396244-dfe8-42fd-b26a-e34063377124 |  | checkpoint | Provider to check the valve actuates correctly & test cycles the valve several times
checkpoint-status | bf2b96fd-c491-4a2d-9edb-d8945f52321d |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | c3daff71-0074-4b6b-b7e3-a007c36af750 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Drains: Underslung - Sewer, Stormwater & Vent |  |  |  |  | Yes | (LATEST) Drains: Underslung - Sewer, Stormwater & Vent | 8cf50953-16c9-44ce-b071-d35d28c86ed6
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for underslung/suspended drains (sewer, stormwater and vents)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Penos above have been checked, opened and debris cleared
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status |  |  | checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & traps are clear of debris
checkpoint-status |  |  | checkpoint | Required fall/grade meets AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | ca1f9f2e-d469-4ed7-ab8c-1aa03bfdbb12 |  | checklist | SW Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SW Downpipes/Overflows (Grated Outlets) | 8cf98079-5c89-4fa7-87b2-6762594a1242
checkpoint-status | 139632d0-9941-44df-a0e9-f4750cf748e3 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | efc2a072-57cf-4cfc-a664-c68369476fe0 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 8b7e6002-a799-45b0-b172-08195d2ba67a |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | 6d29b237-9377-46d8-8293-f12bc1ed9d5d |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 02c59c4c-1149-4a27-a249-020b0b2749c7 |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | bf1acc4a-dd50-4b8a-8d26-2a21ea631c33 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | 6355ad2b-1170-4cfc-b6cd-f9bb716737d5 |  | checkpoint | Downpipes are installed
checkpoint-status | 5ae1413b-7b35-4a35-819b-b00644106981 |  | checkpoint | Overflows are installed
checkpoint-status | 53103665-aff1-4134-9e6a-c542c9d595c1 |  | checkpoint | Penetrations are installed
checkpoint-status | 0d9e8db1-aa53-4b71-9f8e-e0e27ae916cd |  | checkpoint | Drain penetrations are caulked
checkpoint-status | b6c7516e-0d9e-4aaa-97a4-21ca7bf811bf |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 10542f97-c53d-456e-9d91-7f462d6bfab4 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 00f719c7-d7d0-4362-8c4e-265c8069dd99 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | f9d4da3c-28b3-4029-9f85-68b979a97d51 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 65f1c80a-2eda-4739-a266-f9b472e112d1 |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status | 5ada9ab1-358a-4977-a962-1685c9add4f6 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | FINAL Commissioning - Sewer Pumpwell/s |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Sewer Pumpwell/s | 8eeae03e-d9c6-4f89-bb60-5b6af0095434
checkpoint-status |  |  | checkpoint | Sewer pumpwell/s commissioning report/s to be uploaded here
checkpoint-status |  |  | checkpoint | Sewer pumpwell final install photos to be uploaded here (show connection to active board)
checklist-flat |  |  | checklist | Comm/HO - Tempering Valve |  |  |  |  | Yes | (LATEST) Comm/HO - Tempering Valve | 9067dccb-0fec-4169-8cca-d5c696c91d2e
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for commissioning Tempering valve and temp testing each tap/mixer
text | a62ebe8b-1891-5d21-982a-3de35e357bbe |  | textbox | Hot water delivery time from cold to stable hot to be logged |  |  | secs
text | fca77884-981b-5abe-84f7-d836a6471604 |  | textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint-status |  |  | checkpoint | System has been returned to working conditions
text | cf27168e-0f44-51c0-9fa7-214238d89edc |  | textbox | Temp and Time reading photos from each fitting must be taken at start & finish of test
checklist-flat | 9b72104e-0a8e-4f22-bdcd-8e6de671e75b |  | checklist | FO Showers |  |  |  |  | Yes | FO Showers | 908c2c6c-910d-4871-8d62-2b5d61aa8549
checkpoint-status | a39513ee-167a-4d59-86dc-304fd88e3fae |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d4910cae-7e92-492c-9e8b-14790c235933 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 05ec5230-667f-486b-98d3-c0c1e4d26e70 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 570dd1b0-bf54-4c35-b750-c45f52539c78 |  | checkpoint | Solid installation of wall mounting plates, levers, wall rails & sprays
checkpoint-status | eb44ee61-139c-4b88-abcf-52fe12290939 |  | checkpoint | Check floor grate or channel for flush fit & alignment
checkpoint-status | 1df1e37c-2ba7-49a0-8518-5ded83004b94 |  | checkpoint | Check for flexible hose leakage
checkpoint-status | ce7e65c3-b8a1-4aee-a398-814986322aaf |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 9901ad1f-42ff-41a7-b491-23113eb923b2 |  | checkpoint | Check inside floor waste for signs of debris etc
checkpoint-status | 6b3b1987-9243-45ac-af41-c6602c9edd49 |  | checkpoint | Operate mixer & discharge to floor waste
checklist-flat | 43822bf8-0e0b-4fa7-b6d3-3faccbd13ae0 |  | checklist | FO Thermostatic Mixing Valve (TMV's) |  |  |  |  | Yes | FO Thermostatic Mixing Valve (TMV's) | 9259be96-55b7-4c87-8280-229b0f4196fc
checkpoint-status | 2302f8e5-1534-4287-b432-d9bc7b4c92a9 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 1553a07a-6370-4a4e-86e2-841593b7c72b |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 416ecf6f-f9b1-4eff-8402-90874342fb3d |  | checkpoint | General finish & alignment both level & centre of tapware
checkpoint-status | d51f505a-eb77-49c3-bc83-675b7cdf66d6 |  | checkpoint | Solid installation & mounting of tapware
checkpoint-status | e99bf9cd-e9e6-4840-ae88-998645244aec |  | checkpoint | Check cover plates are installed
checkpoint-status | b97b8fe5-4fc8-46ff-af9d-f9671520990f |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | dbd69e55-27c3-4bb6-906b-558efca9dc85 |  | checkpoint | Valve tag or signage is installed if required.
checkpoint-status | 9061ad88-8c77-4f7c-b828-932bfd1e5653 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | c35c9a6c-8803-4675-8c5e-6136afec56d4 |  | checkpoint | Temperature test warm water to ≤ 43°C
checkpoint-status | 5b699cec-cf49-435b-b301-9419df02c979 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c6ed048d-a5a0-4725-aeff-8fd7d1b31493 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 5a75e9f8-b58f-447c-b91b-3dfe0e55cd70 |  | checkpoint | Test sticker to be adhered to pipe inside wall box or in a visible position
checkpoint-status | 117e5a3a-efe8-4aad-b03f-bea0bd852920 |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | Drains: Stack Riser - Sewer, Stormwater & Vent |  |  |  |  | Yes | (LATEST) Drains: Stack Riser - Sewer, Stormwater & Vent | 926df064-289b-4933-937a-c192a3dd4fdb
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for stack risers servicing sewer, stormwater & vents
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint-status |  |  | checkpoint | Peno has been caulked (top and underside of slab)
checkpoint-status |  |  | checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint-status |  |  | checkpoint | Pipes & junctions are clear of debris
checkpoint-status |  |  | checkpoint | Inspection opening caps have been tightened and duct tape applied
checkpoint-status |  |  | checkpoint | For sewer: Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Pipes requiring lagging have been temporarily labelled
checklist-flat | 6cebf7f5-4f1f-44b6-9d1e-92c745a96446 |  | checklist | TST Testing Roof Downpipes (Air Test) |  |  |  |  | Yes | TST Testing Roof Downpipes (Air Test) | 95bc8d7a-020a-4a09-aaae-99fb2ae0069b
checkpoint-status | 4407e1be-c60f-4d9b-ab01-7765bf0871e0 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.3 (2018)
checkpoint-status | 7c3d8e8e-f367-4bb9-a3c1-c79bb3dc086f |  | checkpoint | Ensure bore is completely free of any blockages, constrictions or debris
checkpoint-status | 94dcc042-a003-4e87-96c9-26e81a9ac7a1 |  | checkpoint | Ensure pipe-work is securely fixed to eliminate movement during pressure test
checkpoint-status | 04cc8620-9750-4295-9c85-fb8d1a07b45a |  | checkpoint | Temporarily plug & seal open ends of pipe-work section to be tested
checkpoint-status | f1dadf99-e09f-481d-b663-9015e5853af5 |  | checkpoint | Provide a temporary valved test point with union fitting
checkpoint-status | 68424959-63da-42f6-a680-3c23665cca19 |  | checkpoint | Connect pressure testing device to temporary valve point
checkpoint-status | acb671be-11b4-4288-b96f-33c410b930ef |  | checkpoint | Commence choke point testing by slowly increasing pressure up to 30 kPa
checkpoint-status | 7a2c54ea-3515-405c-af2b-66e8bdf4a7ea |  | checkpoint | Hold test at 30 kPa for 3 minutes
checkpoint-status | d977f713-c1ee-44b1-a0b2-8842e98d101e |  | checkpoint | Testing is deemed successful if no pressure drop is recorded up to 3 minutes
checkpoint-status | faaa8b52-cd02-4659-9911-369d6a4e2bbe |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | 5a5d6bfc-96a6-46fe-8e55-54b5eb2caa64 |  | checkpoint | Test sticker on pipe 1500mm high facing a corridor or accessible wall
checkpoint-status | 1b899ced-cd69-4522-bbb6-ebed2dccae62 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 29cf61cf-9150-4652-8aa4-ef970f1756da |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | ed5b8522-b3a1-433b-b59f-b2e41d91d227 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | b3091020-c148-4cb0-b716-f9bdef1e6ebf |  | checklist | SW Stormwater Drainage (In-Ground) |  |  |  |  | Yes | SW Stormwater Drainage (In-Ground) | 9c001e6d-8ce2-4335-8de2-01a66e88f36f
checkpoint-status | b8365a0f-4937-496e-92ef-f63fc1e63d03 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 513944d8-ecb7-4247-9092-74daf11497f0 |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | a6b17e5c-b740-4849-9bc8-462acc5070e9 |  | checkpoint | Authority applications for stormwater drainage & start work notices accepted
checkpoint-status | afcb4eab-1390-4892-b00b-a8427df972ff |  | checkpoint | Municipality connections installed by Richstone
checkpoint-status | 85040453-cc71-4851-bf85-73038730525c |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 8529ac57-8a5e-4ee0-99ed-ba3098c80178 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 069df380-c34b-4f27-abfc-e851043ad2a7 |  | checkpoint | Ensure all grades are correct
checkpoint-status | 80e6f829-4fee-4e51-9a48-22568e9e2b35 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | d1e94e9f-3397-4d0e-8bd9-0302f585e88a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 962d3107-fd6a-45c9-8c4b-92bda242b7f6 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 571bfdfa-9dee-4e4c-a502-390b4c76845b |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | f5f0a31f-4c35-49e7-bb71-ee8a121cbed9 |  | checkpoint | Spoil is removed
checkpoint-status | 5906c341-517d-4e37-ba24-4e62281d78cc |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 5e77ea1c-419b-4b56-8646-5b573154c8bf |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | dcc2401a-e48e-4eda-a630-4339d2b690c8 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | dfc3a690-9479-4c61-848b-7418aec73a86 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | 7fdb2f9d-c092-4cae-adcb-7a9e7f2d132e |  | checkpoint | Marker tape installed
checkpoint-status | 1c3896ca-1f42-474e-a63f-6ddbb45f02e0 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 62142e56-22e4-4d12-ad2f-4d5f038784ba |  | checkpoint | Stormwater junxtion & grated pits are installed in sizes & locations as per design
checkpoint-status | 88012b0c-991e-4aa4-b607-2e7f4141f805 |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 7c5488e3-bcf3-4cd7-869d-839164b7aa94 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 28528542-a917-4756-b4f1-01e8c64164a5 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | a6a8492c-1ed2-4d88-9028-712f161d8544 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e5559603-6ad3-4805-835c-9633804f709c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | 4498cf2c-1445-4bae-a2fa-c74d51e30bbd |  | checklist | TST Testing Reduced Pressure Zone Device (RPZD) |  |  |  |  | Yes | TST Testing Reduced Pressure Zone Device (RPZD) | 9fd0804b-389f-4709-8368-beccdd86bba0
checkpoint-status | d75c0c00-8c56-4696-b5d5-4c1403aea5a1 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018)
checkpoint-status | 630ca4ab-3ef1-425b-a226-286f5e34163a |  | checkpoint | The tester is qualified & trained to carry out the testing procedure required
checkpoint-status | afb54007-3de1-474e-bbb8-c1d12ab9ea99 |  | checkpoint | Engage a certified/licenced specialized sub-contractor to perform & document this test
checkpoint-status | 5d6fb3e1-38e2-4b01-b0fd-e5907e2659db |  | checkpoint | Request & receive a signed certificate of successful test result
checkpoint-status | 625fe90d-2d1f-4d2c-9ada-fd66c85fa946 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 6a97b7ce-ea55-478d-b8a1-0416092242dc |  | checkpoint | Test sticker in visible location
checkpoint-status | 804274e4-8e0b-4767-aaa7-54332477689c |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 28e92426-7cef-42a2-874d-22d9423d3d85 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 520a88b5-24bb-4dcd-bce9-832392886676 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | Plant & Equipment Install - Stormwater Pumpwell/s |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Stormwater Pumpwell/s | a05429d0-29eb-4cae-bc40-06a76791efbc
checkpoint-status |  |  | checkpoint | Stormwater pumpwell/s has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all pumplines has been undertaken
checkpoint-status |  |  | checkpoint | Pumpwell lid has been lifted and all formwork has been stripped
checkpoint-status |  |  | checkpoint | Rails and lifting chains are in place
checkpoint-status |  |  | checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint-status |  |  | checkpoint | Stormwater pumpwell is ready for commissioning by supplier/manufacturer
checkpoint-status |  |  | checkpoint | Pumpwell lid has been resecured and lid fixings resecured
checklist-flat |  |  | checklist | Testing - Potable Water - 1500kpa water test (not an air test) |  |  |  |  | Yes | (LATEST) Testing - Potable Water - 1500kpa water test (not an air test) | a1d2ec8b-1ef2-4339-945c-6d2b0ad26b0f
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for undertaking a hydrostatic test at 1500kPa
checkpoint-status |  |  | checkpoint | Water test is being conducted on material that is rated to withstand 1500kpa
checkpoint-status |  |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status |  |  | checkpoint | Air purging valve point has been nominated
checkpoint-status |  |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint-status |  |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status |  |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status |  |  | checkpoint | Test consisted of slowly increasing the pressure to 1500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint-status |  |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | 7d8a63ef-ac29-5f2c-a7d3-775be0fa8b0d |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat |  |  | checklist | Testing - Natural Gas |  |  |  |  | Yes | (LATEST) Testing - Natural Gas | a1e7e803-4a28-49c5-b8d7-c7da30754555
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for air test on fittings to meet manufacturer's guidelines
checkpoint-status |  |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status |  |  | checkpoint | Air purging valve point has been nominated
checkpoint-status |  |  | checkpoint | Pressure testing valve point has been nominated
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | All terminal open ends are securely capped off
checkpoint-status |  |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with air until completely purged
checkpoint-status |  |  | checkpoint | Pressure testing device was connected to the nominated test point
checkpoint-status |  |  | checkpoint | Pressure testing device is calibrated
checkpoint-status |  |  | checkpoint | Test must be undertaken to pressure of 7kPa OR 1.5 times the operating/working pressure whichever is greater (eg 3.5 kPa working pressure = 8.75 kPa testing pressure)
checkpoint-status |  |  | checkpoint | Testing was deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status |  |  | checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
text | b9ab95c3-63f1-574b-b79e-678e5cab23a8 |  | textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist-flat | ff956960-6e27-4227-bede-84ff8f18e39a |  | checklist | SD Stacks & Vents (Main Droppers) |  |  |  |  | Yes | SD Stacks & Vents (Main Droppers) | a2cd0e89-6009-4709-b978-254cb494faba
checkpoint-status | 7941410a-3c37-4764-8295-d8685904a9f2 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 0bf5d5e7-4b3e-4eda-8100-643cbcf9bcdc |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 9e9b0deb-af77-464e-86d9-bc39fa1f910b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 5df94118-fae5-47ee-bd5d-c2c65a6b41e1 |  | checkpoint | Sewer stacks are installed
checkpoint-status | 92bba95d-01a0-45d4-8194-2ea195b058e3 |  | checkpoint | Sewer vents are installed
checkpoint-status | 622c82f7-357a-4f21-a34e-6ffb1921cc46 |  | checkpoint | Cross vents are correct
checkpoint-status | 4efc1fba-9185-4a2d-a3bb-0c550507e0f3 |  | checkpoint | PAPA vents are installed (if applicable)
checkpoint-status | 0f313ecd-8542-424a-ac23-cee999c8286c |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 6c84ede1-4f9d-4252-bbf4-d81d02aed08d |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 44f3e762-d837-4bf9-b270-ef24d1984559 |  | checkpoint | Stack base I.O. is installed
checkpoint-status | 93ce5784-3d0f-42cd-82cc-67b73949735b |  | checkpoint | Stack bases supported correctly
checkpoint-status | 7b48acd5-5db6-4aec-b32a-be93332ef6d3 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 00148390-f71a-430c-b742-00bc50dc50b8 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 3d34168e-1faa-4944-83c3-b117c0289590 |  | checkpoint | Penetrations are installed
checkpoint-status | 17ae0545-37af-4c59-82cf-c6fc8ce70253 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | fd0c08d2-355d-43d5-bec6-e861f0979851 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 28d96a95-4ce8-4482-b49e-bc1064f61bcf |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 99a8002d-b7a9-4bc5-add3-9af9c82181cf |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | aa4a3e98-871d-4e2b-a5bd-10ffe8c21ecf |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 46a1fbc1-c953-4cf2-813b-e584503bc895 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | ec391417-091d-4965-a4cc-fb7634823e30 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | f40a5919-ae91-4829-ba93-a296e3bde413 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 9cd22b2c-7405-4c07-90a2-f8dd4ddccf57 |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 7022f71b-cd1e-41e5-a479-3073cd245874 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 6e14e3bc-2ee5-45e4-a372-3ca6bd980f21 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 7a119e10-93ae-49f1-a3a6-beaf6be2f7a4 |  | checklist | PE Above-Ground Rain Water Storage Tank |  |  |  |  | Yes | PE Above-Ground Rain Water Storage Tank | a6785ef9-8b47-42a1-a5ec-403671fff966
checkpoint-status | 2247d7ac-66bc-4b52-9314-63af84522c72 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 259d64be-1563-4b73-bf82-f1b207bd437d |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 1d3d6a44-6044-4eb4-b592-464fed8ce987 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | e62a7278-0322-48af-b7f3-99a8f04141f4 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 2e42a238-cef1-4212-89b2-130332151b68 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | bca5bfba-7453-4490-90b0-d51ced0bbad8 |  | checkpoint | Vents are installed if required
checkpoint-status | b47c024d-da8a-4c95-8a78-e224b379f8df |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 6baf48f2-19bf-441f-bb18-0069a16803cd |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | e220d33e-1833-4d63-9725-0a2e2c2ed0bf |  | checkpoint | Overflow drain is installed to discharge over stormwater pit
checkpoint-status | af9bf4b3-3925-4d2d-96c3-651b68cdd69b |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status | bacb02bc-497e-412e-828f-cdb76b81c6b1 |  | checkpoint | Suction line installed & connected
checkpoint-status | c90f4f5c-78ef-4c92-8064-40e317da820c |  | checkpoint | Isolation valves are installed (if required)
checkpoint-status | c81aecd7-bf9c-4d82-8fcd-c30002f4c7f5 |  | checkpoint | Electrical cable is installed
checkpoint-status | 02e776b2-f024-4f3b-a473-6504fefedc2d |  | checkpoint | Control panel is installed
checkpoint-status | 4417ea46-4e3d-4ed4-bdc0-d383ace5e678 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 8a0c6a07-2ca9-415e-b58c-052dfe98d0ef |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | b3ce1d75-0ed5-4e24-9603-8d61a8c71e3d |  | checkpoint | Tank provider installation certification obtained
checkpoint-status | 28037e31-0493-408c-9b1f-83a0541a3136 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | b7069851-e9e1-4659-bf08-cfe3b3c4502c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | c8b92ed3-193f-4219-ba2d-97014d5ba950 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | f6aada93-a150-4f5c-ab8d-37238c410612 |  | checklist | NG Risers |  |  |  |  | Yes | NG Risers | a708366d-6a58-4e2a-9c0d-c5859e48b7a0
checkpoint-status | 8e9cf19d-3740-4095-a809-783dc51a8be2 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | e9c1e589-1c5d-49a0-9916-ee9bb05e543e |  | checkpoint | Authority applications are completed for work to commence
checkpoint-status | 93d770e3-4381-45ce-8c94-36471fbdad00 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 13f0de7e-a714-4248-a272-06c59132bb13 |  | checkpoint | Penetrations are installed
checkpoint-status | 855635fa-749b-4adc-bce5-17f11163378e |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 1b0cc16a-c502-48b6-a9a5-373d67491e9f |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | ae814549-49ab-4b30-979b-65b71808d99c |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 447b343f-b68e-472b-8cc6-27c33a9e6a76 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 239a3936-5597-4d4f-99ad-911406792375 |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | 8f48c33a-97c1-451a-a2a6-e911b9431d93 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | 10645813-4546-4205-8b2b-52cafad75b7f |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | 0fb3474b-44d8-4f1b-84e8-4936b77aa47b |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | d3202c05-1c80-41ad-ae4a-4b8fc6ff9274 |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | 53aa107c-c5ef-4100-b046-fb5382f072cc |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 5a38ccc5-7870-4cd9-ae3d-1fc67b315212 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | dc646945-1082-49cc-8c21-69c4e2c2bd56 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 5e0aab60-8b5f-4b08-a38f-c11ce3073959 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 7c9abfc3-2a48-48bc-8011-697106de547b |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | 228e1146-732c-4775-824b-658b50f43e82 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 68f6cabf-7219-427e-bfcd-1c64403a25ba |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | 4754abc0-409a-4710-a2ad-9c9313dc1eec |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 8281face-b55b-4a14-9be6-2d93df7719cf |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 8a6cfdb8-aa9b-4f96-b538-2609b0fa2715 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | b208642e-dda9-41be-b93b-fee0637e06f7 |  | checklist | FO Drinking Fountain |  |  |  |  | Yes | FO Drinking Fountain | a9659aea-e8b9-4fbe-951f-d96265d505bb
checkpoint-status | 53b29557-010a-4a22-955e-9d844d67e530 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 445ca55b-d94c-4c5d-a5a6-11f237652248 |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status | 28f1d815-f73e-43c3-b993-80fed1b94571 |  | checkpoint | Solid installation & mounting of cabinet, sink bowl & mixer
checkpoint-status | 2183d46f-f356-4738-bf75-ca94afc78077 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | e4e9fdde-962c-4f23-9cf4-cce5e0c7846f |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 32e34e67-9732-4aac-82d9-b1ac92c6b7d4 |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | e044d4d6-d4c0-4e57-99f9-175ff444b31f |  | checkpoint | Check pressure reduction valve if required.
checkpoint-status | 4b8958d9-b76d-4011-99ed-220c01f6be42 |  | checkpoint | Check flexible connections for leaks, kinks or twisting
checkpoint-status | 14a54af2-7448-4ab4-8736-75ae0cd892bb |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | 85dc06d6-e7da-4ac5-9d8a-2e42724eb186 |  | checkpoint | Adjust & throttle water flow-rate if necessary
checkpoint-status | a3f998b8-6ba0-4c90-9d2d-493808f08c55 |  | checkpoint | Check trap & waste pipe connection for signs of leakage
checkpoint-status | 23f4e928-1a16-4509-bfa2-abdf33f79fa6 |  | checkpoint | Check inside bowl trap for signs of debris etc
checklist-flat |  |  | checklist | Rough In: Apartment Water Services (High & Low Level Rough In) |  |  |  |  | Yes | (LATEST) Rough In: Apartment Water Services (High & Low Level Rough In) | aa4b0e99-65cb-4d2c-9f8c-adb431c24556
checkpoint-status |  |  | checkpoint | Pressure Pipework (for high & low level rough-in) checked off as below
checkpoint-no-status |  |  | checkpoint | Install Phase
checkpoint-status |  |  | checkpoint | If WaterPex is being insulated with armaflex, a barrier of duct tape has been applied to all pex crimp fittings
checkpoint-status |  |  | checkpoint | All joints have been crimped correctly and to manufacturers spec
checkpoint-status |  |  | checkpoint | Leak detection indicator has broken away and 3 crimp lines are visible on the crimped fitting
checkpoint-status |  |  | checkpoint | Spacing of clips and fixings for WaterPex as per AS3500.1.2021
checkpoint-status |  |  | checkpoint | Any WaterPex through metal studs is entirely protected from sharp edges (achieve through additional oversized sleeving or suitable grommets)
checkpoint-status |  |  | checkpoint | Check has been undertaken to ensure no cross connections
checkpoint-status |  |  | checkpoint | All pex fittings are crimped and ready for 1500 kPa bump test
checkpoint-no-status |  |  | checkpoint | Rough In Fitting Install
checkpoint-status |  |  | checkpoint | Installation and location of tempering valve or T.M.V is correct (must be within access panel area)
checkpoint-status |  |  | checkpoint | Location of shower mixer is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of lugged elbow is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of WC water point is as per latest IFC
checkpoint-status |  |  | checkpoint | Location of vanity water points are as per latest IFC
checkpoint-status |  |  | checkpoint | Location of kitchen water points are as per latest IFC
checkpoint-status |  |  | checkpoint | Location of laundry water points are as per latest IFC
checklist-flat | 852a84e3-b161-47bd-a95f-824fa20869e7 |  | checklist | MT Re-Cycled Water Meters |  |  |  |  | Yes | MT Re-Cycled Water Meters | acf1666e-2b56-42ee-9285-49e5fa409ec8
checkpoint-status | e3244d10-d284-4810-97aa-95df138651e7 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 2376ed94-c9d3-462d-a5e2-0a0d7f764355 |  | checkpoint | Water Meter Details:
text | 0b3b7f8b-4d64-5d05-938c-418b59d75565 |  | textbox | Meter No:
text | 07a2bc3e-35b6-5ecb-abb9-0bfa36f43e13 |  | textbox | Meter Location:
text | db04ee19-5823-560d-8e77-1f5e10647140 |  | textbox | Meter Size:
checkpoint-status | bd83844f-7135-40d2-9938-8e50e65a6a31 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | 15017363-0efb-466d-96cd-075e089cec2f |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 3e41572b-b13c-4fea-aa00-55bc1d8c7260 |  | checkpoint | Meter bracketed
checkpoint-status | a5182713-f909-4441-ab51-64b29e9de8d2 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | 113a4131-fc93-4da3-a9fd-351c2158e541 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | f94c06b3-72dd-47c7-acbf-c91ace7e36c7 |  | checkpoint | Pulse rate value is correct
checkpoint-status | ae3a0afd-e69d-47b8-adc8-9276bda4e3e5 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 848aeadd-3e37-413e-859d-e8084240bcf9 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 990dc4e9-b95c-43e0-b6b1-5b71f3884cff |  | checkpoint | Flow direction is correct
checkpoint-status | f6021ffa-a1ed-4234-929f-6e2b8421d80b |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 70fe2cfa-3b6f-484e-97e0-42b25b33fe36 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 4f7e7d4b-8fa4-4250-a421-e268c34aecb3 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | e33df46f-2ba7-42c4-a844-d5ba772856e9 |  | checklist | FC Floor/Wall Penetrations |  |  |  |  | Yes | FC Floor/Wall Penetrations | afed1aaf-0bfc-45a4-82c7-09ffe7599260
checkpoint-status | 6e542ab9-2de5-42ca-b1fd-b76dfabaa949 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 58991598-97c2-4a44-9b40-b758eb11ae7a |  | checkpoint | Confirm all penetrations locations are as per current IFC documentation
checkpoint-status | faea985c-0a8c-4e61-9e4b-89276d2a89af |  | checkpoint | Check both alignment & height are correct
checkpoint-status | 02adecd7-eb1b-4f81-ad41-9b510ecd196c |  | checkpoint | General visual check for damage, etc
checkpoint-status | 1349e7f0-cb3c-4b47-801b-9a82dfd37f69 |  | checkpoint | Check (floor) fire collars are rated & sized as per current IFC documentation
checkpoint-status | 54a75285-8937-4813-8752-aa5e51dbf295 |  | checkpoint | Check (wall) fire collars are rated & sized as per current IFC documentation
checkpoint-status | 298add3d-7993-440c-935a-1739a70298c5 |  | checkpoint | Check fire wrap is correctly rated & located as per current IFC documentation
checkpoint-status | a735a07e-3c69-4bbd-accd-cdc17f1af4a7 |  | checkpoint | Check metal sleeve penetrations are sized & located as per current IFC documentation
checkpoint-status | f7f43e84-f263-4b14-9af6-9a19d43addfc |  | checkpoint | Check cast-in roof outlet/overflow bodies are installed in locations & heights as required
checkpoint-status | 1cd26d83-4093-4c3c-9632-c5b645344c90 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | bb439a32-9ba5-480b-92b2-0f50d8949fec |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 949e0ba6-8bba-4350-877b-64705773388e |  | checkpoint | Check all fire collars are Logged & Registered
checkpoint-status | b9574a27-84d8-4331-8a27-0ca5af05b3f0 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | cc7e5904-94b5-4485-b737-cb616db0166c |  | checklist | WW TMV/TCV Rough-in |  |  |  |  | Yes | WW TMV/TCV Rough-in | b123db2d-e198-4620-aa4f-71726c86dde2
checkpoint-status | 27b823bb-558a-4f22-8be7-e96c8ab62ce7 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 5eabc3d2-49cb-4ce9-b3fa-a1ba064ce728 |  | checkpoint | General finish & alignment both level & center of fixture/tapware
checkpoint-status | 206ea6fd-13cc-4665-b92b-486716f18b2e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | e59105ba-0a41-4af9-8801-6b1e2896e616 |  | checkpoint | Check silicone applied to studs
checkpoint-status | 20f3a3ba-5cc8-4763-a9fb-0fb9b86338c0 |  | checkpoint | Wall box is installed if required
checkpoint-status | 0cc60f13-d595-4784-b831-1f88ef9f3895 |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | e4fe5227-4642-4069-999f-aff68bcc54ac |  | checkpoint | Check for possible cross connections
checkpoint-status | b18c97fd-bd2c-4680-b7e4-ad7f2dfa0aaa |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 489d89de-a1c1-4a50-b61a-6cca8754b3ca |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | 6ec7cf4b-1c11-40ae-a908-8a9dc5d39815 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 55dc583f-d65b-4a14-bf27-c038d6ea18f1 |  | checkpoint | Seal or cap off any open ends if required for security
checklist-flat |  |  | checklist | Ingrounds - Cast in |  |  |  |  | Yes | (LATEST) Ingrounds - Cast in | b41f71b1-7bd7-4907-be24-c468e4d231bf
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - cast in elements
text | 40d0473b-0529-5d4f-bb63-8cc8794d0319 |  | textbox | Description of work zone (e. suction lines within location/drawing grid reference)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | All pipe elements free of damage prior to install
checkpoint-status |  |  | checkpoint | Where practical, pipes water tested prior to the pour
checkpoint-status |  |  | checkpoint | Pipe grades and size have been checked
checkpoint-status |  |  | checkpoint | Invert levels and finished levels have been checked
checkpoint-status |  |  | checkpoint | PVC has been lagged (add photos)
checkpoint-status |  |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status |  |  | checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint-status |  |  | checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint-status |  |  | checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status |  |  | checkpoint | Details of cast in element
text | a7904a72-5e77-508d-8085-1fb81daf9b8c |  | textbox | Location and description of what has been cast in (eg pumplines, trade waste, greasy waste etc)
checklist-flat | 4a491bdf-fe91-4904-8d7d-f41741ce776b |  | checklist | checklist |  |  |  |  | Yes | New Template | b4803b92-ceb7-4c39-be74-9c6d8db9f1da
checklist-flat | f8ace16a-6393-4e03-b05c-cf04aa7980a4 |  | checklist | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 3) - [Island Sink] | b621280d-0401-4522-a615-425c60c6d227
checkpoint-status | 540198af-590e-4ce7-a645-37a27a38cbbe |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 9cc75e12-d155-4078-bd40-679d5b921eeb |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 0e59f5de-4b9c-4826-9e05-f7df39a683d3 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 42af5337-9ec6-4985-8158-619b4874ec1e |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | 56d23694-c620-4561-aaff-091a572bdb03 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 12c3b941-66e7-4e77-8f42-d721a721d3f4 |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 2bd6478f-03b9-4496-95bf-7208904b1de2 |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 162e9c98-36ec-4f06-b6e0-86bc3c49aa44 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 9144910c-3090-4b6d-acc4-89f3386e37e8 |  | checkpoint | Shut off the water feeder valve
checkpoint-status | 8cc8f244-0182-494a-8b09-abdbb6368de1 |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status | 817f2a10-ff15-45f0-9d4f-42931bd192c2 |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status | ab80d119-bcf2-4238-8b0d-59e55342a82e |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status | e6637bed-01f9-4b2b-8eab-47399c44539d |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 66c4ef08-43a1-49fb-ae3c-204a66ecaa60 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 8e633bc9-7c2d-441f-adcf-015298486fde |  | checkpoint | Test sticker in visible location
checkpoint-status | f42ea759-f5d8-4d76-aaa4-d60ccbd1d495 |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 2b8955da-cd96-47c8-8f92-d82025d8733d |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | b4cfcfef-7c0b-4f8e-85a9-1336139cc098 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | 6bab71a3-858f-4a08-9a86-6039e9b0646d |  | checklist | NG Rough-in (High Level) |  |  |  |  | Yes | NG Rough-in (High Level) | b6e58e87-0e3a-4956-9caa-a91439e15333
checkpoint-status | 8b9abd83-6fc9-480d-8a5c-33e35b6538a4 |  | checkpoint | container
checklist-flat | e681976b-4ad0-452c-b3ec-c99277f9dcd9 |  | checklist | PE In-Ground Stormwater Pump Station |  |  |  |  | Yes | PE In-Ground Stormwater Pump Station | b7213c4a-2cc3-43eb-abaf-10761d0fd8fc
checkpoint-status | 6095d800-a3e2-4aa3-ba78-cb385d194760 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | f4bb1123-18b5-46ad-8a09-68acb49af26c |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 29c37349-e102-4fd0-b81f-42eb4983cd86 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 46089c82-6558-46a2-a103-02e4aa4a2d2d |  | checkpoint | General visual check for damage, etc
checkpoint-status | faa0342e-6957-4345-960d-787f1e0d28cf |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | e3df8eef-db9f-4fd6-a079-697bb65e4677 |  | checkpoint | Vents are installed if required
checkpoint-status | 86b27655-6447-48f1-9611-a213c919ce4a |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 6a25d2bb-fd51-4699-9ce9-d978f36812ab |  | checkpoint | Spoil is removed
checkpoint-status | 36c3dd18-6968-41c8-a32c-203bfcf871b9 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | a1d6c9e5-e606-4e72-ba53-edc56c7549b9 |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status | d6dccf8b-8c1c-4bfa-bf38-d592c903a2a7 |  | checkpoint | Electrical conduit is installed
checkpoint-status | 9dde6184-5c56-40cc-85b3-63a7e97672f9 |  | checkpoint | Electrical cable is installed
checkpoint-status | 7892e77d-a2ad-4b9a-b30b-3b4a947b07f9 |  | checkpoint | Control panel is installed
checkpoint-status | 6a1a1f81-316e-4ded-9920-7dd63d8fa569 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 3b7c5611-7633-461a-b986-9ac0d262dc70 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | d78dd29d-c8dc-400a-bee4-ee3a351288aa |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | b4f70a3e-0e1c-4c07-9d93-1ea5c3a48da6 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 4dffaec9-a6e8-4626-8ea8-ba2a451e099d |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Plant & Equipment Install - Sewer Pumpwell/s |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Sewer Pumpwell/s | b7aa45cb-357e-4e3a-ab5c-14455587568a
checkpoint-status |  |  | checkpoint | Sewer pumpwell/s has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all pumplines have been undertaken
checkpoint-status |  |  | checkpoint | Pumpwell lid has been lifted and all formwork has been stripped
checkpoint-status |  |  | checkpoint | Rails and lifting chains are in place
checkpoint-status |  |  | checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint-status |  |  | checkpoint | Sewer pumpwell is ready for commissioning by supplier/manufacturer
checklist-flat | 77d551e9-5678-4f90-aeb1-1fdffe4ac0cb |  | checklist | Peno - Wall |  |  |  |  | Yes | Peno - Wall | b7c9408d-238c-45c1-b187-8f2878606cd5
checkpoint-status | a53ff6c4-89cc-4308-b297-d02524bfea5d |  | checkpoint | Installation complies with current IFC shop drawings
text | 1de11901-d881-5c25-9bb2-3efc22992481 |  | textbox | Document invert level wall peno has been installed at |  |  | mm
checkpoint-status | 04871f94-087b-4b4e-9be6-59250eb088c4 |  | checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | 591c5895-2631-41ec-8aa9-d77eab96a34b |  | checkpoint | Concrete pour details
text | 8daada6f-e51d-5b22-b00f-21a4d4ae94ff |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat |  |  | checklist | Temps Set Up |  |  |  |  | Yes | Temps Set Up | bb076a7f-a011-4b8f-9fd6-56f397cffc41
checkpoint-no-status |  |  | checkpoint | ITP/ Checklist for set up of Temps for site
text | 8e12350b-b93c-5edf-8cfa-46237ee47470 |  | textbox | Description of work zone/s (eg site sheds, lunch room, jump form)
checkpoint-status |  |  | checkpoint | All poly pipe, temp pex/SharkBite/york flex for damage or leaks
checkpoint-status |  |  | checkpoint | Check pipe joints & witness marks are correct
checkpoint-status |  |  | checkpoint | PVC pipe for sewer and stormwater has been checked and is free of damage
checkpoint-status |  |  | checkpoint | PVC pipe connections are glued and have been water tested
checkpoint-status |  |  | checkpoint | All waste or rain water discharges to a live drainage system
checkpoint-status |  |  | checkpoint | Poly pipe used has a high pressure rating to suit all purposes across the site
checkpoint-status |  |  | checkpoint | Poly pipe mechanical joins have been tested
checkpoint-status |  |  | checkpoint | Jump form temp connection has slack for jacking
checkpoint-status |  |  | checkpoint | Temp pumps have been tested and are adequate for use throughout construction
checkpoint-status |  |  | checkpoint | Boiler and/or chiller unit installed and functioning
checklist-flat |  |  | checklist | FINAL Commissioning - GIT |  |  |  |  | Yes | (LATEST) FINAL Commissioning - GIT | be91bcac-adb2-460e-b968-fe973384a5bf
checkpoint-status |  |  | checkpoint | Plant & Equipment Installation checked off as below
label | 51c9785a-cdff-5fd9-970f-c38874e6c230 |  | note | Add Comments &/or Photos below as applicable
label | 9adcb14c-d344-59e0-83e3-e2b00b256d71 |  | note | Installer is a Registered Plumber (VIC) with endorsements for this work
button | 01adce75-6804-52de-9ee2-613997909fe5 |  | button | Installation complies with current AS/NZS-3500 (2018) | Yes,No,N/A
button | a03f09c1-78ab-583d-ab86-a6f060c8d63f |  | button | Installation complies with current drawings & specifications | Yes,No,N/A
button | 995e3959-ed00-50b8-be2a-9e128727d592 |  | button | Installation materials were used in accordance with manufacturer requirements | Yes,No,N/A
button | b7e6a3a3-25f4-559e-a384-19e9030bcc13 |  | button | Check for damage or leaks | Yes,No,N/A
button | 8dd873d1-ed34-5f62-9aaf-feeac6641bbc |  | button | Check plant/equipment is level & aligned correctly | Yes,No,N/A
button | edd1ecd5-06e8-5241-b0be-e6ed9ea013ca |  | button | Check connecting pipework levels & alignment are correct | Yes,No,N/A
button | 19dae2f9-efc4-543f-a8f0-3ad089a71d63 |  | button | Check control panels are accessible | Yes,No,N/A
button | b4cfe71a-d90d-57a1-9ae1-512077e54ae1 |  | button | Check maintenance hatches are accessible | Yes,No,N/A
button | 8558dab2-4f88-5bf2-aff9-400e5d675a7b |  | button | Check access ladders are installed | Yes,No,N/A
button | 1d7ffeea-0265-5172-a9e5-96f026502da5 |  | button | Check filter cartridge containers are accessible | Yes,No,N/A
button | 6b278206-650c-5383-bede-4d1a01e0a845 |  | button | Check all wiring or pneumatic lines have been installed correctly | Yes,No,N/A
button | 689062ac-884a-5898-b8a2-054256ef8a3b |  | button | Check all fixings & anchor points are installed & torqued correctly | Yes,No,N/A
button | 13460968-dc6e-5435-b11c-e087880bbf9d |  | button | Check pressure relief or back-wash pipes discharge to a dedicated drain point | Yes,No,N/A
button | b51d6aef-7e1c-5319-9e0b-88c1b1504cb4 |  | button | Check pressure/temperature gauges are visible | Yes,No,N/A
button | 465781a8-4ed5-512a-b2fe-9a8c0764d03a |  | button | Check isolation & non-return valves are installed correctly & flow direction is correct | Yes,No,N/A
button | b8fddfe7-1890-55ac-a81c-c0d856e872e1 |  | button | Check all vent & breather pipes are installed correctly | Yes,No,N/A
button | e9d2fec5-82a8-5956-a8ec-6e21b379cc12 |  | button | Check gas flues & power manifolds are installed to regulation | Yes,No,N/A
button | 2a734083-3e2e-5dfb-8067-e4ac6ca28c60 |  | button | Check protective covering is installed & area has been left clean | Yes,No,N/A
checklist-flat |  |  | checklist | Peno - Floor |  |  |  |  | Yes | (LATEST) Peno - Floor | be994d5a-eba2-4212-81c0-5755339d4874
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawing
checkpoint-status |  |  | checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint-status |  |  | checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint-status |  |  | checkpoint | Collars are firmly secured into formwork
checkpoint-no-status |  |  | checkpoint | Concrete pour details
text | afeebeb2-68ed-5879-8c01-cf51b3c2b4a4 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 93438107-2f43-4987-a004-75991fccc064 |  | checklist | PE In-Ground On-Site Detention Tank |  |  |  |  | Yes | PE In-Ground On-Site Detention Tank | c1446ec7-71a7-49f7-872e-20839849149d
checkpoint-status | a4e67305-52d5-4b6d-81a2-8e486ea819b6 |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | b2526c7e-cada-41ce-9127-d325003c04b8 |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 5494983b-7424-4992-a60f-05d87635002a |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | a2583272-3335-4ad8-8de8-67179160945f |  | checkpoint | General visual check for damage, etc
checkpoint-status | 06349107-db23-4e19-8ffe-6c9aeb5b273d |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | afe85473-48ad-4033-a0da-fe23d9557cb7 |  | checkpoint | Vents are installed if required
checkpoint-status | c7787664-8103-45cd-a739-f7caa22df562 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 04f34623-0621-4408-81cd-c2b5559f6741 |  | checkpoint | Spoil is removed
checkpoint-status | e0fbbb3e-e7b6-47c7-9d54-ba51f5e2ffa8 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | 1e082e26-916f-4524-af0d-e7a7b5aa780e |  | checkpoint | Outlet drain is installed & connected
checkpoint-status | 8ec407fd-7364-458b-becb-6525e4e3cf6f |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 1ea271ab-c641-4bad-8d8f-2c92aaa197b5 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Ingrounds - Drainage |  |  |  |  | Yes | (LATEST) Ingrounds - Drainage | c34f682e-c906-42a8-bfc3-737d067b0547
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - Drainage
text | 710c5373-7c82-562d-a005-c5cbba623bde |  | textbox | Description of work zone (e. location/drawing grid reference)
checkpoint-status |  |  | checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint-status |  |  | checkpoint | Inspection openings and/or clean outs have been installed
checkpoint-status |  |  | checkpoint | All drains are clear of debris and have been securely capped
checkpoint-status |  |  | checkpoint | Invert levels for drains and inspection openings have been checked against current IFC drawings
checkpoint-status |  |  | checkpoint | All drains have been tested
checkpoint-status |  |  | checkpoint | All drains have been backfilled and compaction completed
checklist-flat | e29035ef-6fbb-462a-ab2c-c1e6b88dcc90 |  | checklist | SW Downpipes/Overflows (High Level) |  |  |  |  | Yes | SW Downpipes/Overflows (High Level) | c3ee1bd8-2bf9-4250-b7b6-7460fd457964
checkpoint-status | 78af03ac-992c-42d4-a0ff-59d1c2efa0d1 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | c16c8a1b-53fb-4d5b-90a9-c6d30cfddee6 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | bed223e3-ad5b-4770-b434-f2ac1efef06c |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 49d4f8db-7b05-4df5-a2e1-87769de0aa06 |  | checkpoint | Downpipes are installed
checkpoint-status | 88e358c0-002d-42a3-861e-a32f656044b7 |  | checkpoint | Overflows are installed
checkpoint-status | 9bd7eb7e-1950-48e2-9166-07fc8b02254b |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 66d9e700-bbea-417e-b497-895ce132a86a |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | b1b48c37-0299-4757-9097-d3aa1a975906 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 09a8cf2b-d72e-4ba7-bf86-7812ba7b357b |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 3976a576-d100-4b97-af9b-5ccd302e32a6 |  | checkpoint | Penetrations are installed
checkpoint-status | b8ad3d8e-6819-4c95-beb6-7d4e7bf23286 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 409101f9-d5d6-4878-9ad6-932262b7c653 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 12d5da9b-357a-4992-84f2-b8ce28f79475 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 11423a9a-f342-4daf-8f59-9a812a31960f |  | checkpoint | Roof/overflow outlets installed
checkpoint-status | 18ee377f-b158-4174-a138-b07e0973de31 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 12f24b0f-411d-460a-82e1-5048ececc487 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 6ed63db9-7548-4d3f-af92-0a49c066b387 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 0bc66fb8-2c9f-4c8f-9613-7ad59fda85e5 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | caf63ef2-89d2-455d-a56e-f2a6a4e0be86 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | Pod Drain Connection (Prefab Bathroom or Laundry) |  |  |  |  | Yes | (LATEST) Pod Drain Connection (Prefab Bathroom or Laundry) | c50b2bd0-7144-4d73-a96e-348b634dc231
checkpoint-no-status |  |  | checkpoint | Drain connection from pod to building stack has been installed as outlined below
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Expansion joint has been fitted above and below the de-aerator fitting
checkpoint-status |  |  | checkpoint | Expansion joints are securely clipped and fixed to precast or solid element
checklist-flat | 266c4210-4dd7-4940-b40a-e45f185a55d0 |  | checklist | SD Wastes & Vents (High Level) |  |  |  |  | Yes | SD Wastes & Vents (High Level) | c541a97a-c81f-4376-8bbb-17ab7ee0b5d8
checkpoint-status | 8f8908d7-0ec9-4e9a-a167-55d8c5d41fda |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | db277a13-3ce9-4797-af73-2ffbf9e7ad8f |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | d17d5484-f1a5-4caa-85ca-b62ac5456a7d |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 45dc78fb-7b07-4e63-b1f4-412fb4c99339 |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | cec293e0-a50e-4cd1-a09c-32b587c45385 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | e89ec3d9-97d5-4de9-a9cb-031d9d999871 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | d0f8669c-6dd6-452e-b46d-ea0b9a50ecd3 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 7ce66702-73ff-40fd-a2cd-5620a8247ed4 |  | checkpoint | Fixture vent, group vent or AAV is installed as per design
checkpoint-status | b2d3ef0a-2a52-4954-ac6b-e19aa7163a71 |  | checkpoint | Penetrations are installed
checkpoint-status | 32c78a62-a216-48ee-859e-262247463fb5 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 289318ca-81fe-4487-b6dc-830fa20f459d |  | checkpoint | Fire collars are installed & registered
checkpoint-status | cd4dab72-fcf3-4da2-a7e3-7b4c72bd36b0 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 60518aea-b070-423e-af0d-4b066ce800fc |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 6d96d086-18aa-4930-8669-fc29f2bb9d47 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 262266a9-6d6f-470b-9a57-2625f3d2a7bb |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | fa6f1557-f51c-44d6-bb80-d5d21471b0f6 |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 78c3d6ea-377e-4767-bcea-3d0eff543fa7 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | c9161ee8-f454-4c19-bb30-64a1e1e26f61 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 3b53dce3-141f-4a6c-a737-b9336cdec7e4 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | 3f01773f-2642-4800-9e7c-9f96f0e59288 |  | checklist | MT Cold Water Meters |  |  |  |  | Yes | MT Cold Water Meters | c5db2115-999f-4eb3-9df8-e3d11cdb314c
checkpoint-status | 8533f8b7-09b5-40fc-9e1d-924ab1188146 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | bff55e62-b354-46e9-b68d-7db909a9c884 |  | checkpoint | Water Meter Details:
text | c8e478b3-0ff5-547a-8b05-3e38f7a25a88 |  | textbox | Meter No:
text | d966d79d-275f-56a0-af85-a2bafe1ad881 |  | textbox | Meter Location:
text | 6b4931a0-6245-56c4-9b12-1ff53e4714c3 |  | textbox | Meter Size:
checkpoint-status | adf61660-7b9b-4572-b31f-97864484273d |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | f4a0fc37-1db5-4645-b06e-f2a34c4bd5f8 |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | 1c12c5d8-1aae-457a-bd3f-0176f722944f |  | checkpoint | Meter bracketed
checkpoint-status | 0308d782-9300-41a4-88ef-4c6afc2ce2eb |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | cf772497-667f-4609-acb8-7abab64ea7d0 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | 9cf737ff-7328-4191-b6d5-991cab841c7c |  | checkpoint | Pulse rate value is correct
checkpoint-status | 4f64a605-56fd-4539-a5f0-95a2d40770c9 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | 176e9c5c-577a-4fcf-ad01-00c2dae00a23 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | 9208746c-8599-41f0-adce-c98cc70483b2 |  | checkpoint | Flow direction is correct
checkpoint-status | 9b83986c-32fa-4ed8-8ef1-db0b55ce1552 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 67e9aa3a-2476-4338-bbc7-afe434e7331b |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 839d76ff-eed3-4d2f-b985-fda84b1fdc37 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat |  |  | checklist | Rough In - Mains Water Meter Assembly |  |  |  |  | Yes | (LATEST) Rough In - Mains Water Meter Assembly | c67c0097-bc07-4288-8868-91e49f0bb751
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for specific design requirements for CW water meter assembly
checkpoint-status |  |  | checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint-status |  |  | checkpoint | Installation meets water authority requirements with specific clearances, distances and heights achieved
checkpoint-status |  |  | checkpoint | Barrel unions have been used to allow for future maintenance ease
checklist-flat | 1c2915eb-5071-442c-bf55-da52b92dcecb |  | checklist | PE In-Ground Sewer Pump Station |  |  |  |  | Yes | PE In-Ground Sewer Pump Station | c823c564-abf5-44d7-9dd5-84cf8f92eb37
checkpoint-status | 319f65ee-a82a-406f-bd86-c830a2aa06fb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | f7abb189-83b6-4a6d-a945-a9758f9962cb |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 11ac37bd-53db-41ad-b5b8-b247a234cefa |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 58d18dd2-92a4-4f74-92d0-00c555593b62 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 7bd8cb26-73a3-4d8e-aa3e-06c7efb6e0b9 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | ed53daf7-b26d-4ec9-b703-3082a0772c26 |  | checkpoint | Vents are installed if required
checkpoint-status | 6449a620-a553-45fb-84ac-988e1fc15f84 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | e1b95dbb-5853-43f9-b9f5-546d7e02bc68 |  | checkpoint | Spoil is removed
checkpoint-status | 16ff8d8f-a269-46e9-8942-04d35fabc214 |  | checkpoint | Inlet drain is installed & connected
checkpoint-status | c19644a0-d4a0-4364-bc18-7e8b88053a63 |  | checkpoint | Outlet rising mains installed & connected
checkpoint-status | 330cf135-a2bc-4b1a-93e3-4f8bb674621d |  | checkpoint | Electrical conduit is installed
checkpoint-status | eb236ccd-f71b-4d56-b529-48170e0480e3 |  | checkpoint | Electrical cable is installed
checkpoint-status | 59e8e31f-c6ff-4627-9409-5f1efd66edd7 |  | checkpoint | Control panel is installed
checkpoint-status | 470751c2-1980-4651-a771-e33b1e98d95c |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | f5f09f07-269d-4894-9ef3-6db1a63d8aa7 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | 47cfd242-15f3-49dd-9651-e46601303f95 |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | fc2c8e69-39d8-40f4-8b79-32b512ae5086 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | e424278f-32fe-413c-abde-0d69ac441abb |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Ingrounds - Stormwater LPD |  |  |  |  | Yes | (LATEST) Ingrounds - Stormwater LPD | c8533076-29be-4679-a1c6-93062772562a
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for Ingrounds - Stormwater LPD
checkpoint-status |  |  | checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | Installation meets Council requirements
checkpoint-status |  |  | checkpoint | All pipe elements free of damage prior to install
checkpoint-status |  |  | checkpoint | Civil pit/s installed and supported correctly
checkpoint-status |  |  | checkpoint | If applicable, reflux valve is installed and supported correctly
checkpoint-status |  |  | checkpoint | Access riser to surface level is installed
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - Waste & Trap Clean Out |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - Waste & Trap Clean Out | c99a0ae5-2153-4c80-9c2f-af1e9c6bffef
checkpoint-status |  |  | checkpoint | Shower waste trap has been vaccuumed - no debris remaining (include photos)
checkpoint-status |  |  | checkpoint | Bathroom/s floorwaste trap has been vaccuumed - no debris remaining (include photos)
checkpoint-status |  |  | checkpoint | Laundry floorwaste trap has been vaccuumed - no debris remaining (include photos)
checkpoint-status |  |  | checkpoint | All grates have been resecured to each waste
checklist-flat |  |  | checklist | Main Run Rough In (Cold Water) |  |  |  |  | Yes | (LATEST) Main Run Rough In (Cold Water) | cbf7924f-92a5-4e25-8837-6bd229e173f3
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for the main CW run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status |  |  | checkpoint | Clips and fixings are correct
checkpoint-status |  |  | checkpoint | Pipe run position & levels are correct
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Connected to meter manifold and pipe labelled with destination
checkpoint-status |  |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status |  |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status |  |  | checkpoint | Flexible connections are correct
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat | 05f90333-6bad-45b7-b051-05a26d42a25b |  | checklist | TST Testing Potable Water (1500 kPa) |  |  |  |  | Yes | TST Testing Potable Water (1500 kPa) | cc38e78d-76b2-4410-8990-148fbe4ab5d8
checkpoint-status | c280f7fe-a952-4180-83fd-753e2c64ce5e |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 0cc0d62d-c320-47d2-bb33-db765877f376 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | b5d68d34-9e15-4d70-a399-646dc8378a11 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 8a2bb612-6f05-4b49-871c-219a3c157ca4 |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | 05e61a94-4910-4878-9373-62742344bd02 |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 0d4fec3a-7f75-41bc-9dbe-e214ef3a62ac |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | cc166192-8c70-4ab5-8645-36a5a31105b9 |  | checkpoint | Ensure all in-wall mixer assemblies & pressure sensitive meters, etc are isolated/removed from the test zone
checkpoint-status | 7c292632-19bb-4185-a170-9ca52bee860b |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 6dbae139-4943-448a-869e-acd3a2ffa646 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 09a6d2e5-78d9-44cc-8586-4d8c79ed0dda |  | checkpoint | Shut off the water feeder valve
checkpoint-status | b91a3f22-3a36-42ce-a7f7-21257d150150 |  | checkpoint | Commence testing by slowly increasing pressure up to 1500 kPa and hold for 30 minutes
checkpoint-status | 108344ff-9535-4ba9-872e-a67a8fb72e78 |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 00033189-574c-4e55-abc7-88c500d6663d |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral working conditions
checkpoint-status | edd51325-8933-4b66-a8ec-0c77c6d60f24 |  | checkpoint | Test sticker in visible location
checkpoint-status | ec38c39a-05b5-4e4e-b7a8-abc8a63e161d |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 555414e2-7fb6-4844-b89d-08949e181aa2 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | edc0a378-b742-414b-a42c-5aea6dd95015 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | Peno - Cast In |  |  |  |  | Yes | (LATEST) Peno - Cast In | ce443834-fa9c-4c69-b2ff-43633d0bcc52
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status |  |  | checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint-status |  |  | checkpoint | Where practical, pipes water tested prior to the pour
checkpoint-status |  |  | checkpoint | Pipe grades and size have been checked
checkpoint-status |  |  | checkpoint | Invert levels and finished levels have been checked
checkpoint-status |  |  | checkpoint | PVC has been lagged (add photos)
checkpoint-status |  |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status |  |  | checkpoint | RWO body installed level
checkpoint-status |  |  | checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint-status |  |  | checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint-status |  |  | checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint-status |  |  | checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status |  |  | checkpoint | Concrete pour details
text | 771de81a-4563-5b32-9212-c640bacde2bf |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat | 6a59addf-7996-4c6f-b63d-467eddc0db90 |  | checklist | PE Above-Ground Large Hot Water Circulating Pump Package |  |  |  |  | Yes | PE Above-Ground Large Hot Water Circulating Pump Package | cf93b81c-6ff9-4e63-9089-1b96e646ef1c
checkpoint-status | f8c62dde-7e25-4288-a9f9-08164ac0affb |  | checkpoint | The installer is qualified & trained to carry out the task as assigned
checkpoint-status | 1302e0c2-bd6e-4417-ae0b-dd5d0d17698d |  | checkpoint | Plant & Equipment installation conforms with current IFC documentation
checkpoint-status | 45781883-f86d-4f16-be5b-67c21ed09ea1 |  | checkpoint | General finish & alignment both level & finished height are OK
checkpoint-status | 1c352714-70fd-49ff-87cc-dfc43b733687 |  | checkpoint | General visual check for damage, etc
checkpoint-status | 3c11b4ee-e5e7-4276-aeef-6ca887808256 |  | checkpoint | Visual check for water & oil leakage
checkpoint-status | b77f8aff-57ad-41b8-80fc-b013c9e82526 |  | checkpoint | Mountings fixed & torqued down to plinth
checkpoint-status | 0cb1c96c-9ef5-4e96-9fa2-ae22bf7fb3a8 |  | checkpoint | Inlet pipework is installed & connected
checkpoint-status | 2ba64e78-0fb7-4a36-8172-0922a718c3f0 |  | checkpoint | Outlet pipework is installed & connected
checkpoint-status | d6888f90-603e-4242-88c0-156bdbf4883d |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | fca5d790-4668-4b42-a6b6-cea0d8c2ff9e |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | f6315781-8614-49de-a280-593e8ec895b0 |  | checkpoint | Electrical cable is installed
checkpoint-status | c56b18cb-72b7-41a3-b3d4-c077a092269c |  | checkpoint | Control panel is installed
checkpoint-status | 59aa8689-c0a1-4441-bc1c-14e191eb1875 |  | checkpoint | Electrical Connections to control panel installed by electrician
checkpoint-status | 60af1fd2-60c4-431c-945d-484c71bd8b36 |  | checkpoint | Electrical Connections is certified by electrician
checkpoint-status | 2cf3d8dd-b883-4411-bf43-d0c07eb0796b |  | checkpoint | Pumps cycles set & test run & certified by pump provider
checkpoint-status | 1e4a3464-f4bd-4bd2-95e3-35af20a7b318 |  | checkpoint | Pressure gauges installed & running within operating limits
checkpoint-status | 76b4b318-df47-4bd9-b507-ef82ade1ce7a |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | d8e8af38-c5e4-4181-9c6a-51a39af063ed |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | c81faa0e-4e3c-4c6e-a132-2cd62786397b |  | checklist | AU Application for New Service Connection |  |  |  |  | Yes | AU Application for New Service Connection | d5cbae36-f24f-4de7-8181-fcadc999c064
checkpoint-status | 63202722-ddb7-4f3b-acfe-58897cac82a9 |  | checkpoint | Road Opening Permit
checkpoint-status | 4f3a9e38-b164-4a1a-91f9-f06e29639fe3 |  | checkpoint | Storm Water Drainage
checkpoint-status | 98262b79-b627-4d79-9baa-3fe0ae7e8583 |  | checkpoint | Sewer Drainage
checkpoint-status | 9c05d000-c544-4050-9cd0-fb4270e07127 |  | checkpoint | Water Supply
checkpoint-status | 4de82bc0-9716-4d21-ac34-a7d9ee5a35a8 |  | checkpoint | Natural Gas Supply
checklist-flat | 479e8223-3dc4-4ab3-8aa0-2ec8b64cac7c |  | checklist | FO Laundry Troughs |  |  |  |  | Yes | FO Laundry Troughs | d9c7dbca-9366-4711-b530-803f25ebc4ac
checkpoint-status | f6b3b926-5452-4861-988f-6523829dad78 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 011bafb5-984c-4b50-82e7-ff0dc0f4e756 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | a0a51384-9c09-49f9-9453-f81dfff64170 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | ab86f0f0-4bc5-4c19-aeac-72b1f60824d7 |  | checkpoint | Solid installation & mounting of trough bowl & mixer
checkpoint-status | 71fc92e2-8106-4468-a4f2-a3f29d3fb305 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 19991366-948e-4f64-b722-8e199464f5eb |  | checkpoint | Check for evidence of leakage
checkpoint-status | 8103c10b-37ba-4a05-8408-97dbe35c7050 |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | 18d0e8af-38f7-4e92-b9ab-2d185f4048be |  | checkpoint | Check cover plates are installed
checkpoint-status | 712a47e2-f8ea-416b-88b1-ea307d74b9bc |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | 5ffdb949-5c5b-455f-b013-c73fdc97dc62 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 4ceb4f7d-de28-4c6b-9391-8de276853515 |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | e2ef7898-6f93-4c4e-8dcc-e12ec8c8cdb0 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 132f2ac3-c35d-4c33-939e-1eb1f155976a |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 4d770028-ae6e-4973-a82a-487f120a0f82 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | a8640459-30ca-4e52-8ff9-2af503534be9 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 0732a9c9-33a9-481d-92d4-04b13909a081 |  | checkpoint | Check caulking is correct
checklist-flat | 317a61fb-66c2-4542-aa33-d642dc3db858 |  | checklist | CW Rough-in (High Level) |  |  |  |  | Yes | CW Rough-in (High Level) | e26e0e3a-2ee9-4c4d-9cc1-3db0497e624d
checkpoint-status | 4febba3e-254a-4cf1-a6de-23d960316ca6 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | decbaa89-e025-43bd-9577-157eb26633ef |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 41461c29-e788-4c7f-9a29-7d4c929426da |  | checkpoint | Pipe materials are correct for application
checkpoint-status | b338e99f-16be-4e66-b849-e54cd0001f3d |  | checkpoint | Check silicone applied to studs
checkpoint-status | b316c8d5-9cc1-4283-9c7f-28e0aa27e255 |  | checkpoint | Check TCV/TMV correct location & securely clipped
checkpoint-status | 7baf7dbd-4548-4e13-bc8f-9b6feac7bf5a |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | 893bd3a3-27c7-409c-a7ad-738ca44aeec5 |  | checkpoint | Check for possible cross connections
checkpoint-status | 2f541550-6057-4d46-8be6-a4195a698dcc |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 738f5f82-7edc-4442-9f3f-e5cf3da3101b |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | f8bbd45d-5a21-4b59-85bd-98f9ea603916 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | a5a70a7a-8ad6-4917-a994-2a55f44c1055 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 47353388-b8bb-4765-af52-689d8d648dd0 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 88b4115f-5be2-452a-8d37-8c7ab9af1da2 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 61a95dd8-0a66-4cff-a957-ee3409bfb3e9 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 6eae96cd-34d5-421d-8aea-0dc13821151f |  | checklist | Peno - Cast In |  |  |  |  | Yes | Peno - Cast In | e314223f-88bc-48fc-89f2-55a3f8d30bd2
checkpoint-status | 0b800f90-91a6-44e5-b937-6550ab578e9c |  | checkpoint | Installation complies with current IFC shop drawings
checkpoint-status | c74b6969-04a6-4be5-a83e-495b19abe884 |  | checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint-status | d1dec170-f25f-42fb-bad8-196ed77feec0 |  | checkpoint | Where practical, pipes water tested prior to the pour
checkpoint-status | dd8a1dd8-a76c-4584-ba49-2d74c33e9132 |  | checkpoint | Pipe grades and size have been checked
checkpoint-status | 72edaf9d-8540-4c73-8597-d1a559837ecb |  | checkpoint | Invert levels and finished levels have been checked
checkpoint-status | 74ec447d-b992-44e9-bc5d-e8b79801d799 |  | checkpoint | PVC has been lagged (add photos)
checkpoint-status | 1f182a49-dda1-4bef-a943-9c02304849a4 |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status | 329c3e3a-4e58-442d-8d48-da054b825065 |  | checkpoint | RWO body installed level
checkpoint-status | 72df4363-9875-49cf-98dc-21ff0ad5a357 |  | checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint-status | a8b6d5fb-2ce2-4888-ae50-49c95dbc1c07 |  | checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint-status | 1c44af43-8ee8-4190-bc69-1a2451add19d |  | checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint-status | 20e93eb8-d6dc-4b05-b78f-1bf293aa08f8 |  | checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | f969b0eb-e295-4b66-8210-ae36c4497460 |  | checkpoint | Concrete pour details
text | 7e763907-1221-52e4-8f7c-684cc44330a0 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat |  |  | checklist | Pod Rough In Connection (Prefab Bathroom or Laundry) |  |  |  |  | Yes | (LATEST) Pod Rough In Connection (Prefab Bathroom or Laundry) | e8176dd2-87a4-40df-a4ac-e15523259190
checkpoint-no-status |  |  | checkpoint | Drain connection from pod to building stack has been installed as outlined below
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Cold & hot water pipework is connected
checkpoint-status |  |  | checkpoint | Check isolation valves are installed correctly
checkpoint-status |  |  | checkpoint | TMV/TV has been installed
checkpoint-status |  |  | checkpoint | Protective covering is installed & area has been left clean
checklist-flat | 14ea98d9-de68-4517-a2bc-086b98d74442 |  | checklist | Incomplete or Delayed Works |  |  |  |  | Yes | Incomplete or Delayed Works | e86632a0-7f26-43d5-9ebd-63e4c5b29cf7
checkpoint-status | ecbdc03e-6897-4ced-a830-85136cb07d2b |  | checkpoint | Incomplete or Delayed Works Details:
text | ec46fe0d-a73c-5d4a-b6ca-5fef6003f277 |  | textbox | Detail:
checklist-flat | ead0cd33-da45-4047-997a-29c7164db499 |  | checklist | CW Risers (Pumped or Mains Pressure Risers) |  |  |  |  | Yes | CW Risers (Pumped or Mains Pressure Risers) | e884fc68-9e4d-480f-840f-225e71fb690b
checkpoint-status | d96c60c8-b339-4dd3-adf6-bd5655d1b624 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | cd22172b-6b27-4d4a-a384-d9837ff35e79 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | e66fdcfe-42a4-4934-bfe3-3e6265a82139 |  | checkpoint | Penetrations are installed
checkpoint-status | 44d3bb3f-4c64-4c32-8146-0937ac3660d9 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 7a137a6d-69f1-4661-baf4-cefcb4b21492 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | bedd0e43-d2d9-47c0-a033-4c583d29bffe |  | checkpoint | Check all valves &/or meter assemblies conform with current documentation
checkpoint-status | e91b6ab8-b954-4d8d-8350-b09053a18f31 |  | checkpoint | Ensure all risers are installed professionally with no abnormalities
checkpoint-status | 6d06500e-d347-4784-8318-4fcc618d399d |  | checkpoint | Roll Groove joints are torqued down to manufacturers Instructions
checkpoint-status | c7772602-7747-4894-a01b-8e6e984aea77 |  | checkpoint | Welded pipe joints are completed
checkpoint-status | cbf3afac-88a3-4a3c-8a2e-85113cc854ed |  | checkpoint | CU pressed pipe joints crimped & witness marked as per manufacturers instructions
checkpoint-status | b7a2ae79-40cc-4c62-9c18-d6b47f7aa0a5 |  | checkpoint | XLPE pipe joints are correctly crimped & witness marked as per manufacturers instructions
checkpoint-status | d866e64b-12e4-4672-beea-637238fb0732 |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | fb95b0a6-97d6-497c-96bc-653c19387d1f |  | checkpoint | Anchors are installed as per manufacturer instructions & compliant with AS3500
checkpoint-status | 428a14af-2770-4b63-8ddc-dc174ff253b3 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 368127d2-36cc-4c20-9af3-683730fef22a |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 4a29a372-8616-45c1-86f2-b60defa2d062 |  | checkpoint | Expansion device or loop is correctly sized & installed conforming with AS3500
checkpoint-status | 165782c1-c196-4d19-a55e-cd0e5011177c |  | checkpoint | Isolation valves are installed & flow correct
checkpoint-status | e4dd0230-7909-4ad8-a81a-8425cc848f14 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 537a57d0-ad0f-44c9-b15d-df5f11691b9d |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | bd4c51e4-c63d-4dd9-8c7b-e6e760304b35 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 482a44e7-e346-4f57-87ab-4350413bf0e9 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | ab7ca4e5-e379-4348-8539-abc4cfa9f4cd |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | fcc12517-6a20-46a0-93c0-86d007210b28 |  | checklist | SYP Syphonic Downpipes/Overflows (Grated Outlets) |  |  |  |  | Yes | SYP Syphonic Downpipes_Overflows (Grated Outlets) | e9ddb64e-aa87-43b6-b4e6-01ff70243ad2
checkpoint-status | f038bd67-7e13-4beb-8285-7401dfe9d659 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 958da979-e848-4b96-9cf3-d9739e5bfbb4 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | a73db63d-af91-4335-87af-7475eef4719c |  | checkpoint | Balcony (BO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | 4d358ccb-b547-4aa6-bc92-63241783d77c |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 973c394b-f653-42a8-9358-b1eaaee30cd7 |  | checkpoint | Cast-in round/square (RWO/OF) grates & bodies are installed in sizes & locations as per design
checkpoint-status | a7b4c76f-f49a-410f-afb2-7defdddd8ee6 |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | bc739b70-e1de-4569-a3cd-91f5f5b4a4d0 |  | checkpoint | Downpipes are installed
checkpoint-status | e3513615-ac96-4d2d-8018-d5deb4a4d31e |  | checkpoint | Overflows are installed
checkpoint-status | 173e9f68-5869-46de-baac-693002245e78 |  | checkpoint | Penetrations are installed
checkpoint-status | 80e73a5d-72d5-4f7e-8342-f815a0e5609e |  | checkpoint | Drain penetrations are caulked
checkpoint-status | d65b8191-a2df-4172-8b71-4c500597769b |  | checkpoint | Trench channels & grates are installed in sizes & locations as per design
checkpoint-status | 842ef5cb-6592-4b4b-a137-bad5a39c4875 |  | checkpoint | Cast-in round/square grates & bodies are installed in sizes & locations as per design
checkpoint-status | 0ca4b50d-15e8-47cd-9bc3-36336f474a9e |  | checkpoint | Cast-in planter box/tree grates & bodies are installed in sizes & locations as per design
checkpoint-status | a6aa6353-e73a-42c1-b72a-f053422fd933 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 0aeda3ad-e34e-4b66-8aea-8624b4b8e355 |  | checkpoint | Check inside trap for signs of debris etc
checkpoint-status | dfff1166-01bd-4331-a668-f5c227c9460b |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat |  |  | checklist | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test) |  |  |  |  | Yes | (LATEST) Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test) | eab07587-db4f-4cfe-9f6b-3cee34bfe79e
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for undertaking a bump test on Couta WaterPex fittings to meet manufacturer's guidelines
checkpoint-status |  |  | checkpoint | Pressure sensitive valves have been removed from test section (Note: this test will damage pressure sensitive fittings)
checkpoint-status |  |  | checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint-status |  |  | checkpoint | Air purging valve point has been nominated
checkpoint-status |  |  | checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint-status |  |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status |  |  | checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status |  |  | checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint-status |  |  | checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint-status |  |  | checkpoint | Electric pressure testing pump is calibrated
checkpoint-status |  |  | checkpoint | Pressure was slowly increased to 1500kpa and held for 2 minutes
checkpoint-status |  |  | checkpoint | Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa for a further 2 minutes.
checkpoint-status |  |  | checkpoint | The previous step has been repeated: Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa and held for 30minutes.
text | 549875db-4242-54bc-bdcd-8520b259da72 |  | textbox | Pressure reading photos must be taken at start & finish of 30minutes test. Add in comments (test duration etc)
checklist-flat | 2621f28a-16ed-4cb6-a8c7-2b0d04f2effc |  | checklist | FO Wash Basins |  |  |  |  | Yes | FO Wash Basins | eb5c9d47-c46a-48f6-9d3e-18b9b5c18623
checkpoint-status | a5cf5286-a124-430d-b18b-1e1f30a5dd9a |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | d3f104b2-51bb-4ee4-8d13-fd4be7fed049 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 2c893281-2829-4039-8e7b-9b26132b98ee |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | fc8aff1d-97f2-4f94-80dd-22bd3004c382 |  | checkpoint | Solid installation & mounting of basin bowl & mixer
checkpoint-status | 6c2ad2bd-8e4b-4334-83a2-e368c0792e4d |  | checkpoint | Check operation of plug & washer
checkpoint-status | a1ab04b6-15b5-4dd2-bc05-c4d85a9bed76 |  | checkpoint | Check for evidence of leakage
checkpoint-status | ede52012-7f3e-4e7b-b5cb-d375ed9af3b7 |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | b283b46e-baf6-4dcb-abcc-97add8a3a608 |  | checkpoint | Check cover plates are installed
checkpoint-status | cec46ea2-0c6f-4e88-b74f-2af11161342e |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | 33d8dc8c-0b07-493a-b347-0bd839b0fc42 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 832c3585-81ab-4f56-a9d9-047b66eb17bf |  | checkpoint | Check trap is installed & nuts are tight
checkpoint-status | 2132aa53-9eb4-4dce-bbb5-19552d58bc30 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 8bc537bd-9e36-4eaf-8dba-ea99475e3e45 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 8defba0a-95c8-4ce2-94ec-1a69080874c7 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 320d36a6-cfc0-44de-a18d-a396c9eb6108 |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 21dd1305-255c-45b3-abbc-efae17edaae0 |  | checkpoint | Check caulking is correct
checklist-flat | 4c1dc7d7-d88e-48e8-a3a8-8a13e4e0bc60 |  | checklist | Modular Bathroom (Pod Unit) Connections |  |  |  |  | Yes | Modular Bathroom (Pod Unit) Connections | eb858476-1fe5-4302-80da-bbce368a18d2
checkpoint-status | 59caf3ad-f632-4fa7-9547-9bb8a502547e |  | checkpoint | Confirm Pod Unit supplied & installed as per contract specification
checkpoint-status | 4d8e8bc8-f84e-4a2d-a1e6-5c1aff1e0fab |  | checkpoint | General finish & alignment of Pod unit is level & centred
checkpoint-status | 5d004951-9e0a-4278-b18f-19894920f053 |  | checkpoint | Check condition of all Pod Unit fixtures/tapware
checkpoint-status | 22638500-2d1b-4bb1-8513-0f2cbf4c846a |  | checkpoint | Check that the Pod Unit sewer drainage is connected to the building system
checkpoint-status | 6645d8c4-7534-4117-8637-f0e60f63c97b |  | checkpoint | Check that the sewer pipe-work is acoustically lagged as required
checkpoint-status | 15c1112f-8c30-4245-9c63-00c3a3cdbcb2 |  | checkpoint | Check that the Pod Unit cold-water pipework is connected to the building system
checkpoint-status | f4582fe1-0093-49a5-80e4-1528327501d6 |  | checkpoint | Check that the Pod Unit hot-water pipework is connected to the building system
checkpoint-status | 89777261-60bb-400d-b30a-08fcddcb38e6 |  | checkpoint | Check that the hot-water pipe-work is thermally lagged as required
checkpoint-status | 8f04d5be-e688-429b-97e2-5d7d31ea751c |  | checkpoint | Check the Pod Unit is provided with an in-built Temp Valve or Thermo Mixing Valve
checkpoint-status | 732632dd-987b-4902-890d-4d7df2cdb909 |  | checkpoint | Check in cupboard for signs of leakage
checkpoint-status | d36dc2d9-c11a-4428-9303-63e8fe1ac914 |  | checkpoint | Look for evidence of behind the wall leakage showing on floor
checkpoint-status | 1952ce65-aabe-4888-951d-ae45352a2c8a |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | bd1b282b-2996-433b-aa67-fdbe98d71d3f |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | ad19d4bf-1b52-428e-a60f-d266e58950d5 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 27d0de1d-13df-49a9-a6c4-15286403b0ec |  | checkpoint | Temperature test warm water to ≤ 50°C
checkpoint-status | fe4323f8-e10d-46e2-900d-d9914c7f80a0 |  | checkpoint | Temperature test warm water to ≤ 43°C if Pod Unit is DDA compliant
checkpoint-status | e628fb36-b6a1-4f3e-a807-332ba1ac8d7e |  | checkpoint | Test result is compliant with AS3500 (Record test by photo & time/date)
checkpoint-status | 6e1c5161-d4b1-4faf-b29b-763650e9b45c |  | checkpoint | Valve is securely turned off (if required)
checklist-flat |  |  | checklist | Plant & Equipment Install - Water Storage Tank |  |  |  |  | Yes | (LATEST) Plant & Equipment Install - Water Storage Tank | eba013f8-85fe-4e12-9c67-9f4d6292c73c
checkpoint-status |  |  | checkpoint | Water storage tank has been installed as per IFC drawings
checkpoint-status |  |  | checkpoint | Testing of all supply lines to tank has been undertaken to the furtherest point possible pre commissioning
checkpoint-status |  |  | checkpoint | Flow control valve (eg Bermad) has been installed and is watermarked
checkpoint-status |  |  | checkpoint | Ensure float connection is secure and to be part of commissioning at a later date (note, if the float comes off, it will lead to overfow issues)
checkpoint-status |  |  | checkpoint | Overflow is positioned 50mm above highest float setting (this is critical)
checkpoint-status |  |  | checkpoint | There is a physical air break from the tank-fill pipe height to the height of the overflow
checkpoint-status |  |  | checkpoint | If specified, tank level probes have been installed
checkpoint-status |  |  | checkpoint | If specified, provision for BMS connection
checkpoint-status |  |  | checkpoint | Access ladder is installed with lock on top of the tank access panel
checkpoint-status |  |  | checkpoint | Statutory warning signage is visible
checklist-flat | 7e842858-79d9-4833-ad7c-f92ad001aa73 |  | checklist | CW Cold Water Tapping to Meter Room |  |  |  |  | Yes | CW Cold Water Tapping to Meter Room | ebe4e682-29e4-483a-a94d-c0239935b851
checkpoint-status | 8528278d-b66f-4ba9-891a-460e3dd9af56 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 70265ef3-746b-429b-9ea5-f2475f82706d |  | checkpoint | DBYD received & verified before commencement of work
checkpoint-status | 916ec1f2-e71d-4258-adfe-4f0c78b6955a |  | checkpoint | Traffic management plan in place & approved
checkpoint-status | 3378ff3f-3ff8-4792-874c-cfd4f3bf1f8f |  | checkpoint | Authority water applications & start work notices accepted
checkpoint-status | 10672f58-07f1-420a-bd26-cf1e52a158bc |  | checkpoint | Municipality asset opening notices placed & accepted
checkpoint-status | 4c35712e-6c66-49d4-b347-e84982c3288a |  | checkpoint | Authority divide valve assembly or tee insertion installed by authority contractor
checkpoint-status | 34b981d3-8aa9-4f98-be6e-05fab056bb86 |  | checkpoint | Sluice valves installed including flanges bolted, torqued & denso protected
checkpoint-status | 1491b884-2f14-4ecf-a6f0-200b45537910 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 76d2745a-0dcf-48dc-9557-af20d7c4b311 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | c1fc07ed-e934-4699-a878-1711e3e1329e |  | checkpoint | Location & levels are correct
checkpoint-status | 4a617154-d3fd-443b-ba94-aacf38038ae4 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | e52cb5b1-f715-4518-91c8-3322b529f9e4 |  | checkpoint | Incoming pipework is installed & layed to meter room
checkpoint-status | 69af53c8-e410-4eb5-821c-5e6c24e7254c |  | checkpoint | Pipe sleeve installed & sealed if required
checkpoint-status | 0b4c921b-8266-4ea9-8e00-6b73d24eb7f1 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 265b69da-22a9-48ec-af13-73cefc27e777 |  | checkpoint | Electrolysis prevention in place if required
checkpoint-status | 980a235d-5a3e-449c-b3cd-4840197232fb |  | checkpoint | Marking tape installed
checkpoint-status | 6f7cda74-9a51-40da-911e-80666334ad36 |  | checkpoint | Backfill is specified materials & compacted to test OK
checkpoint-status | 8804c83f-ac34-4402-8856-045207f93d93 |  | checkpoint | Spoil is removed
checkpoint-status | e5469ebd-9664-4645-aaa6-471a787c25d2 |  | checkpoint | Temporary top-dress of trenches with cold mix etc.
checkpoint-status | f3c7d6a3-f9c8-410e-b0a5-f587329e1d0c |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | a0ba3fc2-e8aa-46df-abcc-652cad52d688 |  | checkpoint | Clips & Shanks etc. are completely corrosion protected by use of "Denso" type wrapping & sealing
checkpoint-status | 7145ae1b-83a1-4b41-a768-021410b7b5ce |  | checkpoint | Pipe penetrations are caulked
checkpoint-status | a8584a05-300b-471f-9c23-2bf2c27f1c99 |  | checkpoint | Above ground pipework fixed & pipe I.D. labelled compliant with AS3500
checkpoint-status | 496f2e99-41a5-4a9f-ab36-4de811ac6943 |  | checkpoint | Main meter inlet valves installed & locked off
checkpoint-status | 2b51d6f8-2402-4648-ba64-1ea746d13e35 |  | checkpoint | Connection flanges fixed & torqued down to manufacturer specification
checkpoint-status | 13847041-566b-49d3-bf40-8525adbb6ced |  | checkpoint | Authority main meters installed & secured as per authority installation guide
checkpoint-status | 78ced649-d032-448d-9038-11e745b75f90 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | bf67f5be-1c8b-492f-9d63-765acc4b140a |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checklist-flat | e3a16824-66b8-444b-b932-6157e00760b2 |  | checklist | NG Rough-in (Low Level) |  |  |  |  | Yes | NG Rough-in (Low Level) | ec75d7e2-e905-4553-869a-a672e7ff92ca
checkpoint-status | 9aabebd9-2be5-438e-b4a0-ab51575cf344 |  | checkpoint | This installation and following checks are to comply with AS-5601
checkpoint-status | 77e50b7e-fd44-464b-85d8-6febc2ae701e |  | checkpoint | Check general visual check for pipe damage/leaks, etc
checkpoint-status | 4f99aaec-b8cc-461a-8fc5-29620cba72a7 |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 9332272a-defe-436b-8776-9be09b38618f |  | checkpoint | Check silicone applied to studs
checkpoint-status | f58ab7bc-56d0-4961-84a8-92a10783b412 |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 6eaadfb5-cf34-4ad2-bce6-f856f8ebf3ea |  | checkpoint | Check In-wall lugged elbows are installed to correct locations
checkpoint-status | 19b0510b-a2f4-42a6-ad4e-19e9ad7b7812 |  | checkpoint | Check all crimped joints & witness marks
checkpoint-status | 8b452ee8-175a-499e-a57a-219c7d04d467 |  | checkpoint | Check clip spacing are correct at ≤600mm
checkpoint-status | 0f683da0-7096-4963-b275-3a4b66351f58 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | 7a1b5f46-ef35-4490-b8fb-25d7152a030c |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | f96ce4b9-e89d-4542-8ba7-a19c3171b47f |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | 0d96660f-49e3-4a31-96f7-9e387921208b |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | bd044203-ac68-485f-821c-0f9cc82cbd30 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 7c24b739-5e5e-4af4-ab0c-ad22011e2251 |  | checklist | CC Concrete Coring & Cutting |  |  |  |  | Yes | CC Concrete Coring & Cutting | ed455c4c-f25f-474c-8b79-6475017c64a3
checkpoint-status | 15e9a927-14fd-4aeb-aaf5-d600fac089cd |  | checkpoint | Structural Engineer has been consulted & certified the proposed cutting
checkpoint-status | 74c27774-9f7f-4733-86c4-5897f73f6a2c |  | checkpoint | Post tensioning design has been overlayed
checkpoint-status | de5dc733-c0fc-43d5-a1b4-13c3b9bf509e |  | checkpoint | Electronic/Sonic survey has been completed & certified
checkpoint-status | fdbe9a16-3695-4d60-9f5e-e8cac8c65a8f |  | checkpoint | Safety procedures have been certified & work area is in compliance
checkpoint-status | 49d84437-b04c-4d54-b9c7-d5184f917e91 |  | checkpoint | Installed & sized as per current documentation
checkpoint-status | e32ff4ad-a1be-4e03-beec-656c4688c52e |  | checkpoint | Covers installed if required for security
checkpoint-status | 29f9b308-f1d1-4ac5-94c7-a4e27ea35661 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 4bb4c53d-7c87-4de8-8405-5567f81c5f2e |  | checkpoint | Check cast-in roof outlet/overflow bodies installed in locations & heights as required
checkpoint-status | fddabea0-79c2-46fb-ba83-0849a21fe4d5 |  | checkpoint | Finished R.L. are correct & verified
checkpoint-status | cf0f70e1-0e82-4ce3-b087-5f644c88a6ec |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 1a48747c-883a-4d70-9df0-402e8cfb0072 |  | checkpoint | Record installation by photo & time/date
checklist-flat |  |  | checklist | Rough In - Meter Install (Fitout) |  |  |  |  | Yes | (LATEST) Rough In - Meter Install (Fitout) | ed6c2abe-47d1-45b8-8ad0-c2625efe17c5
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for install of meter for future fitout
checkpoint-status |  |  | checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint-status |  |  | checkpoint | Meter installation meets water authority requirements
checkpoint-status |  |  | checkpoint | Isolation valve has been installed
checkpoint-status |  |  | checkpoint | PRV has been installed
checklist-flat | 34f1d5db-fd6f-4ddd-bf7e-a03611053f5e |  | checklist | FO Toilets |  |  |  |  | Yes | FO Toilets | ef011454-8ae5-4976-aa62-c587c6a359ae
checkpoint-status | 5f91e575-181f-4315-89a8-8241bfcc1b54 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 714e56d6-4c0f-4254-a6fe-56e12b1edfbd |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 0e212eb8-1e99-4fd7-91a2-40d3267fc21d |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | ac85a536-2f4c-46ac-80d7-1e4cc1007044 |  | checkpoint | Solid installation & mounting of pan, seat, cistern & button plate
checkpoint-status | c9c00658-5774-4031-9a8a-91372d44ec37 |  | checkpoint | Check for evidence of leakage
checkpoint-status | 6241395c-0a10-4e8a-b554-0b394006a829 |  | checkpoint | Operate both full & half flush & check for internal overflow
checkpoint-status | 96d079fc-0106-421a-a368-1fe47a63321e |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 65330522-891b-4b90-a470-0db16b4235fc |  | checkpoint | Check caulking is correct
checklist-flat | d88ad4bb-8d0c-4a0b-b6c0-208ffb30c767 |  | checklist | NG Natural Gas Meters |  |  |  |  | Yes | NG Natural Gas Meters | f073ad15-5be3-4edc-b438-01424290b9f0
checkpoint-status | ee0ab9b9-54d0-4659-9319-f5d85be827df |  | checkpoint | Water Meter Details:
text | 6e087735-9bc3-52b0-bf18-0581bfac45a2 |  | textbox | Meter No:
text | 0fb89f5e-24c3-56dd-8703-34a44ef8f349 |  | textbox | Level:
text | ab09a87c-914a-5741-8ed0-41e7360df1e2 |  | textbox | Meter Size:
checkpoint-status | 23e77c86-0e0b-44dc-a140-e68576b2b7d6 |  | checkpoint | General visual check for pipe damage/leaks, etc
checkpoint-status | ed287a05-da94-4ae9-a8a7-fde00facc4fe |  | checkpoint | Meter installed & sized as per current documentation
checkpoint-status | c5efcbdd-8213-44be-a92a-711075e29123 |  | checkpoint | Meter bracketed
checkpoint-status | f38c1178-3e0d-4d05-a461-6303b64e6868 |  | checkpoint | Analogue meter display is facing upright
checkpoint-status | b5668587-6b31-4b5a-bd2f-1a0e63280f03 |  | checkpoint | Confirm I.D. point against the meter register
checkpoint-status | cfbb6db4-3494-4fcf-bd63-4e9c556bb26c |  | checkpoint | Pulse rate value is correct
checkpoint-status | ddcdb926-9b5c-447e-b06a-d934f5bc7d65 |  | checkpoint | Pulse rate is output is manually proved
checkpoint-status | a093004a-172b-42a4-b0f3-0212c347ccb2 |  | checkpoint | BMS wiring connected by mechanical contractor
checkpoint-status | c52ba520-59e8-4827-bf32-0fef590a0c96 |  | checkpoint | Flow direction is correct
checkpoint-status | 0db3bcfc-f5d5-41a5-8b62-2bddf757464d |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checkpoint-status | bbb0c906-86d6-4301-b111-323c1e2f9cd0 |  | checkpoint | Record installation by photo & time/date
checkpoint-status | 8cad8cf9-53f2-4d7f-9a58-85eab17352b0 |  | checkpoint | Isolation valves closed after testing (If Required)
checklist-flat | 4908bd2c-b83e-400d-a255-9eff6b37cdcc |  | checklist | Peno - Floor |  |  |  |  | Yes | Peno - Floor | f0855c49-4d54-4d11-9027-245d738f5664
checkpoint-status | 4f3de2ee-ccb0-407b-9f55-b63e849e3254 |  | checkpoint | Installation complies with current IFC shop drawing
checkpoint-status | 12669f1c-2cbc-40f8-8917-5f1098d1ee9b |  | checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint-status | 04d1c707-89ad-4879-b5c9-9702f9a03699 |  | checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint-status | 8dd4d621-0b57-40fa-bfcd-da2d13f422bc |  | checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | 82774d2d-df88-4e7e-90b5-6367f534c105 |  | checkpoint | Concrete pour details
text | 756ad826-067d-521e-87b9-1bfce5473522 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist-flat |  |  | checklist | Testing - Air Test - Stormwater & Downpipe |  |  |  |  | Yes | (LATEST) Testing - Air Test - Stormwater & Downpipe | f2a0f3e7-97c9-4432-bd14-74c660bad404
checkpoint-no-status |  |  | checkpoint | Test Phase (stormwater)
checkpoint-status |  |  | checkpoint | The stormwater drainage pipe has been filled with air as per section 9.4.2 of AS3500.3.2021
checkpoint-status |  |  | checkpoint | Pressure of 30 kPa has been applied to the drain and maintained at this pressure for 3mins (with compressor remaining operational for air temp to stablize)
checkpoint-status |  |  | checkpoint | Compressor was shut off and the time taken for the pressure to drop from 25 kPa to 20 kPa was greater than 90sec for DN 225 or smaller (or 180secs for DN 300 or DN 375)
text | b64f3a51-58cc-5950-be31-699d5fecc098 |  | textbox | Start of test: Note start time and include photo of calibrated gauge at the start of 90sec (or 180sec) test
text | c94a184a-059f-5863-8f80-7104d4ca38f3 |  | textbox | End of test: Note end time and include photo of photo of calibrated gauge at the end of 90sec (or 180sec) test
checkpoint-status |  |  | checkpoint | The test has been deemed successful
checkpoint-no-status |  |  | checkpoint | Test Phase (for downpipe)
checkpoint-status |  |  | checkpoint | The internal downpipe been filled with air as per section 9.3.1 of AS3500.3.2021
checkpoint-status |  |  | checkpoint | Pressure of 30 kPa has been applied to the drain and maintained at this pressure for not less than 3mins
text | 0e0bd203-399f-5f23-ad22-a6609e060aad |  | textbox | Start of test: Note start time and include photo of calibrated gauge at the start of 3min test
text | f43b2636-17bd-5114-9feb-7149a82cd067 |  | textbox | End of test: Note end time and include photo of calibrated gauge at the end of 3min test
checkpoint-status |  |  | checkpoint | The test has been deemed successful
checklist-flat | 37f26242-42c2-4a62-9fc0-f7ef81325618 |  | checklist | SD Wastes & Vents (Low Level) |  |  |  |  | Yes | SD Wastes & Vents (Low Level) | f2b11cdd-f44f-41d0-b70b-be94b0902263
checkpoint-status | 0d064349-bb5a-42bc-a3a4-983243197133 |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ec39b847-a9b8-481b-899a-691d13a90ec4 |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | d10ad83d-25f4-4d69-86b9-638fb259718b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | cf6eeed1-76ba-41e8-87cd-1db7ef2153db |  | checkpoint | Check in-wall noggings are installed to correct locations
checkpoint-status | 0ec0e095-cb41-434f-a993-a1574b8173cd |  | checkpoint | Check waste pipes are installed to correct heights & locations
checkpoint-status | 81825e49-4400-455e-b103-5f8751885051 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | ff1254ed-7e89-444e-8665-f53a377fff0c |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | cc51d20b-c79b-43ed-ba25-9a6a7d219618 |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 018216ba-a84b-462d-9964-0c80c7ee090c |  | checkpoint | Penetrations are installed
checkpoint-status | 37f25a09-a0c6-4c00-b759-dcd71f943447 |  | checkpoint | Drain penetrations are caulked
checkpoint-status | 313f9a78-ac9d-4f12-8589-daf1c9fd2725 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | 84e7172a-6df9-4392-b052-6fc50f1187e4 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | 62bfa711-beb9-43f9-8838-6e82c8e103fa |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | 21a0a5e8-e3fd-4b35-b723-55825decdb39 |  | checkpoint | Check traps are correct locations, finished heights & clear of debris
checkpoint-status | 034077b2-0f5b-4ffa-9dcf-4e6b18e17fa2 |  | checkpoint | Rising mains installed & connected if required
checkpoint-status | c0fc399d-f87c-4192-95c9-e1e9e74d0ffe |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 1adaa4e7-7d2c-4f02-ace7-3f368e058278 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | bc6699a0-519f-4cd6-be3d-7f96c5e71e43 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | 2a29f700-e421-4329-980e-d11b54b6b8d2 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat | aadb5aa4-833c-41fa-880f-1cbdf8d86e67 |  | checklist | Pour Sequence Layout Checklist |  |  |  |  | Yes | Pour Sequence Layout Checklist | f316003f-bc53-42e4-8e8b-2556d99ce5b5
checkpoint-no-status | 31093558-174b-4e00-8306-d371b6246586 |  | checkpoint | Pour sequence layout reference attached
checklist-flat |  |  | checklist | Rough In - Meter Manifold Install |  |  |  |  | Yes | (LATEST) Rough In - Meter Manifold Install | f5330bbd-c421-4350-a935-bfb804603bbc
checkpoint-status |  |  | checkpoint | Installation in accordance with Water Authority requirements (no meter is located more than 1500mm from FFL or positioned lower than 150mm from FFL)
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status |  |  | checkpoint | Clips and fixings are correct
checkpoint-status |  |  | checkpoint | Connection to meter manifold complete and pipe labelled
checkpoint-status |  |  | checkpoint | All manifold points are capped
checklist-flat |  |  | checklist | Fit Off/ Fixture Install - All Items |  |  |  |  | Yes | (LATEST) Fit Off/ Fixture Install - All Items | f5a41eaa-c4a1-45b7-9388-0c39908b0b24
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for fit off of all fixtures (this is not a commissioning ITP)
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | All fixtures were checked for damage. Damaged fixtures do not get installed
checkpoint-status |  |  | checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint-status |  |  | checkpoint | All floor wastes and trap/s are clear of debris
checkpoint-status |  |  | checkpoint | All fixtures are covered and protected and the area is clean
checkpoint-no-status |  |  | checkpoint | Items installed
checkpoint-status |  |  | checkpoint | Vanity installed - aligned, level, secure, damage free (include photo)
checkpoint-status |  |  | checkpoint | Vanity tapware installed - aligned, level, damage free (include photo)
checkpoint-status |  |  | checkpoint | Shower rail/rose installed - secure, damage free (include photo)
checkpoint-status |  |  | checkpoint | Shower mixer installed - secure, damage free (include photo)
checkpoint-status |  |  | checkpoint | Kitchen sink installed - aligned, level, damage free (include photo)
checkpoint-status |  |  | checkpoint | Kitchen mixer installed - aligned, level, damage free (include photo)
checkpoint-status |  |  | checkpoint | Kitchen underbench boiling & chilling unit installed & connected - (include photo)
checklist-flat |  |  | checklist | Main Run Rough In (Non Potable/Rainwater) |  |  |  |  | Yes | (LATEST) Main Run Rough In (Non Potable/Rainwater) | f7e2e4fb-64bb-4737-80dd-cdf846903c79
checkpoint-no-status |  |  | checkpoint | ITP/Checklist for the main RW run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint-status |  |  | checkpoint | Clips and fixings are correct
checkpoint-status |  |  | checkpoint | Pipe run position & levels are correct
checkpoint-status |  |  | checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint-status |  |  | checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Valve flow direction & disconnection unions are correct
checkpoint-status |  |  | checkpoint | Extension points have sacrificial valves
checkpoint-status |  |  | checkpoint | Final check for cross connections has been undertaken
checkpoint-status |  |  | checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint-status |  |  | checkpoint | Flexible connections are correct
checkpoint-status |  |  | checkpoint | Labels have been applied
checkpoint-status |  |  | checkpoint | Rough in is ready for a hydrostatic water test
checklist-flat | eb7c4ec3-05dd-4804-abd3-6334b67ac00b |  | checklist | SYP Syphonic Downpipes/Overflows (Main Droppers) |  |  |  |  | Yes | SYP Syphonic Downpipes/Overflows (Main Droppers) | f81e69d3-0d47-488b-989e-1038f52e2a80
checkpoint-status | c82ad264-3aad-4421-8b97-d1f832ca1e0b |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | 245f131b-eb74-4b8b-90ac-c84834dd7e1f |  | checkpoint | General visual check for pipe damage, etc
checkpoint-status | 5c8e0edd-0df3-4f85-b947-fc252fa5c60b |  | checkpoint | Pipe materials are correct for application
checkpoint-status | 0a3cec5a-0592-4f8e-ad57-1db3bf293495 |  | checkpoint | Downpipes are installed
checkpoint-status | 6277b43f-5a00-4beb-82aa-8c02d7144417 |  | checkpoint | Overflows are installed
checkpoint-status | b4b89140-7370-4526-8877-a6dfd384e58b |  | checkpoint | Expansion joints are installed & compliant with AS3500
checkpoint-status | 3fd97d6f-12a9-4c0c-b0db-8c925e546965 |  | checkpoint | Ensure expansion joint spacers are removed
checkpoint-status | 60e68993-8ee3-4b6e-b78b-a95ffefb5561 |  | checkpoint | Clips are solidly fixed & of correct size/type as per manufactures instructions.
checkpoint-status | 79dad772-ce6d-4ecd-ac59-83c0efe6b07c |  | checkpoint | Clips & spacing are installed & compliant with AS3500
checkpoint-status | 09e8cc27-400a-4ec3-b8ce-daee17fad53e |  | checkpoint | Penetrations are installed
checkpoint-status | 6dc6777b-0c3f-4089-ba7b-a155d412c91f |  | checkpoint | Drain penetrations are caulked
checkpoint-status | a32705e0-e30e-49b8-b062-b002cc572607 |  | checkpoint | Fire collars are installed & registered
checkpoint-status | fcd15b94-bf08-435c-b412-f0be60ca7442 |  | checkpoint | Pipe-work is designed, installed & sized as per current IFC documentation
checkpoint-status | e7463696-3e36-4e7b-9554-40907f7d62a8 |  | checkpoint | Seal or cap off any open ends if required for security
checkpoint-status | b42fec64-aa30-4eaf-a14b-9b187997146f |  | checkpoint | Acoustic insulation installed & correct weight as designed
checkpoint-status | 180995ee-8055-4a4a-8262-b573e959a429 |  | checkpoint | Test by Pneumatic/Hydrostatic method as per AS3500 & RSG procedure
checkpoint-status | ff99860d-ff87-43ab-b2f3-460b3fe73a6b |  | checkpoint | Test sticker to be adhered to pipe 1500mm above floor level facing a corridor or accessible wall
checkpoint-status | db88d7c8-e942-465d-a8f5-59e45ed983a4 |  | checkpoint | Test result to be recorded by photo/time/date. (Provide comment if required)
checkpoint-status | b3492878-1a9a-452d-a708-c658065e8b50 |  | checkpoint | Pipe I.D. labels are installed & spaced compliant with AS3500
checklist-flat |  |  | checklist | Drains: Syphonic - Stack Riser |  |  |  |  | Yes | (LATEST) Drains: Syphonic - Stack Riser | f82c43aa-3f03-4795-ae82-04cd3360314f
checkpoint-no-status |  |  | checkpoint | Syphonic stack risers have been installed as outlined below
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint-status |  |  | checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint-status |  |  | checkpoint | Specific clipping method & anchor points are correct (including a clip to support each trap & bend)
checkpoint-status |  |  | checkpoint | HDPE fusion welds are witness marked
checkpoint-status |  |  | checkpoint | Pipes & junctions are clear of debris
checkpoint-status |  |  | checkpoint | Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint-status |  |  | checkpoint | Any open ends have been sealed (including the penos above slab)
checklist-flat | 592558d1-3bd4-44a8-aef3-4bf93deae2e2 |  | checklist | TST Testing Potable Water (900 kPa Test 2) |  |  |  |  | Yes | TST Testing Potable Water (900 kPa Test 2) | f938733d-accb-48de-9695-8152a2abe497
checkpoint-status | 92180c66-e9f0-4055-a1a4-6305ff80efd1 |  | checkpoint | This testing procedure conforms with that as set out in AS-3500.1 (2018) &/or AS-3500.4 (2018)
checkpoint-status | 38a43369-8c4a-4b1b-b3d1-7b5b0dd01d19 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | dba9ca20-ed74-4dea-a921-3a375f805d2e |  | checkpoint | Nominate an air purging valve point
checkpoint-status | f61d4418-ca26-4100-9de0-b68822381359 |  | checkpoint | Nominate a pressure testing valve point (if none at meter manifold)
checkpoint-status | bdec5106-f762-4e4d-9b9d-a34e0776886f |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | 3ddc551c-8018-47a9-90cc-0fb490dfc05a |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 0bdbb971-6e3c-4d0e-81c1-37f7b8929dfa |  | checkpoint | Slowly open a feeder valve & fill the test zone with water until completely purged of any air
checkpoint-status | 265ce4c8-fe86-4286-99da-50be65c2c419 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | 12b4ab85-a273-481f-95b7-cc626c0989fe |  | checkpoint | Shut off the water feeder valve
checkpoint-status | 6c14702b-346a-4342-89a0-dce3d3e01f2e |  | checkpoint | Commence testing by slowly increasing pressure up to 900 kPa and hold for 30 minutes
checkpoint-status | 0c5645a0-7e80-4868-88ca-c08ac1f264b5 |  | checkpoint | [For Couta System] Release pressure down to 500 kpa and hold briefly
checkpoint-status | 60545919-ed95-432d-a5d3-7f9d8081a38c |  | checkpoint | [For Couta System] Rapidly increase shock pressure back to 900 kPa and hold for test duration
checkpoint-status | 1fe7d052-9bb7-4a97-b1a8-cc8c2df44d75 |  | checkpoint | Testing is deemed successful if the water pressure remains unchanged after 30 minutes
checkpoint-status | 339b24fa-3e69-4330-a926-7e5f479dec10 |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | 18e82550-a068-420b-95b2-921ece4cc147 |  | checkpoint | Test sticker in visible location
checkpoint-status | b25a5ea0-3877-4089-bf36-e864b93c151d |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | b6b7b3fe-78df-4763-b3db-6d62ca7c4033 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 0c93be56-8eb4-4144-b996-4eac3a3410f8 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat | d4205060-a0ae-4247-8bf0-780eaa39623f |  | checklist | FO Kitchen Sinks |  |  |  |  | Yes | FO Kitchen Sinks | f974822d-f5fb-4eb9-b4e6-ac208c62e380
checkpoint-status | 96f7cb8f-69ae-4d6a-a229-797dae78ddcf |  | checkpoint | This installation and following checks are to comply with AS-3500
checkpoint-status | ce628496-bc5b-45d5-a50a-32e6249cea37 |  | checkpoint | Confirm type supplied & installed as per contract specification
checkpoint-status | 70961ac6-758c-4cf5-8085-c61d25ad2bd2 |  | checkpoint | General finish & alignment both level & centre of fixture/tapware
checkpoint-status | 04724081-01e1-412e-b8bf-eef20a02499f |  | checkpoint | Solid installation & mounting of sink bowl & mixer
checkpoint-status | 9f14ddbf-ebae-4cab-a698-00dc5a2a1416 |  | checkpoint | Check operation of plug & washer
checkpoint-status | 5da08c81-4815-4fdc-a4ee-bb53cf2b07dc |  | checkpoint | Check for evidence of leakage
checkpoint-status | 42d78458-6f56-46dd-bb77-8ffec3c8b49e |  | checkpoint | Check in cupboard for glue, cleaner or pencil marks
checkpoint-status | e51fcf0e-101a-4ac1-a73d-2d41a129dc15 |  | checkpoint | Check cover plates are installed
checkpoint-status | acb841a0-8e2c-4c27-a076-010d2eeccae8 |  | checkpoint | Check mini stops for operation & leaks
checkpoint-status | d2af9941-b87b-4856-925f-326acb081f39 |  | checkpoint | Check flexible connections for kinks or twisting
checkpoint-status | 61141f05-b0e6-4ad2-91e8-2d4c239226cd |  | checkpoint | Check double bowl connector & trap is installed & nuts are tight
checkpoint-status | 0173bb2f-e415-4cbc-9800-7b9c1d7afb66 |  | checkpoint | Check AAV installation (if required)
checkpoint-status | 9fce44e4-6dce-402d-b3f1-def014c52483 |  | checkpoint | Operate mixer & half fill bowl then discharge
checkpoint-status | 069d328a-64db-47da-83ca-6c67823fd4e3 |  | checkpoint | Check hot water delivery time & temp against contract doc's
checkpoint-status | 4156bbfc-0e2d-4ba6-9d28-6b5dab46d2be |  | checkpoint | Check inside bowl trap for signs of debris etc
checkpoint-status | 6fcb6224-1fd1-4ab3-8b82-50e7031aaffb |  | checkpoint | Check caulking is correct
checklist-flat |  |  | checklist | FINAL Commissioning - Stormwater Treatment System/Filter |  |  |  |  | Yes | (LATEST) FINAL Commissioning - Stormwater Treatment System/Filter | fee8675a-0f00-4d74-96fc-76da0da57976
checkpoint-status |  |  | checkpoint | Stormwater treatment system/ filter commissioning report/s to be uploaded here
checklist-flat | eb2c6937-e45b-4b6f-9e40-27eda939ced9 |  | checklist | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure |  |  |  |  | Yes | TST Testing Natural Gas Service (Nitrogen/Air Test) Low Pressure | ff092e08-8b63-4fd2-aa17-bdb231a44b06
checkpoint-status | 01b94993-31a6-4ce4-be9e-1b264f05a7cd |  | checkpoint | This testing procedure conforms with that as set out in AS-5601.1 (2013)
checkpoint-status | cefd50b9-29df-4a6a-b03f-65c605448236 |  | checkpoint | Ensure all valves dedicated to isolating the test zone are securely shut off & tagged
checkpoint-status | 55762a80-c691-4d3a-918d-4f4b23e23fd9 |  | checkpoint | Nominate an air purging valve point
checkpoint-status | 2660c54f-73d0-4011-914d-8bd6e90caf70 |  | checkpoint | Nominate a pressure testing valve point
checkpoint-status | f787082a-6b04-43b4-b323-80461d35c97e |  | checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint-status | a4586d4d-77fd-45b2-8023-9becc3b74d3d |  | checkpoint | Ensure all terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint-status | 3c07dc20-9606-422f-b3b9-5bf504c72787 |  | checkpoint | Slowly open test feeder valve & fill the test zone with nitrogen/air until completely purged
checkpoint-status | 59d86380-fd45-4ddf-ab86-90ffe3fed153 |  | checkpoint | Connect pressure testing device to the nominated test point
checkpoint-status | dc8f2167-b573-4200-b4e7-73052cd11ba6 |  | checkpoint | Shut off the gas feeder valve
checkpoint-status | b0dc1ff6-f12b-4ec7-b55f-906f8248d9b7 |  | checkpoint | Commence testing by slowly increasing pressure up to 1.5 kPa above working pressure
checkpoint-status | 2502bd84-5fa9-4166-9b3b-044f64846991 |  | checkpoint | Testing is deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint-status | 174f13a4-1249-4e4c-a966-4386e10e9f8a |  | checkpoint | If test is successful, slowly release test pressure and return the system back to neutral conditions
checkpoint-status | a17a2a28-f4d2-4be6-b9db-2ddf7e26b01b |  | checkpoint | Test sticker in visible location
checkpoint-status | ac5de83e-355a-4a74-8a8d-4c68caa2c8ab |  | checkpoint | Test result recorded by photo/time/date
checkpoint-status | 9adbfd3c-7223-47d1-a564-8f2e9cca04a6 |  | checkpoint | Test route/location attached to this Check Point as PDF plan or snap shot with its unique I.D. number.
checkpoint-status | 097fa124-6cbd-4b2b-851d-23fca800ce97 |  | checkpoint | Failures are to be immediately reported to management for analysis & repatriation
checklist-flat |  |  | checklist | Peno - Wall |  |  |  |  | Yes | (LATEST) Peno - Wall | ff46cb10-215d-4bf8-8e1e-9e8e04426c6c
checkpoint-status |  |  | checkpoint | Installation complies with current IFC shop drawings
text | 4d5931b2-5182-56bc-8bf9-eec613a19e56 |  | textbox | Document invert level wall peno has been installed at |  |  | mm
checkpoint-status |  |  | checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status |  |  | checkpoint | Concrete pour details
text | 0471beb5-c128-5532-99cc-b8b362f249b0 |  | textbox | Details of pour (date, supervised by RSG, approx time of day etc)