## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | Temps Set Up | [5 empty] | Amenities - Temps Set Up
section | Details
checkpoint-no-status | ITP/ Checklist for set up of Temps for site
textbox | Description of work zone/s (eg site sheds, lunch room, jump form)
checkpoint | All poly pipe, temp pex/SharkBite/york flex for damage or leaks
checkpoint | Check pipe joints & witness marks are correct
checkpoint | PVC pipe for sewer and stormwater has been checked and is free of damage
checkpoint | PVC pipe connections are glued and have been water tested
checkpoint | All waste or rain water discharges to a live drainage system
checkpoint | Poly pipe used has a high pressure rating to suit all purposes across the site
checkpoint | Poly pipe mechanical joins have been tested
checkpoint | Jump form temp connection has slack for jacking
checkpoint | Temp pumps have been tested and are adequate for use throughout construction
checkpoint | Boiler and/or chiller unit installed and functioning
checklist | Ingrounds - Drainage | [5 empty] | Amenities - Ingrounds - Drainage
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - Drainage
textbox | Description of work zone (e. location/drawing grid reference)
checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint | Inspection openings and/or clean outs have been installed
checkpoint | All drains are clear of debris and have been securely capped
checkpoint | Invert levels for drains and inspection openings have been checked against current IFC drawings
checkpoint | All drains have been tested
checkpoint | All drains have been backfilled and compaction completed
checklist | Ingrounds - Pumpwells/Tanks/Pits | [5 empty] | Amenities - Ingrounds - Pumpwells/Tanks/Pits
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - Installation of pumpwells/tanks/pits
textbox | Description of work zone (e. location/drawing grid reference)
checkpoint | Installation complies with AS/NZS-3500 (2021), current IFC drawings & specifications
checkpoint | Installation methods & materials are in accordance with manufacturer requirements
checkpoint | Invert levels for inlets, outlets and cover levels have been checked against current IFC drawings
checkpoint | Connection of drainage to pumpwell/tank/pit has been sealed/caulked/grouted both inside and outside
checkpoint | Cast in conduits to pump control panels are correctly sized and in accordance with current IFC drawings
checklist | Ingrounds - Cast in | [5 empty] | Amenities - Ingrounds - Cast in
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - cast in elements
textbox | Description of work zone (e. suction lines within location/drawing grid reference)
checkpoint | Installation complies with current IFC shop drawings
checkpoint | All pipe elements free of damage prior to install
checkpoint | Where practical, pipes water tested prior to the pour
checkpoint | Pipe grades and size have been checked
checkpoint | Invert levels and finished levels have been checked
checkpoint | PVC has been lagged (add photos)
checkpoint | HDPE fusion welds are witness marked
checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | Details of cast in element
textbox | Location and description of what has been cast in (eg pumplines, trade waste, greasy waste etc)
checklist | Ingrounds - Sewer BT Authority Connection | [5 empty] | Amenities - Ingrounds - Sewer BT Authority Connection
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - Sewer BT Authority Connection
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets water authority requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Boundary trap is installed and supported correctly
checkpoint | Reflux valve is installed and supported correctly
checkpoint | Access riser to surface level is installed
checklist | Ingrounds - Stormwater LPD | [5 empty] | Amenities - Ingrounds - Stormwater LPD
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - Stormwater LPD
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets Council requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Civil pit/s installed and supported correctly
checkpoint | If applicable, reflux valve is installed and supported correctly
checkpoint | Access riser to surface level is installed
checklist | Ingrounds - Authority Connection to Meter Room | [5 empty] | Amenities - Ingrounds - Authority Connection to Meter Room
section | Details
checkpoint-no-status | ITP/Checklist for Ingrounds - Authority connection to meter room
checkpoint | Installation complies with AS/NZS-3500 (2021) and current IFC drawings
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation meets water authority requirements
checkpoint | All pipe elements free of damage prior to install
checkpoint | Pipework is connected to water meter assemblies
checkpoint | Pipes have been wrapped in plastic (or denso wrap)
checkpoint | Pipe bedding is correct
checkpoint | Pipes are labelled
checkpoint | Any open ends have been sealed
checkpoint | All mechanical joints are correct and have been checked
checkpoint | Access riser from sluice valves to surface level installed
checklist | Peno - Floor | [5 empty] | Amenities - Peno - Floor
section | Details
checkpoint | Installation complies with current IFC shop drawing
checkpoint | Floor fire collar types & sizes are correct against IFC shop drawing
checkpoint | Top and bottom of peno/collar is capped & sealed
checkpoint | Collars are firmly secured into formwork
checkpoint-no-status | Concrete pour details
textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist | Peno - Wall | [5 empty] | Amenities - Peno - Wall
section | Details
checkpoint | Installation complies with current IFC shop drawings
textbox | Document invert level wall peno has been installed at |  |  | mm
checkpoint | Collars and sleeves are capped & sealed
checkpoint-no-status | Concrete pour details
textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist | Peno - Cast In | [5 empty] | Amenities - Peno - Cast In
section | Details
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Collar & pre-fab elements free of damage prior to install
checkpoint | Where practical, pipes water tested prior to the pour
checkpoint | Pipe grades and size have been checked
checkpoint | Invert levels and finished levels have been checked
checkpoint | PVC has been lagged (add photos)
checkpoint | HDPE fusion welds are witness marked
checkpoint | RWO body installed level
checkpoint | Clips, fixings & anchor points are correct and secure
checkpoint | All cast in elements are clear of debris, securely capped & sealed prior to pour
checkpoint | Water has been poured into PVC for deep beam/thick slab pour
checkpoint | Unfixed pipes are tied to reo (where necessary)
checkpoint-no-status | Concrete pour details
textbox | Details of pour (date, supervised by RSG, approx time of day etc)
checklist | Drains: Underslung - Sewer, Stormwater & Vent | [5 empty] | Amenities - Drains: Underslung - Sewer, Stormwater & Vent
section | Details
checkpoint-no-status | ITP/Checklist for underslung/suspended drains (sewer, stormwater and vents)
checkpoint | Installation complies with current IFC shop drawings
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/grade meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist | Drains: Stack Riser - Sewer, Stormwater & Vent | [5 empty] | Amenities - Drains: Stack Riser - Sewer, Stormwater & Vent
section | Details
checkpoint-no-status | ITP/Checklist for stack risers servicing sewer, stormwater & vents
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Clips, fixings & anchor points are correct and secure (includes independent clipping (no piggy backed clips)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint | Pipes & junctions are clear of debris
checkpoint | Inspection opening caps have been tightened and duct tape applied
checkpoint | For sewer: Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist | Drains: Syphonic - Underslung | [5 empty] | Amenities - Drains: Syphonic - Underslung
section | Details
checkpoint-no-status | Syphonic underslung drains have been installed as outlined below
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checklist | Drains: Syphonic - Stack Riser | [5 empty] | Amenities - Drains: Syphonic - Stack Riser
section | Details
checkpoint-no-status | Syphonic stack risers have been installed as outlined below
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Specific clipping method & anchor points are correct (including a clip to support each trap & bend)
checkpoint | HDPE fusion welds are witness marked
checkpoint | Pipes & junctions are clear of debris
checkpoint | Expansion joint clipped and spacer removed (to allow for expansion)
checkpoint | Any open ends have been sealed (including the penos above slab)
checklist | Drains: Greasy Waste - Underslung, Stacks & Vents | [5 empty] | Amenities - Drains: Greasy Waste - Underslung, Stacks & Vents
section | Details
checkpoint-no-status | ITP/Checklist for underslung/suspended drains for greasy waste
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Branch junction/s & off set invert levels have been checked and are correct
checkpoint | Expansion correctly clipped
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Peno has been caulked (top and underside of slab)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Greasy waste/pumpline has been water tested (include photos)
checklist | Drains: Trade Waste - Underslung, Stacks & Vents | [5 empty] | Amenities - Drains: Trade Waste - Underslung, Stacks & Vents
section | Details
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct (including a clip to support each trap & bend)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Tradewaste pipes have been tested with water (include photos of test)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist | Drains: Pumpline - Underslung & Stacks | [5 empty] | Amenities - Drains: Pumpline - Underslung & Stacks
section | Details
checkpoint-no-status | Underslung & stack pumpline drains have been installed as outlined below
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Penos above have been checked, opened and debris cleared
checkpoint | HDPE has been used & fusion sockets witness marked
checkpoint | Clips, fixings & anchor points are correct with secure fixings to reduce pipe movement (eg thrust bracing)
checkpoint | Pipe & trap invert levels have been checked and are correct
checkpoint | Pipes & traps are clear of debris
checkpoint | Required fall/gradient meets AS/NZS 3500 (2021)
checkpoint | Any open ends have been sealed (including the penos above slab)
checkpoint | Pumplines have been tested with water (include photos of test)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checklist | Pod Drain Connection (Prefab Bathroom or Laundry) | [5 empty] | Amenities - Pod Drain Connection (Prefab Bathroom or Laundry)
section | Details
checkpoint-no-status | Drain connection from pod to building stack has been installed as outlined below
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Expansion joint has been fitted above and below the de-aerator fitting
checkpoint | Expansion joints are securely clipped and fixed to precast or solid element
checklist | Main Run Rough In (Cold Water) | [5 empty] | Amenities - Main Run Rough In (Cold Water)
section | Details
checkpoint-no-status | ITP/Checklist for the main CW run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Connected to meter manifold and pipe labelled with destination
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied
checkpoint | Rough in is ready for a hydrostatic water test
checklist | Main Run Rough In (Hot Water) | [5 empty] | Amenities - Main Run Rough In (Hot Water)
section | Details
checkpoint-no-status | ITP/Checklist for the main HWF & HWR run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips, fixings & furrel blocks are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Hot water meter has been installed
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Rough in is ready for a hydrostatic water test
checklist | Main Run Rough In (Non Potable/Rainwater) | [5 empty] | Amenities - Main Run Rough In (Non Potable/Rainwater)
section | Details
checkpoint-no-status | ITP/Checklist for the main RW run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied
checkpoint | Rough in is ready for a hydrostatic water test
checklist | Main Run Rough In (Gas) | [5 empty] | Amenities - Main Run Rough In (Gas)
section | Details
checkpoint-no-status | ITP/Checklist for the main gas run from riser to tenancy/bathrooms/apartments/hotel rooms
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Pipe run position & levels are correct
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Expansion joints/loops are correct as per IFC and to AS/NZS 3500 (2021)
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Final check for cross connections has been undertaken
checkpoint | Check pipe clear spacing (service separation min 25mm has been achieved)
checkpoint | Flexible connections are correct
checkpoint | Labels have been applied
checkpoint | Rough in is ready for a gas test
checklist | Rough In - CW Design Components | [5 empty] | Amenities - Rough In - CW Design Components
section | Details
checkpoint-no-status | ITP/Checklist for specific design requirements for CW
checkpoint | CW tank bypass has been roughed in
checkpoint | CW backup to RW system has been roughed in
checkpoint | Check meter installed
checkpoint | RPZD/ back flow prevention device installed
checkpoint | Isolation valves installed
checkpoint | Pressure reducing valves installed
checkpoint | Future provision for connection to BMS
checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist | Rough In - RW Design Components | [5 empty] | Amenities - Rough In - RW Design Components
section | Details
checkpoint-no-status | ITP/Checklist for specific design requirements for CW
checkpoint | CW backup to RW system has been roughed in
checkpoint | Check meter installed
checkpoint | Isolation valves installed
checkpoint | Future provision for connection to BMS
checkpoint | Installation complies with current IFC Schematic & shop drawings
checklist | Rough In - Mains Water Meter Assembly | [5 empty] | Amenities - Rough In - Mains Water Meter Assembly
section | Details
checkpoint-no-status | ITP/Checklist for specific design requirements for CW water meter assembly
checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint | Installation meets water authority requirements with specific clearances, distances and heights achieved
checkpoint | Barrel unions have been used to allow for future maintenance ease
checklist | Rough In - Meter Install (Fitout) | [5 empty] | Amenities - Rough In - Meter Install (Fitout)
section | Details
checkpoint-no-status | ITP/Checklist for install of meter for future fitout
checkpoint | Installation complies with current IFC Schematic & shop drawings
checkpoint | Meter installation meets water authority requirements
checkpoint | Isolation valve has been installed
checkpoint | PRV has been installed
checklist | Rough In - Meter Manifold Install | [5 empty] | Amenities - Rough In - Meter Manifold Install
section | Details
checkpoint | Installation in accordance with Water Authority requirements (no meter is located more than 1500mm from FFL or positioned lower than 150mm from FFL)
checkpoint | Pipe joints & witness marks are correct (for pex & copper)
checkpoint | Clips and fixings are correct
checkpoint | Connection to meter manifold complete and pipe labelled
checkpoint | All manifold points are capped
checklist | Rough In: Commercial (High & Low Level Rough In) Water Services | [5 empty] | Amenities - Rough In: Commercial (High & Low Level Rough In) Water Services
section | Details
checkpoint-no-status | ITP/Checklist for rough in of high level and low level water services to specific areas (tea point/bathrooms/EOT etc)
checkpoint | Pressure Pipework (for high & low level rough-in) checked off as below
checkpoint-no-status | Install Phase
checkpoint | If pex is being insulated with armaflex, a barrier of duct tape has been applied to all pex crimp fittings
checkpoint | All joints have been crimped correctly and to manufacturers spec
checkpoint | Spacing of clips and fixings for WaterPex as per AS3500.1.2021
checkpoint | Any pex through metal studs is entirely protected from sharp edges (achieve through additional oversized sleeving or suitable grommets)
checkpoint | Check has been undertaken to ensure no cross connections
checkpoint | All pex fittings are crimped and ready for 1500 kPa bump test
checkpoint-no-status | Rough In Fitting Install
checkpoint | Installation and location of tempering valve or T.M.V is correct (must be within access panel area)
checkpoint | Location of shower mixer is as per latest IFC
checkpoint | Location of lugged elbow is as per latest IFC
checkpoint | Location of WC water point is as per latest IFC
checkpoint | Location of vanity water points are as per latest IFC
checklist | Rough In: Apartment Water Services (High & Low Level Rough In) | [5 empty] | Amenities - Rough In: Apartment Water Services (High & Low Level Rough In)
section | Details
checkpoint | Pressure Pipework (for high & low level rough-in) checked off as below
checkpoint-no-status | Install Phase
checkpoint | If WaterPex is being insulated with armaflex, a barrier of duct tape has been applied to all pex crimp fittings
checkpoint | All joints have been crimped correctly and to manufacturers spec
checkpoint | Leak detection indicator has broken away and 3 crimp lines are visible on the crimped fitting
checkpoint | Spacing of clips and fixings for WaterPex as per AS3500.1.2021
checkpoint | Any WaterPex through metal studs is entirely protected from sharp edges (achieve through additional oversized sleeving or suitable grommets)
checkpoint | Check has been undertaken to ensure no cross connections
checkpoint | All pex fittings are crimped and ready for 1500 kPa bump test
checkpoint-no-status | Rough In Fitting Install
checkpoint | Installation and location of tempering valve or T.M.V is correct (must be within access panel area)
checkpoint | Location of shower mixer is as per latest IFC
checkpoint | Location of lugged elbow is as per latest IFC
checkpoint | Location of WC water point is as per latest IFC
checkpoint | Location of vanity water points are as per latest IFC
checkpoint | Location of kitchen water points are as per latest IFC
checkpoint | Location of laundry water points are as per latest IFC
checklist | Pod Rough In Connection (Prefab Bathroom or Laundry) | [5 empty] | Amenities - Pod Rough In Connection (Prefab Bathroom or Laundry)
section | Details
checkpoint-no-status | Drain connection from pod to building stack has been installed as outlined below
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials were used in accordance with manufacturer requirements
checkpoint | Cold & hot water pipework is connected
checkpoint | Check isolation valves are installed correctly
checkpoint | TMV/TV has been installed
checkpoint | Protective covering is installed & area has been left clean
checklist | Risers (CW, HWF & HWR, Rainwater/Non Potable) | [5 empty] | Amenities - Risers (CW, HWF & HWR, Rainwater/Non Potable)
section | Details
checkpoint-no-status | ITP/Checklist for install of all risers
checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint | Any v-hose, victaulic joints are watermarked and installed correctly
checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Branch junctions & off-set levels are correct
checkpoint | Pipe joints & witness marks are correct
checkpoint | Checked for damage prior to install
checkpoint | Valve flow direction & disconnection unions are correct
checkpoint | Extension points have sacrificial valves
checkpoint | Labels have been applied
checkpoint | Pipes requiring lagging have been temporarily labelled
checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint | All risers are ready for testing
checklist | Risers (Gas) | [5 empty] | Amenities - Risers (Gas)
section | Details
checkpoint-no-status | ITP/Checklist for install of all risers
checkpoint | Installation complies with current IFC shop drawings, schematics & AS/NZS 3500 (2021)
checkpoint | Expansion loop position and length comply with IFC schematics & AS/NZS 3500 (2021)
checkpoint | Clips, fixings & anchor points are correct (etc - fixed anchor, slide guide clamp, spring clip)
checkpoint | Any v-hose, are AGA compliant and installed correctly
checkpoint | Clips used are not dissimilar metals and will not corrode an element
checkpoint | All pipework is clear of debris and any open ends sealed (with duct tape if temporary measure required)
checkpoint | Branch junctions & off-set levels are correct
checkpoint | Pipe joints & witness marks are correct
checkpoint | Checked for damage prior to install
checkpoint | Disconnection unions are correct to allow for future maintenance
checkpoint | Extension points have sacrificial valves
checkpoint | Gas authority labels have been applied with working pressure noted
checkpoint | Penos have been caulked and meet fire rating requirements (top and underside of slab)
checkpoint | Gas riser/s are ready for testing
checklist | Fit Off/ Fixture Install - Toilets & Cisterns | [5 empty] | Amenities - Fit Off/ Fixture Install - Toilets & Cisterns
section | Details
checkpoint-no-status | ITP/Checklist for fit off of toilet and cistern (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Installation is aligned, level and secure
checkpoint | Flush pipe has been measured to suit the pan prior to being cut to size
checkpoint | Button flush plate is in working order and not damaged/scratched
checkpoint | Seat and accessories are secure and correct
checkpoint | DDA suite back rest installed correctly
checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint | Pan trap is clear of debris
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Fixture has been left covered and protected and the area is clean
checklist | Fit Off/ Fixture Install - All Items | [5 empty] | Amenities - Fit Off/ Fixture Install - All Items
section | Details
checkpoint-no-status | ITP/Checklist for fit off of all fixtures (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | All fixtures were checked for damage. Damaged fixtures do not get installed
checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint | All floor wastes and trap/s are clear of debris
checkpoint | All fixtures are covered and protected and the area is clean
checkpoint-no-status | Items installed
checkpoint | Vanity installed - aligned, level, secure, damage free (include photo)
checkpoint | Vanity tapware installed - aligned, level, damage free (include photo)
checkpoint | Shower rail/rose installed - secure, damage free (include photo)
checkpoint | Shower mixer installed - secure, damage free (include photo)
checkpoint | Kitchen sink installed - aligned, level, damage free (include photo)
checkpoint | Kitchen mixer installed - aligned, level, damage free (include photo)
checkpoint | Kitchen underbench boiling & chilling unit installed & connected - (include photo)
checklist | Fit Off/ Fixture Install - Waste & Trap Clean Out | [5 empty] | Amenities - Fit Off/ Fixture Install - Waste & Trap Clean Out
section | Details
checkpoint | Shower waste trap has been vaccuumed - no debris remaining (include photos)
checkpoint | Bathroom/s floorwaste trap has been vaccuumed - no debris remaining (include photos)
checkpoint | Laundry floorwaste trap has been vaccuumed - no debris remaining (include photos)
checkpoint | All grates have been resecured to each waste
checklist | Fit Off/ Fixture Install - Wall Tundish | [5 empty] | Amenities - Fit Off/ Fixture Install - Wall Tundish
section | Details
checkpoint-no-status | ITP/Checklist for fit off of laundry in wall tundish (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Tundish has been installed aligned, level and secure
checkpoint | Trap connection is clear of debris
checkpoint | Fixture has been left covered and protected and the area is clean
checklist | Fit Off/ Fixture Install - Hose Taps | [5 empty] | Amenities - Fit Off/ Fixture Install - Hose Taps
section | Details
checkpoint-no-status | ITP/Checklist for fit off of laundry hose taps (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage. Damaged fixtures do not get installed
checkpoint | Hose Taps have been installed aligned, level and secure
checkpoint | Backflow prevention device has been installed
checkpoint | Fixture has been left covered and protected and the area is clean
checklist | Fit Off/ Fixture Install - Gas Cooktop | [5 empty] | Amenities - Fit Off/ Fixture Install - Gas Cooktop
section | Details
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Fixture has been checked for damage and leaks. Damaged fixtures do not get installed
checkpoint | Cooktop has been installed aligned, level and secure
checkpoint | Surrounding wall material is fire rated and complies with manufacturer specs
checkpoint | Distance from cooktop flame to underside of overhead joinery/rangehood complies with manufacturer specs
checkpoint | Isolation valve has been installed
checkpoint | Gas regulator has been installed
checkpoint | Flexible connections are correct with no twisting or kinks
checkpoint | Full visual inspection undertaken and all required elements having been installed
checkpoint | Fixture has been left covered and protected and the area is clean
checklist | Fit Off/ Fixture Install - Cleaners Sink | [5 empty] | Amenities - Fit Off/ Fixture Install - Cleaners Sink
section | Details
checkpoint-no-status | ITP/Checklist for fit off of cleaners sink (this is not a commissioning ITP)
checkpoint | Installation complies with current IFC shop drawings & AS/NZS 3500 (2021)
checkpoint | Installation materials used in accordance with manufacturer requirements
checkpoint | Sink & tapware has been checked for damage. Damaged fixtures do not get installed
checkpoint | sink & taps have been installed aligned, level and secure
checkpoint | Trap connection is clear of debris
checkpoint | Fixture has been left covered and protected and the area is clean
checklist | Testing - Potable Water - 1500kpa water test (not an air test) | [5 empty] | Amenities - Testing - Potable Water - 1500kpa water test (not an air test)
section | Details
checkpoint-no-status | ITP/Checklist for undertaking a hydrostatic test at 1500kPa
checkpoint | Water test is being conducted on material that is rated to withstand 1500kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 1500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist | Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test) | [5 empty] | Amenities - Testing - Potable Water - 500kpa water test pressure sensitive valves (not an air test)
section | Details
checkpoint-no-status | ITP/Checklist for undertaking a hydrostatic test to 500kPa to accommodate pressure sensitive fittings
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to 500kpa with the water feed shut off and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist | Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test) | [5 empty] | Amenities - Testing - Potable Water - 1500kpa Bump Test Couta Fittings (not an air test)
section | Details
checkpoint-no-status | ITP/Checklist for undertaking a bump test on Couta WaterPex fittings to meet manufacturer's guidelines
checkpoint | Pressure sensitive valves have been removed from test section (Note: this test will damage pressure sensitive fittings)
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Pressure was slowly increased to 1500kpa and held for 2 minutes
checkpoint | Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa for a further 2 minutes.
checkpoint | The previous step has been repeated: Pressure was decreased to 1000kpa and held for 20secs, then immediately and rapidly the pressure was increased back to 1500kpa and held for 30minutes.
textbox | Pressure reading photos must be taken at start & finish of 30minutes test. Add in comments (test duration etc)
checklist | Testing - Natural Gas | [5 empty] | Amenities - Testing - Natural Gas
section | Details
checkpoint-no-status | ITP/Checklist for air test on fittings to meet manufacturer's guidelines
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends are securely capped off
checkpoint | Feeder valve was slowly opened & the test zone has filled with air until completely purged
checkpoint | Pressure testing device was connected to the nominated test point
checkpoint | Pressure testing device is calibrated
checkpoint | Test must be undertaken to pressure of 7kPa OR 1.5 times the operating/working pressure whichever is greater (eg 3.5 kPa working pressure = 8.75 kPa testing pressure)
checkpoint | Testing was deemed successful if the pressure remains unchanged for 5 mins of every 30 litres volume of pipe
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist | Testing Potable Water - (1.5 times maximum working pressure) | [5 empty] | Amenities - Testing Potable Water - (1.5 times maximum working pressure)
section | Details
checkpoint-no-status | ITP/Checklist for water test on fittings that can not be tested to 1500 kPa as per manufacturer's guidelines
checkpoint | Water test is being conducted on material that is rated to withstand BELOW 1500kpa
checkpoint | All valves dedicated to isolating the test zone have been securely shut off & tagged
checkpoint | Air purging valve point has been nominated
checkpoint | Pressure testing valve point has been nominated (if none at meter manifold)
checkpoint | Ensure isolating valves within the test zone are open as required
checkpoint | All terminal open ends i.e. lugged elbows, etc are securely capped off
checkpoint | All in-wall mixer assemblies & pressure sensitive meters, etc have been isolated/removed from the test zone (these items are only rated to max 500kpa)
checkpoint | Feeder valve was slowly opened & the test zone has filled with water until completely purged of any air
checkpoint | Electric pressure testing pump device was connected to the nominated test point
checkpoint | Electric pressure testing pump is calibrated
checkpoint | Test consisted of slowly increasing the pressure to one a half times the working pressure and the pressure held for not less than 30mins
checkpoint | Pressure in the testing area was slowly reduced back to neutral working conditions
textbox | Pressure reading photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist | Testing - Water Hold - Sewer & Stormwater Underslung | [5 empty] | Amenities - Testing - Water Hold - Sewer & Stormwater Underslung
section | Details
checkpoint-no-status | ITP/Checklist for water hold test of underslung sewer & stormwater drainage
checkpoint | Pipe has been checked and is clear of blockage
checkpoint | Pipe work is securely clipped and ready to hold water
checkpoint | Open ends have been sealed
checkpoint | Test was conducted from stack riser 1m above the highest overflow point
checkpoint | Test was successful as it held water at an unchanged level for at least 30mins
checkpoint | Water was drained from the pipe at the end of the test
textbox | Water level photos must be taken at start & finish of test. Add in comments (test duration etc)
checklist | Testing - Air Test - Stormwater & Downpipe | [5 empty] | Amenities - Testing - Air Test - Stormwater & Downpipe
section | Details
checkpoint-no-status | Test Phase (stormwater)
checkpoint | The stormwater drainage pipe has been filled with air as per section 9.4.2 of AS3500.3.2021
checkpoint | Pressure of 30 kPa has been applied to the drain and maintained at this pressure for 3mins (with compressor remaining operational for air temp to stablize)
checkpoint | Compressor was shut off and the time taken for the pressure to drop from 25 kPa to 20 kPa was greater than 90sec for DN 225 or smaller (or 180secs for DN 300 or DN 375)
textbox | Start of test: Note start time and include photo of calibrated gauge at the start of 90sec (or 180sec) test
textbox | End of test: Note end time and include photo of photo of calibrated gauge at the end of 90sec (or 180sec) test
checkpoint | The test has been deemed successful
checkpoint-no-status | Test Phase (for downpipe)
checkpoint | The internal downpipe been filled with air as per section 9.3.1 of AS3500.3.2021
checkpoint | Pressure of 30 kPa has been applied to the drain and maintained at this pressure for not less than 3mins
textbox | Start of test: Note start time and include photo of calibrated gauge at the start of 3min test
textbox | End of test: Note end time and include photo of calibrated gauge at the end of 3min test
checkpoint | The test has been deemed successful
checklist | Testing - Air Test - Sewer | [5 empty] | Amenities - Testing - Air Test - Sewer
section | Details
checkpoint-no-status | Test Phase
checkpoint | The sewer drainage pipe has been filled with air as per section 15.3 of AS3500.2.2021
checkpoint | Pressure of approx 15 kPa has been applied to the drain. When approx 15 kPa has been reached, the compressor has been shut off
checkpoint | Air pressure has been stablised for not less than 3 min while checking for leaks
checkpoint | After the pressure has stablised, commence the test when the pressure has fallen to 10 kPa
checkpoint | Record the time and drop in pressure over the minimum test duration depending on pipe size (eg, 100DN = 2min test)
textbox | Start of test: Note start time and include photo of include photo of calibrated gauge at the start of test
textbox | End of test: Note end time and include photo of include photo of calibrated gauge at the end of test
checkpoint | The test has been deemed successful if the pressure does not drop more than 3 kPa over the test duration
checklist | Plant & Equipment Install - Hot Water Plant | [5 empty] | Amenities - Plant & Equipment Install - Hot Water Plant
section | Details
checkpoint | Hot water plant has been installed as per IFC drawings
checkpoint | Testing of all supply lines upto the hot water plant have been undertaken
checkpoint | All pumps have been installed
checkpoint | Hot water plant is ready for commissioning by supplier/manufacturer
checkpoint | Photos of installed hot water plant have been included
checklist | Plant & Equipment Install - Cold Water Pumpset | [5 empty] | Amenities - Plant & Equipment Install - Cold Water Pumpset
section | Details
checkpoint | Cold water pumpset has been installed as per IFC drawings
checkpoint | Testing of all supply lines have been undertaken
checkpoint | Cold water pumpset is ready for commissioning by supplier/manufacturer
checkpoint | Photos of installed cold water pumpset have been included
checklist | Plant & Equipment Install - Sewer Pumpwell/s | [5 empty] | Amenities - Plant & Equipment Install - Sewer Pumpwell/s
section | Details
checkpoint | Sewer pumpwell/s has been installed as per IFC drawings
checkpoint | Testing of all pumplines have been undertaken
checkpoint | Pumpwell lid has been lifted and all formwork has been stripped
checkpoint | Rails and lifting chains are in place
checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint | Sewer pumpwell is ready for commissioning by supplier/manufacturer
checklist | Plant & Equipment Install - Stormwater Pumpwell/s | [5 empty] | Amenities - Plant & Equipment Install - Stormwater Pumpwell/s
section | Details
checkpoint | Stormwater pumpwell/s has been installed as per IFC drawings
checkpoint | Testing of all pumplines has been undertaken
checkpoint | Pumpwell lid has been lifted and all formwork has been stripped
checkpoint | Rails and lifting chains are in place
checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint | Stormwater pumpwell is ready for commissioning by supplier/manufacturer
checkpoint | Pumpwell lid has been resecured and lid fixings resecured
checklist | Plant & Equipment Install - Stormwater Treatment System/Filter | [5 empty] | Amenities - Plant & Equipment Install - Stormwater Treatment System/Filter
section | Details
checkpoint | Stormwater treatment system/filter has been installed as per IFC drawings
checkpoint | Testing of all supply lines has been undertaken
checkpoint | Filter lid has been lifted and all formwork has been stripped
checkpoint | Rails and lifting chains are in place
textbox | Stormwater treatment system/filter is generally a SPEL/ Gross Pollutant Trap/First Flush/Rain Garden
checkpoint | Stormwater treatment/filter is ready for commissioning by supplier/manufacturer
checkpoint | Pumpwell lid has been resecured and lid fixings resecured
checklist | Plant & Equipment Install - Rainwater Tank | [5 empty] | Amenities - Plant & Equipment Install - Rainwater Tank
section | Details
checkpoint | Rainwater tank has been installed as per IFC drawings
checkpoint | Testing of all pumplines has been undertaken
checkpoint | If underground, tank lid has been lifted and all formwork has been stripped
checkpoint | Flow control valve (eg Bermad) has been installed and is watermarked
checkpoint | Ensure float connection is secure and will be part of the commissioning by supplier (note, if the float comes off, it will lead to overfow issues)
checkpoint | Overflow is positioned 50mm above highest float setting (this is critical)
checkpoint | There is a physical air break from the tank-fill pipe height to the height of the overflow
checkpoint | Float is connected to the diversion valve
checkpoint | Correct specification of pump/s have been delivered and are ready for a pre-priming the day prior to commissioning
checkpoint | Rainwater tank & pump is ready for commissioning by supplier/manufacturer
checkpoint | Lid has been resecured and lid fixings resecured
checklist | Plant & Equipment Install - Water Storage Tank | [5 empty] | Amenities - Plant & Equipment Install - Water Storage Tank
section | Details
checkpoint | Water storage tank has been installed as per IFC drawings
checkpoint | Testing of all supply lines to tank has been undertaken to the furtherest point possible pre commissioning
checkpoint | Flow control valve (eg Bermad) has been installed and is watermarked
checkpoint | Ensure float connection is secure and to be part of commissioning at a later date (note, if the float comes off, it will lead to overfow issues)
checkpoint | Overflow is positioned 50mm above highest float setting (this is critical)
checkpoint | There is a physical air break from the tank-fill pipe height to the height of the overflow
checkpoint | If specified, tank level probes have been installed
checkpoint | If specified, provision for BMS connection
checkpoint | Access ladder is installed with lock on top of the tank access panel
checkpoint | Statutory warning signage is visible
checklist | Plant & Equipment Install - GIT | [5 empty] | Amenities - Plant & Equipment Install - GIT
section | Details
checkpoint | GIT has been installed as per IFC drawings
checkpoint | Testing of all suction lines have been undertaken
checkpoint | GIT lid has been lifted and all formwork has been stripped
checkpoint | Camlocks cap have bene fitted off
checkpoint | Drop pipe installed inside tank
checkpoint | Lid has been resecured and lid fixings resecured
checklist | Plant & Equipment Install - Diversion Valve | [5 empty] | Amenities - Plant & Equipment Install - Diversion Valve
section | Details
checkpoint | Diversion valve has been installed as per IFC drawings and as per MPS Design instructions
checkpoint | Connection to panel board is ready for commissioning
checkpoint | Ensure diversion valve is installed as close as possible to the diversion point to ensure debris is diverted out to the street
checkpoint | Diversion valve is ready for commissioning by supplier/manufacturer
checklist | Plant & Equipment Install - Rainwater Filtration System | [5 empty] | Amenities - Plant & Equipment Install - Rainwater Filtration System
section | Details
checkpoint | Rrainwater treatment system/filter has been installed as per IFC drawings
checkpoint | Testing of all supply lines has been undertaken
checkpoint | Rainwater treatment/filter is ready for commissioning by supplier/manufacturer
checkpoint | If specified, provision for BMS connection
checklist | Comm/HO - TMV | [5 empty] | Amenities - Comm/HO - TMV
section | Details
checkpoint-no-status | ITP/Checklist for commissioning TMV and temp testing each tap/mixer
textbox | Hot water delivery time from cold to stable hot to be logged |  |  | secs
textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | Test has been conducted to fully isolate CW supply to demonstrate HW is not delivered through TMV
checkpoint | System has been returned to working conditions
textbox | Temp and Time reading photos from each fitting must be taken at start & finish of test
checklist | Comm/HO - Tempering Valve | [5 empty] | Amenities - Comm/HO - Tempering Valve
section | Details
checkpoint-no-status | ITP/Checklist for commissioning Tempering valve and temp testing each tap/mixer
textbox | Hot water delivery time from cold to stable hot to be logged |  |  | secs
textbox | Hot water delivery temperature to be logged |  |  | degrees
checkpoint | System has been returned to working conditions
textbox | Temp and Time reading photos from each fitting must be taken at start & finish of test
checklist | Comm/HO - Apartment Final Commissioning - Fixture Group | [5 empty] | Amenities - Comm/HO - Apartment Final Commissioning - Fixture Group
section | Details
checkpoint-no-status | ITP/Checklist for final commissioning of all installed fixtures
checkpoint-no-status | Bathroom/WC Area
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery does not exceed 50degC on any fixtures
checkpoint | For SDA or DDA areas only, hot water delivery does not exceed 45degC on any fixtures
checkpoint | WC toilet seat and lid secured and fastened with soft close function operating
checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint | Wet area grated outlets are installed correctly
checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status | Laundry Area
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Mini stops/trivalve have been securely capped for future washing machine connection by others
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery does not exceed 65degC
checkpoint | Trough tap has been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint | Trough tap has been tested for any evidence of water hammer
checkpoint | Wet area grated outlets are installed correctly
checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status | Kitchen
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Pullout mixer function has been checked and has clear
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint | All fixtures have been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint | Dishwasher has been run through a short cycle
checkpoint-no-status | Kitchen - Gas
checkpoint | Gas appliance connections have been checked for any damage or leaks
checkpoint | Gas valves & regulator flow direction have been checked
checkpoint | All gas burners function correctly and consistently
checkpoint | Check balcony hose tap & NRV are installed correctly
checkpoint | Check balcony floor grate & downpipe are installed correctly
checklist | Comm/HO - Commercial Final Commissioning - Fixture Group | [5 empty] | Amenities - Comm/HO - Commercial Final Commissioning - Fixture Group
section | Details
checkpoint-no-status | ITP/Checklist for final commissioning of all installed fixtures
checkpoint-no-status | Bathroom/WC Area
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery does not exceed 50degC on any fixtures
checkpoint | For SDA or DDA areas only, hot water delivery does not exceed 45degC on any fixtures
checkpoint | WC toilet seat and lid secured and fastened with soft close function operating
checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint | Wet area grated outlets are installed correctly
checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status | Cleaners Sink
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint | All fixtures have been run, sinks plugged for water hold test, and under sink traps checked for any evidence of leaking
checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint | Wet area grated outlets are installed correctly
checkpoint | A visual inspection to ensure all traps & wastes are clear of debris
checkpoint-no-status | Kitchen
checkpoint | Final check for cross connection for all fixtures has occurred
checkpoint | All cover plates & mixer handles are securely fastened and defect free
checkpoint | Pullout mixer function has been checked and has clear
checkpoint | Water pressure has been tested and hot & cold water through all fixtures do not exceed 500kPa
checkpoint | Hot water delivery in the kitchen does not exceed 65degC
checkpoint | All fixtures have been run, sink plugged for water hold test, and under sink trap checked for any evidence of leaking
checkpoint | All fixtures have been tested for any evidence of water hammer
checkpoint | Dishwasher has been run through a short cycle
checklist | FINAL Commissioning - Hot Water Plant | [5 empty] | Amenities - FINAL Commissioning - Hot Water Plant
section | Details
checkpoint | Hot water plant commissioning report to be uploaded here
checkpoint | Hot water plant final install photos to be uploaded here (show temperature on plant setting)
checklist | FINAL Commissioning - Cold Water Pumpset | [5 empty] | Amenities - FINAL Commissioning - Cold Water Pumpset
section | Details
checkpoint | Cold water pumpset commissioning report to be uploaded here
textbox | Cold water pumpset has been commissioned to achieve a set working pressure of |  |  | kPa
checkpoint | Cold Water pumpset final install photos to be uploaded here (show connection to active board)
checklist | FINAL Commissioning - Sewer Pumpwell/s | [5 empty] | Amenities - FINAL Commissioning - Sewer Pumpwell/s
section | Details
checkpoint | Sewer pumpwell/s commissioning report/s to be uploaded here
checkpoint | Sewer pumpwell final install photos to be uploaded here (show connection to active board)
checklist | FINAL Commissioning - Stormwater Pumpwell/s | [5 empty] | Amenities - FINAL Commissioning - Stormwater Pumpwell/s
section | Details
checkpoint | Stormwater pumpwell/s commissioning report/s to be uploaded here
checkpoint | Stormwater pumpwell final install photos to be uploaded here (show connection to active board)
checklist | FINAL Commissioning - Stormwater Treatment System/Filter | [5 empty] | Amenities - FINAL Commissioning - Stormwater Treatment System/Filter
section | Details
checkpoint | Stormwater treatment system/ filter commissioning report/s to be uploaded here
checklist | FINAL Commissioning - GIT | [5 empty] | Amenities - FINAL Commissioning - GIT
section | Details
checkpoint | Plant & Equipment Installation checked off as below
label | Add Comments &/or Photos below as applicable
label | Installer is a Registered Plumber (VIC) with endorsements for this work
button | Installation complies with current AS/NZS-3500 (2018) | Yes,No,N/A
button | Installation complies with current drawings & specifications | Yes,No,N/A
button | Installation materials were used in accordance with manufacturer requirements | Yes,No,N/A
button | Check for damage or leaks | Yes,No,N/A
button | Check plant/equipment is level & aligned correctly | Yes,No,N/A
button | Check connecting pipework levels & alignment are correct | Yes,No,N/A
button | Check control panels are accessible | Yes,No,N/A
button | Check maintenance hatches are accessible | Yes,No,N/A
button | Check access ladders are installed | Yes,No,N/A
button | Check filter cartridge containers are accessible | Yes,No,N/A
button | Check all wiring or pneumatic lines have been installed correctly | Yes,No,N/A
button | Check all fixings & anchor points are installed & torqued correctly | Yes,No,N/A
button | Check pressure relief or back-wash pipes discharge to a dedicated drain point | Yes,No,N/A
button | Check pressure/temperature gauges are visible | Yes,No,N/A
button | Check isolation & non-return valves are installed correctly & flow direction is correct | Yes,No,N/A
button | Check all vent & breather pipes are installed correctly | Yes,No,N/A
button | Check gas flues & power manifolds are installed to regulation | Yes,No,N/A
button | Check protective covering is installed & area has been left clean | Yes,No,N/A
checklist | FINAL Commissioning - Diversion Valve | [5 empty] | Amenities - FINAL Commissioning - Diversion Valve
section | Details
checkpoint | Diversion Valve commissioning report to be uploaded here