## Sheet1
Jensen Steel Fabricators LTD |  | INSPECTION AND TEST PLAN (ITP) | [11 empty] | OP021 |  |  | Rev: 6
AS/NZS 5131 CC4 | [13 empty] | Approved: LT |  |  | Date: 23.12.2021
Jensen Steel Fabricators Quality Assurance Inspection and Test Plan
Client | Fletcher Building Products Limited
Project Name | Project Burgundy
JSF Project No. | 20464
Test Plan | Materials, Assembly, Welding, Inspection and Testing, NDT, Protective Coatings and Erection Documentation
Prepared By | Luke Te Whau | [9 empty] | Date | 01.06.2024
Reference Codes and Specification | [8 empty] | Reference/ Verifying Documents
REF |  | No. | Title | [5 empty] | Doc # / ref. |  |  | Symbol |  | Description
J6041 |  | SGCE | Project Specification | [5 empty] | JSF QM | Quality Manual |  | H | = | Hold Point
AS/NZS Standard |  | AS/NZS 3404 | Steel Structure Standard | [5 empty] | SGS CBIP Website | NDT Personnel Qualification and Certificate |  | W | = | Witness Point
AS/NZS Standard |  | AS/NZS 1554.1 | Welding of steel structures | [5 empty] | OP001 | Technical Review |  | I | = | Inspection
AS/NZS Standard |  | AS/NZS 3678 | Structural steel - Hot rolled plates, floor plates and slabs | [5 empty] | AP 003 | QC Organization chart |  | R | = | Review
AS/NZS Standard |  | AS/NZS 3679-1 | Structural steel - Hot rolled and sections | [5 empty] | QAP | Third Party Inspection Company |  | A | = | Approval
AS/NZS Standard |  | AS/NZS 3679-2 | Structural steel - Welded I section | [5 empty] | SF006 | Visual Testing Procedure |  | V | = | Visual
AS/NZS Standard |  | AS/NZS 1252 | High-Strength bolts with associated nuts and washers for structural engineering | [5 empty] | OP21 | Inspection and Test plan |  | S | = | Submission
AS/NZS Standard |  | AS/NZS 2312 | Guide to the protection of structural steel against atmospheric corrosion by the use of protective coatings | [5 empty] | OP22 | Fabrication Procedure |  | D | = | Document
AS/NZS Standard |  | AS/NZS 2207 | Non-destructive testing - Ultrasonic testing of fusion welded joints in carbon and low alloy steel | [5 empty] | OP22 | Handling, Storage, Packing and Delivery Procedure |  | N | = | NDT (Non-destructive Testing)
AS/NZS Standard |  | AS/NZS 1171 | Non-destructive testing - Magnetic particle testing of ferromagnetic products, components and structures | [5 empty] | DPIR (Daily Paint Inspection Report) | Surface Preparation and Painting Procedure |  | QAM | = | Quality Assurance Manager
AS/NZS Standard |  | AS/NZS 2980 | Qualification of welder for fusion welding of steel | [5 empty] | OP002 | Material Control Procedure |  | DE | = | Design Engineer
AS/NZS Standard |  | AS/NZS 5131 | Structural Steelwork Fabrication and Erection | [8 empty] | FWI | = | JSF Fab and Weld Inspector
ISO Standard |  | ISO 3834.2 | Quality requirements for fusion welding of metallic materials | [8 empty] | SGS | = | Independant Welding Inspector
ISO Standard |  | ISO 9606.1 | Qualification testing of welds - fusion welding | [8 empty] | C | = | Client
[12 empty] | M | = | Monitor
[12 empty] | O | = | Owner
Jensen Steel Fabricators LTD |  | INSPECTION AND TEST PLAN (ITP) | [11 empty] | OP021 |  |  | Rev: 6
AS/NZS 5131 CC4 | [13 empty] | Approved: LT |  |  | Date: 23.12.2021
Item | Process Description and Quality Control Activity |  | Inspection Activity |  |  |  | Inspected by | Acceptance Criteria |  |  |  | Surveillance Inspection |  |  |  |  | Remark
|  |  | V | D | N | R
[8 empty] | Document | Clause | Reference Standard | Verifying Document | Frequency | Jensen | Client | Owner | SG/CPI
1 | PRE-INSPECTION MEETING
1.1 | Shop drawing review |  |  |  |  | x | C |  |  | Project specification | Shop drawings approved for Construction by Engineer | - | S | H/A | -
1.2 | Discuss the implementation of the quality requirement and to ensure that all requirements of Contract are understood |  |  |  |  | x | C |  |  | Project Specification | QAP, ITP Accepted by Client | - | - | H/A | - | -
2 | PROCEDURE AND DOCUMENTS
2.1 | Review/Approve quality assurance plan |  |  |  |  | x | DE |  |  | AS/NZS 5131 | QAP | - | - | H/A | - | R
2.2 | Review/Approve welding plan |  |  |  |  | x | DE |  |  | AS/NZS 5131 | OP030 | - | - | H/A | - | R
2.3 | Review/Approve WPS, PQR |  |  |  |  | x | DE |  |  | AS/NZS1554.1 | WPS | - | - | H/A | - | R
2.4 | Review/Approve Welder qualification test records |  |  |  |  | x | DE |  |  | AS/NZS2980 / ISO 9606.1 | PQR | - | - | H/A | - | R
2.5 | Review/Approve NDE personnel certificate |  |  |  |  | x | DE |  |  | AS/NZS 5131 | AS2214 Welding Supervisor Certificates, CBIP Website | - | - | H/A | - | R
2.6 | Paint System Approval |  |  |  |  | x | DE |  |  | AS/NZS 2312 |  | - | H | R | -
3 | MATERIALS
3.1 | Verify mill certificate and heat marking records both physical marking of material and traceability database record |  |  | x |  | x | QAM | AS/NZS 5131 | Section 5 | AS/NZS 3679-1, AS/NZS 3678, AS/NZS 4600 | Mill certificates, cutting schedule sheets | Monthly | H | - | - | -
3.2 | Inspect all material for any damage |  | x |  |  |  | QAM | AS/NZS 5131 | Section 6 | AS/NZS 3679-1, AS/NZS 3678, AS/NZS 4600 | Mill certificates, cutting schedule sheets | Daily | H | - | -
3.3 | Review mill certificate in accordance with the requirements of project specifications |  |  |  |  | x | QAM |  |  | AS/NZS 3679-1, AS/NZS 3678, AS/NZS 4600 | Mill certificates | Monthly | H | R | R | R
3.4 | Review hardware certificate (Bolt, Nut and Washer) meet specification ( for Grade 8.8 UNO) |  |  |  |  | x | QAM |  |  | AS/NZS 1252 / AS/NZS 1214 | Mill certificates | Monthly | H | R | - | R
4 | MATERIAL PREPARATION
4.1 | Check identification marking on work piece for material traceability |  | x |  |  |  | QAM/FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | Shop drawing, Cutting schedule sheets, Weld Check Summary sheets | Daily | I | - | - | -
4.2 | Check edge preparation in accordance with shop drawing and WPS |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | Shop drawing, Cutting schedule sheets, Weld Check Summary sheets | Daily | I | - | - | -
4.3 | Check surface cutting profile/ gas notch |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | Shop drawing, Cutting schedule sheets, Weld Check Summary sheets | Daily | I | - | - | -
4.4 | Machined and sheared edge preparations and drilled hole shall be debarred |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | Shop drawing, Cutting schedule sheets, Weld Check Summary sheets | Daily | I | - | - | -
5 | ASSEMBLY
5.1 | Check overall pre-weld dimension |  |  | x |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS1554.1, AS/NZS 5131, WPS | Shop drawings, Weld Check Summary sheets | Daily | I | M | M | -
5.2 | Check weld joint cleanliness |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS1554.1, AS/NZS 5131, WPS | Shop drawings, Weld Check Summary sheets | Daily | I | M | M | -
5.3 | Arc strikes outside the area of permanent weld shall be ground smooth and visually inspected |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS1554.1, AS/NZS 5131, WPS | Shop drawings, Weld Check Summary sheets | Daily | I | M | M | -
5.4 | Run-off tabs/Backing bar shall be used on all SAW process |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS1554.1, AS/NZS 5131, WPS | Shop drawings, Weld Check Summary sheets | Daily | I | M | M | -
6 | WELDING
6.1 | Check welder qualification and validity |  |  |  |  | x | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | WPS, Weld Check Summary sheets | Daily | I | M | M | -
6.2 | Monitor electrode storage & useage |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | WPS, Weld Check Summary sheets | Daily | I | M | M | -
6.2 | Monitor electrode storage & useage |  | x |  |  |  | FWI | Shipping class 3YS minimum | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | WPS, Weld Check Summary sheets | Daily | I | M | M
6.3 | Monitor preheating as per WPS |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | WPS, Weld Check Summary sheets | Daily | I | M | M | -
6.4 | Monitor welding sequence, parameter, Interpass temperature |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131, WPS | WPS, Weld Check Summary sheets | Daily | I | M | M | -
7 | POST WELD INSPECTION
7.1 | Check weld profile/ weld contour is in accordance with specification |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
7.2 | Check weld leg, size and length is in accordance with drawing |  | x |  |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
7.3 | Check overall dimension in accordance with drawing |  |  | x |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
7.4 | Check maximum sweep |  |  | x |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
7.5 | Check maximum camber |  |  | x |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
7.6 | Check hole size per drawing |  |  | x |  |  | FWI | AS/NZS 5131 | Section 6 | AS/NZS 1554.1, AS/NZS 5131 | Weld Check Summary sheets | Daily | I | M | M | -
8 | NON-DESTRUCTIVE TESTING (NDT)
8.1 | 100% Visual scaning all weld and examination of all SP weld |  | x |  |  |  | FWI |  |  | AS 3978 sec 10, AS/NZS 1554.1 Table 6.2.2 | Weld Check Summary sheets | Daily | I / D | - | - | -
8.2 | 5-10 % UT for SP butt welds |  |  |  | x |  | FWI |  |  | AS/NZS 1554.1 Table 6.2.1, AS 2207 | UT Reports | Daily | I / D | - | - | -
8.3 | 5% Magnetic particle for SP fillet weld in Seismic areas Noted : Reduced in inspection frequency, if no non-conformances found |  |  |  | x |  | SGS |  |  | AS/NZS 1554.1 Table 6.2.2, AS 1171 | NDT Reports | Daily | I / D | - | -
8.4 | If lack of fusion or cracking is suspected, carry out Magnetic particle testing |  |  |  | x |  | FWI / SGS |  |  | AS/NZS 1554.1 Table 6.2.2, AS 1171 | Weld Check Summary sheets | Daily | I / D | - | - | -
9 | SURFACE PREPARATION AND PAINTING
9.1 | Storage of Paint products |  |  |  |  | x | QAM |  |  | Manufacturers Instructions | Paintstore Register | Daily | I/D | M | M
9.2 | Monitor environment for coating application |  |  |  |  | x | QAM |  |  | Project Specification, AS/NZS 2312, AS/NZS 5131, AS 3894 | Daily Paint Inspection Reports | Weekly | I/D | M | M | -
9.3 | Surface preparation shall be in accordance to AS 1267.4 Class 2.5 |  | x |  |  |  | QAM |  |  | Project Specification, AS/NZS 2312, AS/NZS 5131, AS 3894 | Daily Paint Inspection Reports | Weekly | I/D | M | M | -
9.4 | Check dry film thickness and visual appearance check for coating |  | x |  |  |  | QAM |  |  | Project Specification, AS/NZS 2312, AS/NZS 5131, AS 3894 | Daily Paint Inspection Reports | Weekly | I/D | M | M | -
9.5 | Manufacturer Inspections |  | x | x |  |  | Nace Level 2 Inspector |  |  | Project Specification, AS/NZS 2312, AS/NZS 5131, AS 3894 | Paint Inspection Reports | As Required | I/D | M | M |  | Note this section does not cover the intumescent test plan. This is still to be confirmed with Fosters/ JSF
10 | Installation - Onsite
10.1 | Delivery of materials |  | x | X |  |  | QAM |  |  | AS/NZS 5131 | Delivery dockets | As Required | I/D | - | - | -
10.2 | Bolting procedures. As per JSF High Strength Bolting SOP. All Snug bolts to be marked with an "X" on end of bolt once Snug tensioned. |  |  | x |  |  | QAM / C |  |  | AS/NZS 5131 | Conqa Site Structural and Bolting reports | As Required | I/D | I/M | I/M | -
10.3 | Screws, bolts & nuts to be Grade 8.8 unless otherwise stated. |  |  | x |  |  | QAM |  |  | AS/NZS 5131 | Conqa Site Structural and Bolting reports | As Required | I/D | - | - | -
10.4 | Erection -Tolerances |  |  | x |  |  | QAM |  |  | AS/NZS 5131 | Conqa Site Structural and Bolting reports | As Required | I/D | R | M | -
10.5 | Paint touch-up |  | x |  |  |  | QAM |  |  | AS/NZS 5131/2312 | Conqa Site Structural and Bolting reports | As Required | I/D | W | M | -
10.6 | Final inspection |  | x |  |  |  | QAM |  |  | AS/NZS 5131 | Conqa Site Structural and Bolting reports | As Required | I/D | W | M | -
11 | FINAL INSPECTION AND DOCUMENTATION
11.1 | General visual inspection of completed Project/Phases |  | x |  |  |  | QAM |  |  | Project Specification | Conqa Site Structural and Bolting reports | As Required | I/D | W | M | -
11.2 | Submit Quality Documentation |  |  |  |  | x | QAM |  |  | Project Specification | QA Pack for Client | As Required | D | R | R | -
11.3 | Complete Producer Statement |  |  |  |  | x | QAM |  |  | Project Specification | PS3 | As Required | D | R | R | - | After project/phase completion