## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 46694R309 - ITP - LEVEL 05 - Installation of RIS Access Hatch | itp |  |  |  |  | 46694R309 - ITP - LEVEL 05 - Installation of RIS Access Hatch
section | INSPECTION TEST PLAN
checkpoint | Access point location(s)
label | CHARACTERISTICS - AS5532 7.3 (h) AS1891.4 3.2.2
label | STAGE/FREQUENCY - Prestart installation work
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Manufacturer recommendation
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Safe transition to roof
label | CHARACTERISTICS - AS1891.6.2.2, (e ) Other selection criteria AS1657 4.8.3
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Access hatch connection to the structure
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Access hatch Location
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Transfer sling location
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Transfer anchor location
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Number of fixings, location of fixings and location of supports and specific bracing
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Prevention of corrosion
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Product marking and signage
label | CHARACTERISTICS - RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - x
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Instructions for general use
label | CHARACTERISTICS - AS1891.2 1.4 System Acceptance Criteria a. AS/NZS 1891.4.2009 Section (9). RIS Access Hatch Installation Requirement
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Manufacturer recommendations
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Visual
label | INSTALL SUPERVISOR - H
label | CLIENT - H
holdpoint | HOLD POINT
section | CHECKLIST - Installation (Refer to Installation Instructions)
checkpoint | Access point location(s)
label | REFERENCE - Systems can be accessed safely by trained persons without the risk of an uncontrolled fall.
checkpoint | Safe transition to roof
label | REFERENCE - Access hatches that use ladders have provision for opening and closing the roof access hatch with the use of one hand.
checkpoint | Access hatch location
label | REFERENCE - Access hatch opens away from the fall position or includes handrails to any fall zone on a pitched roof, or, when within 2m of a roof or structural edge.
checkpoint | Hatch handrails
label | REFERENCE - Handrails to the hatch on the top side are located on three sides with grab rails incorporated into the design.
bool | Tick if is not applicable
checkpoint | Hatch transfer strop location
label | REFERENCE - Strop must be positioned to enable user to reach and connect without falling and position themselves in restraint to a safe location on the roof without a risk of falling.
bool | Tick if is not applicable
checkpoint | Operational safety
label | REFERENCE - Where a hatch has a pinch point handling position, the pinch points when opening or closing the hatch are marked with pinch point signage.
checkpoint | Number of fixings, location of fixings and location of line specific bracing
label | REFERENCE - Hatch is fixed to concrete structure with a minimum of 4 x M8 Hilti Dyna bolts OR a minimum of 4 x 4.8mm stainless rivets fixed to the upstand for roof sheet applications. Additional bracing is installed to prevent collapse of the hatch under a load. Back flashing has been installed for roof sheet applications.
label | COMMENTS - Not applicable if back flashing is completed by others.
checkpoint | Prevention of corrosion
label | REFERENCE - Dissimilar metals are not used or separated with EPDM, foam or tape.
checkpoint | Site clean up and picture evidence if handover is not possible
label | REFERENCE - Site has been cleared of swarf or other debris installation inspection completed and witnessed by the customers representative. Where a client cannot sign for handover, clear high resolution pictures have been taken of the installed product.
checkpoint | Systems Installation completion action
label | REFERENCE - Single user signage is installed in visible location.
section | Project Completion
checkpoint | Handover operating and systems documentation issued.
checkpoint | I have carried out all necessary inspections and verify that the above items/activities conform to the contract specification/documents
textbox | Name:
date | Date:
holdpoint | Signature:
checkpoint | I have carried out all necessary inspections and verify that the above work for this work area has been completed and conforms to the contract specification/documents
textbox | Name:
date | Date:
holdpoint | Signature: