## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | 46694R305 - ITP - LEVEL 05 - Installation of RIS Aluminium Ladders | itp |  |  |  |  | 46694R305 - ITP - LEVEL 05 - Installation of RIS Aluminium Ladders
section | INSPECTION TEST PLAN
checkpoint | Access point location(s)
label | CHARACTERISTICS - AS1657 J2.2, 5.4.1 & G5
label | STAGE/FREQUENCY - Prestart installation work
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALL SUPERVISOR - S
label | CLIENT - S
checkpoint | Labelling of Installation
label | CHARACTERISTICS - AS1657 8.2 Labelling of Installation
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Visual
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Material
label | CHARACTERISTICS - AS/NZS 1664.1 & AS/NZS 1664.2
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Visual
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Welding
label | CHARACTERISTICS - AS/NZS 1554.1, AS/NZS 1554.6 or AS/NZS 1665
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Visual
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Headroom
label | CHARACTERISTICS - AS1657 3.1.5
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Level access, change and slip resistance and footing
label | CHARACTERISTICS - AS1657 5.1.1, 3.1.4, 3.1.3 & 5.3.3
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Safety below the ladder
label | CHARACTERISTICS - AS1657 4.5 & 4.6
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Provision of a Barriers
label | CHARACTERISTICS - AS1657 5.4.1 c) i, ii, iii
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Installation Instruction followed
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Stability and structural capacity
label | CHARACTERISTICS - AS1657 7.1.2
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
checkpoint | Finished surfaces, height and hand clearance
label | CHARACTERISTICS - AS1657 5.6.1, 5.6.2 & 5.6.3
label | STAGE/FREQUENCY - On Installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Ladder Access and Egress
label | CHARACTERISTICS - AS1657 7.3.2, 7.3.3.2, 7.3.5 & 7.3.6
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Vertical Fall Arrest System
label | CHARACTERISTICS - AS1657 7.4.7
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Measurement
label | INSTALLER - H
label | INSTALL SUPERVISOR - S
label | CLIENT - S
holdpoint | HOLD POINT
checkpoint | Documentation to be supplied
label | CHARACTERISTICS - AS1657 8.3
label | STAGE/FREQUENCY - On installation
label | RECORDS - Checklist
label | REQUIREMENT/STANDARD/SPECIFICATION - Standard/Specification
label | ACCEPTANCE CRITERIA - Visual
label | INSPECTION/TEST PROCEDURE - Completion Handover
label | INSTALL SUPERVISOR - H
label | CLIENT - H
holdpoint | HOLD POINT
section | CHECKLIST - Installation (Refer to Installation Instructions)
checkpoint | Access point location(s)
label | REFERENCE - Systems can be accessed safely by trained persons without the risk of an uncontrolled fall.
checkpoint | Material and off site fabrication
label | REFERENCE - All materials installed are from tested and pre-fabricated RIS Stock.
checkpoint | Obstructions and Headroom
label | REFERENCE - Pathways to and from the ladder allow 2m of head clearance in proximity to the ladder systems installed.
label | ○ For an internal ladder that requires access through a hatch or other structure, the minimum distance from the stile of the step ladder to the roof or structure must not be less than 950mm.
checkpoint | Level access, change and slip resistance and footing
label | REFERENCE - The spacing between the resting point of the ladder and the first ladder rung is between 270 and 300mm.
label | ○ Top rung of the ladder is level with the exit landing.
label | ○ Maximum cross slope angle is no greater than 7 degrees and 3 degrees from the horizontal.
label | ○ Minimum foot clearance from the nose of each tread horizontally is 200mm.
checkpoint | Safety below the ladder platform
label | REFERENCE - Toe boarding or infill barrier is applied to areas that require direct access under the ladder landings, where people are exposed to dropped objects
checkpoint | Provision of a Barriers/Cage
label | REFERENCE - Cage starts between 2m and 2.2m above landing point and terminates 1m above step off point.
label | ○ The inside of the cage has no projections (protusions).
label | ○ The maximum opening size must be less than 150mm for vertical slats.
checkpoint | Stability and structural capacity
label | REFERENCE - Ladder fixing bracket is placed at the top rung of the ladder and then spaced at no more than 3m centres with 2 x M8 x 45mm stainless steel cup heads bolts to the ladder with flange and dome nuts. The support bracket fixings to the structure:
label | ○ Concrete: 3 x M8 Hilti HSA fixings or
label | ○ Steel work: 2 x M12 stainless bolts, or
label | ○ Roof sheeting: 5 x 8mm structural rivets, or
label | ○ Purlins: 2 x M12 ESL
label | Ladder base angle secured and bolted to substructure with 2 x M12 bolts or 3 x 8mm rivets.
label | To secure the ladder to the ladder base angle use 2 x M8 x 100mm stainless steel cup bolt with flange and dome nut. Ladder splice join is secured in the ladder frames 300mm either side of the join and riveted using 8 x 6.3mm aluminium rivets distributed evenly on each rung either side of the joint.
checkpoint | Finished surfaces, height and hand clearance
label | REFERENCE - Surfaces and finishes are free from sharp edges, burs and other unsafe conditions.
label | ○ Minimum 50mm clearance where they meet adjacent structures. The last rung on the ladder is level with landing surface.
checkpoint | Vertical Fall Arrest System
label | REFERENCE - Ladder is fitted with full length internal splice joiner bar from the top of the ladder to the ground on both sides of the ladder with the lifeline attachment point welded at the top of the ladder.
label | ○ The top ladder rung finishes level with the step of point, the base of the ladder is secured to the substructure at the bottom. The swagging tool is tested/calibrated within the last 12 months. Fork swage at top of ladder has 5 crimped swage marks within the first 85mm of the cable entering the fork fitting and the tensioner is at the base. All static line connection points are securely fitted.
checkpoint | Ladder Access and Egress
label | REFERENCE - Angled between 70 to 90 degrees with 75 degrees recommended.
label | ○ Landing platform is the same width as the ladder or 600mm whichever is the larger. The length of the landing at the step on/off point is 900mm long or greater.
label | ○ The vertical distance between the landings is 6m or less.
checkpoint | Site clean up and picture evidence if handover is not possible
label | REFERENCE - Site has been cleared of swarf or other debris installation inspection completed and witnessed by the customers representative. Where a client cannot sign for handover, clear high resolution pictures have been taken of the installed product.
checkpoint | Systems installation completion action
label | REFERENCE - Fit for use sticker/tag filled in and attached to the system, mark with confirmed rating. Entry point signage updated and installed.
section | Project Completion
checkpoint | Handover operating and systems documentation issued
checkpoint | I have carried out all necessary inspections and verify that the above items/activities conform to the contract specification/documents
textbox | Name:
date | Date:
holdpoint | Signature: