## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-055-CIV-CPD-Conduit & Pits-Rail (Supply & Install) | itp |  |  |  | Yes | ITP-055-CIV-CPD-Conduit & Pits-Rail (Supply & Install) - Rev 0
section | 1. Referenced Documentation
checkpoint-no-status | 1. Referenced Documentation
label | Document Title: ITP-055-CIV-CPD-Conduit & Pits-Rail (Supply & Install)
label | ITP Description: Conduit & Pits - Rail (Supply and Install)
label | Document Number (in Teambinder): MRP-0000-MRPA-ALT-ITP-00XX
label | Discipline (e.g. CIV/STR/RAIL): CIV
label | Revision Number: 0
label | Revision Date: 4/08/2023
label | ITP created by: Andrew Carlini
label | ITP approved for use by: Pradeep Talasila
checkpoint | 1.1 - Non Dependent
label | Reference - IFC Drawings L1-CHE-STD-043 (VRIOGS 012.2.1) L1-CHE-SPE-070 Australian Standards MRPA Standards
section | 2. Preliminaries - Materials
checkpoint | 2.1 - Conduits
label | Reference - HV Conduit: AS 2053, HV Conduit (boring): AS 4130, Comms Conduit: AS/ACIF S008:2006, LV Conduit: AS/NZS 3000 - 2000. L1-CHE-STD-043, L1-CHE-SPE-070
label | Acceptance Criteria - LV & Signalling: 100Ø (114mm OD), orange electrical heavy duty 5.9mm wall thickness
label | ○ LV & COMMS CONDUITS TO HAVE A MIN 600mm BENDING RADIUS
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.2 - Pits and Pit Lids
label | Reference - IFC Drawings VRIOGS 012.2.1 Section 6.15-16, VRIOGS 012.2.1 Section 6.9, VRIOGS 012.2.1 Cl.6.7 (c) L1-CHE-SPE-070 Cl.10 AS1289
label | Acceptance Criteria - Pits:
label | ○ Pits located within 1.5m of nearest rail, pit to be 300LA Railway loading
label | ○ Pits 900x900mm or greater, multipart pits lids to be used.
label | Pit Lids:
label | ○ Pit Covers shall comply with AS3996-2006
label | ○ Pit lids in trafficable areas to be Class D, non-trafficable areas to be Class C.
label | ○ LV, Comms Cover: pit covers shall be labelled with the words “RAILWAYS SIGNALS & COMMUNICATIONS” (L1-CHE-STD-043 14.6)
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.3 - Warning/Marker Tape
label | Reference - IFC Drawings AS/NZ 2648.1 TS-SP-013 L1-CHE-STD-043 6.4
label | Acceptance Criteria - Warning/Marker Tape:
label | Above LV:
label | ○ 150mm minimum wide orange coloured PVC
label | ○ ‘DANGER RAILWAY SIGNALLING CONDUITS’
label | Above Comms:
label | ○ 75mm minimum wide white coloured PVC
label | ○ ‘WARNING COMMUNICATIONS CABLES’ with an embedded stainless steel trace wire to be laid directly above trenched VicTrack assets
label | Above HV:
label | ○ 300mm minium width orange coloured PVC 'Danger - Electrical Cable Below'
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.4 - Protection Barriers
label | Reference - IFC Drawings L1-CHE-STD-070 10.3.3 AS4702
label | Acceptance Criteria - Protection barriers shall be polymeric cable protection covers complying with AS4702 OR a min. 40mm thick concrete barriers (pavers) not less than 15MPa at 28 days
label | ○ Inspect materials upon delivery and attached delivery dockets.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.5 - Backfill Material (stabilised sand)
label | Reference - IFC Drawings, L1-CHE-STD-043 Section 2 Table 1
label | Acceptance Criteria - Material free of rocks that will not pass a 30mm sieve. The material shall be free or organic matter or anything that could dmanage the conduits.
label | ○ Inspect backfill material.
label | ○ Attached delivery dockets (if applicable).
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.6 - Bedding Sand
label | Reference - IFC Drawings AS2758.1
label | Acceptance Criteria - Bedding Sand shall be a clean sand that is an uncrushed fine aggregate to AS2758.1 and shall have a thermal resistivity ≤ 1.2 °Cm/W at 5% moisture content.
label | Method - Visual, Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.7 - Draw Wires
label | Reference - TS-SP-013 AS 4142
label | Acceptance Criteria - 6 mm diameter polypropylene blue/yellow
label | Method - Document Review
label | Frequency - Each Material Type, Each Delivery
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - Attach Material Conformnace Certs, Attach delivery dockets
textbox | Date Completed:
checkpoint | 2.8 - Concrete Mix - Trench
label | Reference - L1-CHE-STD-043
label | Acceptance Criteria - N/A
label | Method - N/A
label | Frequency - N/A
label | Category - N/A
label | Responsibility - N/A
label | Verifying Documents - N/A
textbox | Date Completed:
section | 3. Prelimnaries - Procedures & Documentation
checkpoint | 3.1 - Services
label | Reference - Services CAD file
label | Acceptance Criteria - All services within 5m of Excavation location have been identified and appropriate control in place (refer to MRPA Excavation Permit).
label | ○ Survey to mark out existing services.
label | Method - Visual
label | Frequency - Prior to commencement of works
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 3.2 - CSR Works Procedure
label | Reference - WAP_CPD_254
label | Acceptance Criteria - WAP to be reviewed and signed by all relevant stakeholders along with Rail Safety highlighting works proedure with in the Rail Corridor
label | Method - Document Review
label | Frequency - Prior to commencement of works
label | Category - HP*
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
section | 4. Pre-Construction Activities
checkpoint | 4.1 - Survey Set-out
label | Reference - IFC Drawings
label | Acceptance Criteria - Survey to set out trench alignment and pits, and establish construction control (alignment and level).
label | Method - Measure, Visual
label | Frequency - Each element
label | Category - IP
label | Responsibility - Surveyor, SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 4.2 - IFC Drawings
label | Reference - IFC Drawings
label | Acceptance Criteria - Check the revision of the IFC drawings are current as per the drawing register (on Teambinder)
label | Method - Document Review
label | Frequency - Prior to commencement of works and at regualr intervals
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
section | 5. Construction Activities
checkpoint | 5.1 - Trench Excavation
label | Reference - IFC Drawings L1-CHE-SPE-070 7.3 Table 2 L1-CHE-STD-043 L1-CHE-STD-070 7.1c
label | Acceptance Criteria - Trench profile and depth as per IFC drawings.
label | ○ Edge of trenching to be a min. 2m from strucutres/pile foundation (unless it is mounting the structure) and a min. 4m from the rail for HV and 3m from the rail for LV & Comms
label | ○ The bottom of the cable trench shall be level across its width and free from any protrusions and rubble that could cause damage to the conduits.
label | ○ The width of the trench shall be not less than 200 mm (chain or bucket excavation) or 300 mm (backhoe and other).
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.2 - Trench Stability
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings MRPA Standards
label | Acceptance Criteria - Trench stability check:
label | – Shoring,
label | – benching
label | – geotech signoff
label | ○ Attached Geotech Report
label | Method - Visual, Document Review
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.3 - Placement of Bedding Sand for Conduits
label | Reference - IFC Drawings L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070
label | Acceptance Criteria - 100mm of bedding sand/crusher dust to be places at the base of trench.
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.4 - Conduit Placement & Configuration
label | Reference - IFC Drawings L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070, L1-CHE-STD-077
label | Acceptance Criteria - Conduits are configured in accordance with IFC drawings and meet cable separation requirements.
label | Min Cover
label | – HV: 1000mm
label | – VicTrack: 650mm
label | – Signalling: 800mm
label | – LV: 800mm
label | – Electrolysis: 800mm
label | – SCADA: 800mm
label | – MTM Comms: 600mm
label | – 800mm below water coarses (stab sand encasement)
label | – 1200mm Under VicRoads Roads & top of Rail
label | – 900mm below council roads
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.5 - Separation of Services
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070, L1-CHE-STD-077 IFC Drawings
label | Acceptance Criteria - Separation of services
label | – HV: Min. seperation distance between HV conduits at least 50mm
label | – VicTrack: fiber 300mm from HV
label | – Utility: 300mm to utilities
label | – Rail: When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m
label | Method - Measure, Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.6 - Joints
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - All conduit joints shall be made by utilising the spigot and socket ends.
label | ○ Ends to be joined shall be thoroughly cleaned using a solvent approved by the conduit manufacturer.
label | ○ The joint shall be impervious to water and shall be glued with an adhesive approved by the conduit manufacturer.
label | ○ Socket ends to be placed firmly into the spigots then hit with a mallet to ensure a sound connection
label | Method - Visual
label | Frequency - Each Joint in each trench
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.7 - Conduit Inspection
label | Reference - L1-CHE-STD-070 16
label | Acceptance Criteria - Provision shall be made for inspection of cable routes by NA, MTM/VicTrack representatives prior to backfilling.
label | Method - Visual
label | Frequency - Each lot
label | Category - HP*
label | Responsibility - SE/PE MTM / VicTrack Rep.
label | Verifying Documents - This Itp
textbox | Date Completed:
checkpoint | 5.8 - Bedding Sand Installation
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 CL13.1 IFC Drawings
label | Acceptance Criteria - Bedding sand/crusher dust extends 50mm past edge of conduits.
label | ○ Bedding sand/crusher dust extends 100mm above conduits.
label | ○ Attach Delivery Dockets
label | Method - Visual
label | Frequency - Each lot
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.9 - Marker Tape
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-SPE-070 Cl10.3.3
label | Acceptance Criteria - Warning Tape installed a min. 300mm above top conduit or a min. 300mm above HV protection barrers.
label | ○ Tape to be one continuous length.
label | ○ VicTrack to inspect the Marker Tape placement..
label | Method - Visual
label | Frequency - Each lot
label | Category - HP*
label | Responsibility - SE/PE, MTM / VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.10 - Backfill Installation for Conduits
label | Reference - IFC Drawings L1-CHE-STD-043 clauses 6.15 and 6.16
label | Acceptance Criteria - Backfill per trench profile
label | – 150mm layers of 3% stabe sand
label | – conduits under water ways to have 800mm cover from base of water way and backfilled with 3% stab sand
label | ○ The trench shall be finished with a slight mound, height equal to approximately 25% of trench width, to provide for further settlement.
label | ○ Trenches under road pavement - backfill to be same material as the road formation material.
label | ○ Trenches immediately adjacent to footing shall be 3% stab sand. To be thoroughly placed to fill all voids without placing undue strain on or cause displacement of conduits.
label | ○ When conduits are within 2.1m of edge of sleeper they must be encased in stab sand or cover is to be increase to 1.2m
label | ○ VicTrack to be notified and witness the first layer of backfilling.
label | ○ Attached Delivery Dockets
label | Method - Visual
label | Frequency - Each lot
label | Category - HP*
label | Responsibility - SE/PE, MTM / VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.11 - Signalling Pits, LV Pits, Electrolysis Pits, SCADA Pits, MTM Comms Pits
label | Reference - L1-CHE-STD-043 Cl7.14.o, Cl7.14.g
label | Acceptance Criteria - intervals no greater than 400m (electrolysis 190m)
label | – 3m from rail
label | – Access Roads, Class D lids
label | – Footpaths and non traffiacl areas, Class C Lids
label | Method - Visual, Measure
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.12 - Additional Considerations
label | Reference - IFC Drawings
label | Acceptance Criteria - Access tracks to pits
label | ○ Safe access and egress (i.e. lid doesn't open up with workers back to the rail)
label | ○ Hand rail & retaining wall installed as required
label | Method - Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.13 - Bedding for Pit Installation
label | Reference - L1-CHE-STD-070 Cl 7.21.u L1-CHE-STD-043
label | Acceptance Criteria - 150mm of crushed rock under pit extending 500mm past the pit
label | ○ Drainage arrangements shall be provided at the base of each pit.
label | ○ Attach Delivery Dockets
label | Method - Visual, Measure
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.14 - Pit Orientation
label | Reference - IFC Drawings
label | Acceptance Criteria - Pit to be parallel to track and parallel to conduit route.
label | Method - Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.15 - Pit Installation
label | Reference - IFC Drawings
label | Acceptance Criteria - Pit installed to design specifications. Pit chamber floor to be 100mm lower than the underside of the lowest conduit.
label | Method - Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.16 - Conduit Entry onto Pits
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Lowest conduit 100mm from the pit chamber floor.
label | Method - Visual, Measure
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.17 - Tracer Wire
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Warrning tracer wire for Vic Track routes to be drilled into pits and crimped off. If tracer wire broken needs to Crimped
label | Method - Visual
label | Frequency - Each VicTrack Pit
label | Category - HP*
label | Responsibility - SE/PE, MTM / Vic Track Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.18 - Spigots and Bell Mouths
label | Reference - L1-CHE-SPE-070_9.3.4
label | Acceptance Criteria - All conduit ends in pits are to be correctly fitted with spigots to ensure that there are no sharp edges on the conduit; they are to be mounted flush with the pit wall and not touching any other spigots.
label | ○ HV Conduit entering the pit shall extend a minimum of 150mm beyond the edge of the excavation and be fitted with Bell Mouths.
label | Method - Visual, Measure
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.19 - Draw Ropes
label | Reference - VRIOGS 012.2.1
label | Acceptance Criteria - The draw wire shall be continuous for the complete length of the conduit run.
label | ○ The draw wire shall have a minimum of 2 metres of slack within every pit.
label | Method - Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.20 - Backfill and Compaction Testing (if applicable) arouns Pits
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Backfill used around pit & pit lid to achieve 95% standard compaction in layers no more than 150mm layers
label | ○ Sand within sand pits to be compacted in layers no more than 250mm layers
label | ○ Backfill shall be compacted and level with the collar and surrounds for Trafficable Pits.
label | ○ Attach Test Report
label | Method - Document Review, Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.21 - Spare Conduits
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Spare conduits to be sealed and to be included on survey report.
label | Method - Visual
label | Frequency - Each Pit
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.22 - Pit Lables
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Pit labels Brass Label (30mm x 150mm)
label | – HV: DANGER - Railway High Voltage
label | – VicTrack: Victrack Comms
label | – Signalling: Rail Sign Comms
label | – LV Pits: Electrical
label | – Electrolysis: Electrolysis
label | – SCADA: Rail Sign Comms
label | – MTM Comms: Rail Sign Comms
label | Method - Visual
label | Frequency - Each Pit Lid
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.23 - Pit Numbers
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Pit Number Brass Label (30mm x 150mm)
label | – HV (22kVV Feeders): ###HV
label | – DC (HV Feeders for OHLE): ###DC
label | – VicTrack: ###C
label | – MTM Comms: ###M
label | – Signalling LV: ###SL
label | – Signalling HV (2.2 or 3.3kv): ###SH
label | – LV Pits: ###L
label | – Electrolysis: ###E
label | – SCADA: ###MS
label | Method - Visual
label | Frequency - Each Pit Lid
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.24 - Cable Route Markers
label | Reference - L1-CHE-SPE-070_13.2, STD_E0169 and STD_E0170, AS 4799, STD G0003 and STD G0004
label | Acceptance Criteria - Cable Route Markers
label | – points entering & leaving the rail corridor
label | – no greater than 100m spacing
label | – Change of direction (more than 5 degrees)
label | – White posts with marker plates for conduit runs
label | Method - Visual
label | Frequency - Per Cable Route
label | Category - IP
label | Responsibility - SE/Site Supervisor
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.25 - Cable Pulling
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Cable pulling to be witnessed by MTM/Vic Track and to be signed off.
label | Method - Visual
label | Frequency - Per Cable
label | Category - HP*
label | Responsibility - PE, MTM/VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.26 - Cable Labels
label | Reference - L1-CHE-SPE-070 Section 13.3
label | Acceptance Criteria - All installed High Voltage Cables shall be legibly and indelibly marked with an appropriate identifying label at each end of the cable, and at any cable joints.
label | ○ The label shall state the destination points of the cable and the name of the cable relevant to appropriate drawings
label | Method - Visual
label | Frequency - Per Cable
label | Category - HP*
label | Responsibility - PE, MTM/VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 5.27 - Cable Joints
label | Reference - L1-CHE-SPE-070, L1-CHE-STD-043, L1-CHE-STD-070 IFC Drawings
label | Acceptance Criteria - Cable joints are installed correctly, with sufficient fault loops lengths & supported correctly in pits.
label | Method - Visual
label | Frequency - Per Joint / Termination
label | Category - HP*
label | Responsibility - PE, MTM/VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
section | 6. Post-construction / Post-installation Activities
checkpoint | 6.1 - As-built Survey
label | Reference - IFC Drawings L1-CHE-SPE-070 Section 13.1
label | Acceptance Criteria - Survey report to include but not limited to:
label | – Cable joint locations.
label | – Cable pit locations (Corners)
label | – Pit dimensions & pit lid type
label | – Under line crossings
label | – Under road crossings
label | – Changes of direction
label | – Spare Conduits
label | – Conduits labelled as per trench profile
label | – every 10m
label | – Other significant points of the cable route
label | ○ Attached Survey Report
label | Method - Document Review
label | Frequency - Each Lot
label | Category - IP
label | Responsibility - SE/PE
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 6.2 - Handover Check
label | Reference - IFC Drawings
label | Acceptance Criteria - Handover check completed for Testing and Commisioning.
label | ○ Attach MTM/Vic Track Check Sheet (Signed-off)
label | Method - Document Review
label | Frequency - Each Lot
label | Category - HP*
label | Responsibility - PE, MTM/VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 6.3 - Testing and Commissioning
label | Reference - IFC Drawings
label | Acceptance Criteria - Testing and Comminsiong to be completed
label | ○ Attach Testing and Comminsiong Report
label | Method - Document Review
label | Frequency - Each Lot
label | Category - HP*
label | Responsibility - PE, MTM/VicTrack Rep
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | 6.4 - Non-conformance Report (NCR) Closure
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed.
label | Method - Document Review
label | Frequency - Once, prior to closure of this lot / element / Work area
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
textbox | Date Completed:
checkpoint | Final Inspection
note | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
textbox | Date Completed:
signoff | Sign ITP