## Sheet1
ConQA Team Notes:
Document Title: |  | ITP-246-CIV-Supply & Installaton of Street Lighting(Vic Road)
ITP Description: |  | Supply & Installaton of Street Lighting(Vic Road)
Discipline (e.g. CIV/STR/RAIL: |  | 246-CIV
Revision Number: |  | 0
Revision Date: |  | 2025-03-25
ITP created by: |  | Kamel Alshobaki
ITP approved for use by: |  | Pradeep Talasila
Special Notes to ConQA Team :
Inspection & Test Plan -Supply & Installation of Street Lighting
[9 empty] | Revision: | 0
[9 empty] | Date: | 2025-03-25
Legend: HP: Hold Point, HP* Internal Hold Point, WP: Witness Point, IP: Inspection Point, SP: Surveillance Point, AP: Approval Point
Item | Task/Activity Description | Reference | Acceptance Criteria | Inspection / Test |  |  | Responsibility | Verifying Documents | Date Completed | Sign-off
|  |  |  | Method | Frequency | Category
1 | Referenced Documentation
1.1 | Non Dependent | VicRoads Section 731 June 2017 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
1.2 | Non Dependent | VicRoads Section 733 April 2019 | N/A | N/A | N/A | N/A | N/A | N/A | NA | N/A
2 | Preliminaries
2.1 | Obtain and review manufacturer documentations for the supply of materials | Vic road 733.02 AS/NZS 2053 AS/NZS 1345 Vic road 731.02 AS/NZS 3000 Vic road 630.07 AS 1627.1 AS 1627.4 AS/NZS 1554.1 AS 1214 | Materials comply with Vicroad Section 733.02,731.11, 630.07 and relevant specifications. All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001. * Enter: Teambinder Material Approval number [free text box] | Document Review | Per Source | HP* | Nominated Authority | ConQA Hold Point Release
2.2 | Inspect supplied items upon delivery | QMP | Supplied items are to correct spec, class, size and undamaged | Visual /Site Inspection & Document Review | Per Delivery | IP | SE/PE/SPE | Material Inspection Report
3 | Conduit Pit Installation
3.1 | Conduit & pit installation | Vic road section 733 April 2019 | This Item will be completed under the checklist conduit & pit Installation (Road) | Document Review | Per Lot | IP | SE/PE/SPE | This ITP
4 | Foundation
4.1 | Prepare the plinth foundation(Excavation & levels) | VicRoads Standard Drawings IFC | Check levels conform to relevant drawing depending on type of pole to be installed. | Visual Survey | Per Lot | IP | SE/PE/SPE | This ITP
4.2 | Installation Street lighting pole bases | VicRoads Standard Cl731.11 VicRoads Standard Cl731.6 VicRoads Spec Cl733.6 | Pits located 1 metre in advance of, and 1 metre off the line of the pole and in accordance to TC-1210,TC 1220 & TC-1230. A two(2)meter of spare length of each cable shall be left coiled in each pit. · · The slip plane of a slip base pole is to be located 75mm ± 25mm above the surrounding finished surface level · All poles/luminaries to be individually earthed to the earth cable in the pit | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP
4.3 | Installation of frangible poles (Slip base and Impact Absorbing) | VicRoads Specs. Cl 731.06b Requirements TC-1065 TC-1066 TC-1072 TC-1071 TCS014 Supply of Frangible street lighting poles | The slip plane of a slip base pole is to be located 75mm ± 25mm above the surrounding finished surface level as per VicRoads Standard Drawing TC-1072 · The holding down bolts and nuts on the flange are to be slackened of one at a time and re-tightened using a torque wrench to 40Mn for Main nut (Half Nut) and 90Nm for Lock nut (Full Nut) · Record torque of each Slip Base pole in report · Locking nuts to be installed on all hold down bolts · Lock nuts to be installed on Slip base as per VicRoads Drawing TC-1065: Slip base pole assembly, Ground set mounted and VicRoads Drawing TC-1064a: Impact Absorbing | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP
4.4 | Erection of Street lighting columns | VicRoads Standard Drawing TC-1068 | Installed on rigid columns as per VicRoads Standard Drawing TC-1068: Rigid Street Lighting Pole | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP
4.5 | Assembly of outreaches and luminaires | VicRoads Specs. Table 731.061 Requirements TCS065 | Outreach bracket to be installed to the pole spigot using the clamping bolt assemble - Bracket and luminaire to align at right angles to vehicle path on road - Luminaire orientation to comply with Table 731.061 from VicRoads Standard, Section 731 - Road Lighting Installation - Luminaires to conform to TCS 065 - Supply of LED Road Lighting Luminaires - Luminaires shall be supplied with the PE cell bypassed or deactivated |  | Per Lot | IP | SE/PE/SPE | This ITP
4.6 | Installation of lighting distribution cabinet | VicRoads Specs Cl.731.11 IFC Drawing | The lighting distribution cabinets shall be supplied and installed in accordance with VicRoads Specification TCS 043 - Specification for Distribution Box for Road Lighting Power Supply. · The foundation of the distribution cabinet shall be installed as specified in VicRoads Standard Drawing TC-1062. · Distribution cabinets shall be located not less than 5 metres from any carriageway and where possible beyond the clear zone for the particular road. For any distribution cabinet within the clear zone, the Contractor shall provide traffic barriers to protect the distribution | Visual | Per lot | IP | SE/PE/SPE | This ITP
4.7 | Installation of cabling | VicRoads Specs. Cl.731.11 | All electrical cabling to be in accordance with the requirements of AS/NZS 3000: (Australian/New Zealand Wiring Rules) - Each pole to be cables from the pole circuit breaker - All electrical cable joints to be water proof - JUP, JUMA or slip base pole: Cable to be supported by nylon cord or steel catenary. Cable to be attached the support wire with cable ties, no less then intervals of 4m - IA pole: Cable to be supplied through flexible conduit fitted inside the pole from cable termination access door to pole spigot. - Cable for trunk electricity supply from “point of supply” to distribution box to be not less than 16mm square 4 core, three phase copper XPLE cable | Visual & Document Review | Per Lot | IP | SE/PE/SPE | Test Certificate This ITP
4.8 | Labelling of Assets | VicRoads Specs. Cl.731.12 | Labels fixed to poles as per VicRoads Section 731.12 | Visual /Site Inspection & Document Review | Per Lot | IP | SE/PE/SPE | This ITP
5 | Completion
5.1 | Commissioning & testing(if Applicable) | VicRoads Specs. Cl.731.16a & c | Upon final acceptance, the Contractor shall switch on the lighting installation at the distribution cabinet in automatic mode, and record the time, date and meter reading for contractual, warranty and power supply purposes and supply this record to the Superintendent within 48 hours | Commissioning & testing | Upon completion of each section | HP* | SE/PE/SPE Services Engineer | ConQA Hold Point Release
5.2 | As-Constructed Plans | VicRoads Specs. Cl.731.16d | The Contractor shall supply to the Superintendent two copies of ‘As-Constructed’ plans along with a USB drive or other approved storage medium containing the CADD drawing files, and the same shall be supplied by the Contractor to the local distribution company if appropriate. | Document Review | Upon completion/ Work area | AP | SE/PE/SPE | ConQA Hold Point Release
5.3 | Non-conformance Report (NCR) Closure | MRPA Quality Management Plan | Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in CAMs. | Document Review | Once, prior to closure of this lot / element / Work area | HP* | SE/PE/SPE | This ITP
Final Inspection
On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
Print Name: Position: Signature: Date: / /