## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP-246-CIV-FRMS-Supply & Installaton of Street Lighting (Vic Road) | itp |  |  |  |  | ITP-246-CIV-FRMS-Supply & Installaton of Street Lighting (Vic Road) Rev 0
section | 1. Referenced Documentation
checkpoint-no-value | Referenced Documentation
label | Document Title: ITP-246-CIV-Supply & Installaton of Street Lighting(Vic Road)
label | ITP Description: Supply & Installaton of Street Lighting(Vic Road)
label | Discipline (e.g. CIV/STR/RAIL): 246-CIV
label | Revision Number: 0
label | Revision Date: 25/03/2025
label | ITP created by: Kamel Alshobaki
label | ITP approved for use by: Pradeep Talasila
label | 1.1 - Non Dependent
label | Reference - VicRoads Section 731 June 2017
label | 1.2 - Non Dependent
label | Reference - VicRoads Section 733 April 2019
section | 2. Preliminaries
checkpoint | 2.1 - Obtain and review manufacturer documentations for the supply of materials
label | Reference - Vic road 733.02 AS/NZS 2053, AS/NZS 1345
label | ○ Vic road 731.02 AS/NZS 3000
label | ○ Vic road 630.07 AS 1627.1, AS 1627.4, AS/NZS 1554.1, AS 1214
label | Acceptance Criteria - Materials comply with Vicroad Section 733.02,731.11, 630.07 and relevant specifications.
label | ○ All materials shall comply with the standards and specifications shown on the drawings. All structural steel, associated components and welding consumables shall be manufactured by companies that hold quality systems certification to AS/NZS ISO 9001.
textbox | Enter: Teambinder Material Approval number
label | Method - Document Review
label | Frequency - Per Source
label | Category - HP*
label | Responsibility - Nominated Authority
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
checkpoint | 2.2 - Inspect supplied items upon delivery
label | Reference - QMP
label | Acceptance Criteria - Supplied items are to correct spec, class, size and undamaged
label | Method - Visual /Site Inspection & Document Review
label | Frequency - Per Delivery
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - Material Inspection Report
date | Date Completed:
section | 3. Conduit Pit Installation
checkpoint | 3.1 - Conduit & pit installation
label | Reference - Vic road section 733 April 2019
label | Acceptance Criteria - This Item will be completed under the checklist conduit & pit Installation (Road)
label | Method - Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
section | 4. Foundation
checkpoint | 4.1 - Prepare the plinth foundation(Excavation & levels)
label | Reference - VicRoads Standard Drawings IFC
label | Acceptance Criteria - Check levels conform to relevant drawing depending on type of pole to be installed.
label | Method - Visual, Survey
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.2 - Installation Street lighting pole bases
label | Reference - VicRoads Standard Cl731.11
label | ○ VicRoads Standard Cl731.6
label | ○ VicRoads Spec Cl733.6
label | Acceptance Criteria - Pits located 1 metre in advance of, and 1 metre off the line of the pole and in accordance to TC-1210,TC 1220 & TC-1230. A two(2)meter of spare length of each cable shall be left coiled in each pit.
label | ○ The slip plane of a slip base pole is to be located 75mm ± 25mm above the surrounding finished surface level
label | ○ All poles/luminaries to be individually earthed to the earth cable in the pit
label | Method - Visual /Site Inspection & Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.3 - Installation of frangible poles (Slip base and Impact Absorbing)
label | Reference - VicRoads Specs. Cl 731.06b
label | ○ Requirements
label | — TC-1065
label | — TC-1066
label | — TC-1072
label | — TC-1071
label | ○ TCS014 Supply of Frangible street lighting poles
label | Acceptance Criteria - The slip plane of a slip base pole is to be located 75mm ± 25mm above the surrounding finished surface level as per VicRoads Standard Drawing TC-1072
label | ○ The holding down bolts and nuts on the flange are to be slackened of one at a time and re-tightened using a torque wrench to 40Mn for Main nut (Half Nut) and 90Nm for Lock nut (Full Nut)
label | ○ Record torque of each Slip Base pole in report
label | ○ Locking nuts to be installed on all hold down bolts
label | ○ Lock nuts to be installed on Slip base as per VicRoads Drawing TC-1065: Slip base pole assembly, Ground set mounted and VicRoads Drawing TC-1064a: Impact Absorbing
label | Method - Visual /Site Inspection & Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.4 - Erection of Street lighting columns
label | Reference - VicRoads Standard Drawing TC-1068
label | Acceptance Criteria - Installed on rigid columns as per VicRoads Standard Drawing TC-1068: Rigid Street Lighting Pole
label | Method - Visual /Site Inspection & Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.5 - Assembly of outreaches and luminaires
label | Reference - VicRoads Specs. Table 731.061
label | ○ Requirements TCS065
label | Acceptance Criteria - Outreach bracket to be installed to the pole spigot using the clamping bolt assemble
label | ○ Bracket and luminaire to align at right angles to vehicle path on road
label | ○ Luminaire orientation to comply with Table 731.061 from VicRoads Standard, Section 731 - Road Lighting Installation
label | ○ Luminaires to conform to TCS 065 - Supply of LED Road Lighting Luminaires
label | ○ Luminaires shall be supplied with the PE cell bypassed or deactivated
label | Method -
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.6 - Installation of lighting distribution cabinet
label | Reference - VicRoads Specs Cl.731.11 IFC Drawing
label | Acceptance Criteria - The lighting distribution cabinets shall be supplied and installed in accordance with VicRoads Specification TCS 043 - Specification for Distribution Box for Road Lighting Power Supply.
label | ○ The foundation of the distribution cabinet shall be installed as specified in VicRoads Standard Drawing TC-1062.
label | ○ Distribution cabinets shall be located not less than 5 metres from any carriageway and where possible beyond the clear zone for the particular road. For any distribution cabinet within the clear zone, the Contractor shall provide traffic barriers to protect the distribution
label | Method - Visual
label | Frequency - Per lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 4.7 - Installation of cabling
label | Reference - VicRoads Specs. Cl.731.11
label | Acceptance Criteria - All electrical cabling to be in accordance with the requirements of AS/NZS 3000: (Australian/New Zealand Wiring Rules)
label | ○ Each pole to be cables from the pole circuit breaker
label | ○ All electrical cable joints to be water proof
label | ○ JUP, JUMA or slip base pole: Cable to be supported by nylon cord or steel catenary. Cable to be attached the support wire with cable ties, no less then intervals of 4m
label | ○ IA pole: Cable to be supplied through flexible conduit fitted inside the pole from cable termination access door to pole spigot.
label | ○ Cable for trunk electricity supply from “point of supply” to distribution box to be not less than 16mm square 4 core, three phase copper XPLE cable
label | Method - Visual & Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - Test Certificate, This ITP
date | Date Completed:
checkpoint | 4.8 - Labelling of Assets
label | Reference - VicRoads Specs. Cl.731.12
label | Acceptance Criteria - Labels fixed to poles as per VicRoads Section 731.12
label | Method - Visual /Site Inspection & Document Review
label | Frequency - Per Lot
label | Category - IP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
section | 5. Completion
checkpoint | 5.1 - Commissioning & testing(if Applicable)
label | Reference - VicRoads Specs. Cl.731.16a & c
label | Acceptance Criteria - Upon final acceptance, the Contractor shall switch on the lighting installation at the distribution cabinet in automatic mode, and record the time, date and meter reading for contractual, warranty and power supply purposes and supply this record to the Superintendent within 48 hours
label | Method - Commissioning & testing
label | Frequency - Upon completion of each section
label | Category - HP*
label | Responsibility - SE/PE/SPE, Services Engineer
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
checkpoint | 5.2 - As-Constructed Plans
label | Reference - VicRoads Specs. Cl.731.16d
label | Acceptance Criteria - The Contractor shall supply to the Superintendent two copies of ‘As-Constructed’ plans along with a USB drive or other approved storage medium containing the CADD drawing files, and the same shall be supplied by the Contractor to the local distribution company if appropriate.
label | Method - Document Review
label | Frequency - Upon completion/ Work area
label | Category - AP
label | Responsibility - SE/PE/SPE
label | Verifying Documents - ConQA Hold Point Release
date | Date Completed:
checkpoint | 5.3 - Non-conformance Report (NCR) Closure
label | Reference - MRPA Quality Management Plan
label | Acceptance Criteria - Ensure that any NCRs pertaining to the lot / element / Work area that this ITP covers, have been closed in CAMs.
label | Method - Document Review
label | Frequency - Once, prior to closure of this lot / element / Work area
label | Category - HP*
label | Responsibility - SE/PE/SPE
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
textbox | Date Completed:
signoff | Sign ITP
checklist | ITP-247-CIV-FRMS-Traffic Signals - Commission (Supply and Install) | itp |  |  |  |  | ITP-247-CIV-FRMS-Traffic Signals - Commission (Supply and Install) Rev 0
section | 1. Referenced Documentation
checkpoint-no-value | Referenced Documentation
label | Document Title: ITP-247-CIV Traffic Signals - Commission (Supply and Install)
label | ITP Description: Traffic Signals - Commission (Supply and Install)
label | Discipline (e.g. CIV/STR/RAIL): 247-CIV
label | Revision Number: 0
label | Revision Date: 28/03/2025
label | ITP created by: Kamel Alshobaki
label | ITP approved for use by: Pradeep Talasila
label | 1.1 - Non Dependent
label | Reference - VicRoads Section 730 October 2013
label | 1.2 - Non Dependent
label | Reference - AS3000
section | 2. Signalling Electrical System
checkpoint | 2.1 - Point of Supply
label | Reference - Section 730.14 (a), SD TC-1207
label | Acceptance Criteria - The Contractor shall arrange for the installation of the point of supply with the local power distribution company, at the location approved at the pre-installation meeting
label | ○ The point of supply shall be installed in accordance with SD TC-1206 and arranged with the local power distribution company to meet the specific requirements.
label | Method - Review
label | Frequency - Per item
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.2 - Communications Line
label | Reference - Section 730.14 (b), SD TC-1207
label | Acceptance Criteria - A communications conduit along with a two pair telecommunications cable is to be installed from the signal controller to the nearest sutable communication supplier's pit as per SD TC-1207
label | Method - Visual
label | Frequency - Per item
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.3 - Cable Installation
label | Reference - Section 730.14 (c)
label | Acceptance Criteria - Site cabling is to be completed in accordance with Section 730.14 (c), ensuring all cables are installed with no damage to sheathing and insulation, restrained at the point of termination (top of pedestal and MA/JUP access points) to ensure minimal stress on terminations, as well as sufficient cable provided to reach 1.5m above the signal controller base
label | Method - Visual
label | Frequency - Per cable
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.4 - Cable Sizes and Wiring
label | Reference - Section 730.14 (d)
label | Acceptance Criteria - 51 core cable is to be used at intersection traffic signals and its sequencial assemblies. 29 (dual carriageway) or 19 (single carriageway) core cable is to be used at pedestrian operated signals and its sequencial assemblies
label | Method - Visual
label | Frequency - Per cable
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.5 - Pedestrian push button terminations
label | Reference - Section 730.14 (e) Table 730.141
label | Acceptance Criteria - Pedestrian push button detectors are to be connected by 5 core cable and terminated at the required locations.
label | Method - Visual
label | Frequency - Per cable
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.6 - Connecting of traffic signal controller
label | Reference - Section 730.14 (f)
label | Acceptance Criteria - Contractor shall install a 3 core supply cable in a 50mm conduit between the supply point and signal controller base. 1.5m of supply cable shall be coiled in the pit closest to the controller base.
label | Method - Visual
label | Frequency - Per cable
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 2.7 - Testing of Electrical Works
label | Reference - Section 730.14 (l), AS3000 Cl 8.3.3
label | Acceptance Criteria - The following tests are to be carried out prior to the installation of lanterns and hardware:
label | — continuity of all active, neutral and ELV conductors as well as earthing system.
label | ○ Attach: Electrical Test Report
label | ○ Following the installation of all lanterns and hardware, the Contractor shall carry out a flash test.
label | Method - Records
label | Frequency - Per installation
label | Category - HP*
label | Responsibility - SE/Supervisor
label | Verifying Documents - Electrical Test Report
date | Date Completed:
section | 3. Detector Loop Installation
checkpoint | 3.1 - Cutting of detector loops
label | Reference - Section 730.14 (j), VicRoads TCS 054
label | Acceptance Criteria - Detector loops are to be cut as per the locations shown on the design drawings to the TCS 054 specification.
label | Method - Visual
label | Frequency - Per loop
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - This ITP
date | Date Completed:
checkpoint | 3.2 - Installation of detector feeder cables
label | Reference - Section 730.14 (g), SD TC-1300
label | Acceptance Criteria - Detector feeder cables are to be installed to connect detector loops to the traffic signal controller. Installation is as follows:
label | ○ Install 1 cable per loop and each cable pair shall be clearly and durably marked at both ends to enable positive identification
label | ○ Connection of the detector loop cables to the detector feeder cables by soldering
label | ○ 4 wires for each loop (as per SD TC-1300) shall be tied together in a knot close to the conduit end
label | ○ Terminations (joined or unjoined) shall be seperately insulated and sealed against the ingress of moisture with heat shrink
label | ○ Detector cables to have sufficient length to allow 1.5m to be coiled in the pit and 1.5m to reach the top of the controller base
label | ○ Cable diagram shall be provided once complete and visible to the controller installation contractor detailing the loop cable/feeder cable connections.
label | Method - Visual
label | Frequency - Per loop
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 3.3 - Cabling of Large Sites
label | Reference - Section 730.14 (i)
label | Acceptance Criteria - For large signal installations where the standard allocation of cores as specified in SD TC-1204 cannot readily be adopted, MRPA shall draw up a proposed cabling scheme for approval.
label | ○ Attach: Proposed Cabling Scheme Checklst
label | Method - Records
label | Frequency - Per installation
label | Category - HP*
label | Responsibility - SE/PE, NA
label | Verifying Documents - Attach Proposed Cabling Scheme Checklist
date | Date Completed:
section | 4. Pre-Commissioning
checkpoint | 4.1 - Pre-Commisioning Site Inspection
label | Reference - Section 730.16 (a)
label | Acceptance Criteria - Inspection to be carried out between the relevant parties upon completion of the installation works.
label | ○ The Contractor is to notify NA and VR of the inspection.
label | Method - Records
label | Frequency - Per installation
label | Category - IP
label | Responsibility - P/E, NA, Supervisor, VR
label | Verifying Documents - Attach Pre-Commissioning Installation Report
date | Date Completed:
checkpoint | 4.2 - Provision of power
label | Reference - Section 730.16 (b)
label | Acceptance Criteria - Obtain connection of mains supply by submitting all necessary paperwork and payment of fees.
label | Method - Records
label | Frequency - Per installation
label | Category - IP
label | Responsibility - PE, Supervisor
label | Verifying Documents - Sign ITP
date | Date Completed:
checkpoint | 4.3 - Traffic Controller Installation
label | Reference - Section 730.16 (c)
label | Acceptance Criteria - Contractor to notify VR when the site is completed, tested and ready for the traffic signal controller to be installed.
label | ○ Traffic signal controller to be installed by controller supplier or authorised representative.
label | ○ Contractor shall arrange issuing the Certificate of Electrical Safety and the necessary paperwork to obtain connection.
label | Method - Records
label | Frequency - Per installation
label | Category - IP
label | Responsibility - PE, Supervisor
label | Verifying Documents - Attached Certificate of Electrical Safety
date | Date Completed:
section | 5. Completion of Site Works and Commissioning
checkpoint | 5.1 - Switch-On
label | Reference - Section 730.17 (a)
label | Acceptance Criteria - Prior to switching the signals on, a 'flash test' of the installation shall be carried out to ensure that each lantern is connected to the correct cable core. The flash test shall be witnessed by the Nominated Authority and VR and confirmed as acceptable.
label | ○ The controller supplier is to record the relevant details required for the Electrical Test Report.
label | Method - Review
label | Frequency - Per lantern
label | Category - HP*
label | Responsibility - PE, NA, VR, Supervisor
label | Verifying Documents - Attach Electrical Test Report
date | Date Completed:
checkpoint | 5.2 - Removal of redundant hardware
label | Reference - Section 730.17 (b)
label | Acceptance Criteria - All redundant components of hardware and equipment shall be removed unless specified on the design drawings.
label | Method - Visual
label | Frequency - Per installation
label | Category - IP
label | Responsibility - SE/Supervisor
label | Verifying Documents -
date | Date Completed:
section | 6. Post-construction / Post-installation Activities
checkpoint | 6.1 - Survey as-built
label | Reference - IFC Drawings
label | Acceptance Criteria - Survey to As Built Traffic Signalling works.
label | ○ As Constructed Traffic Signal plan to be submitted to Vic Roads.
label | Method - Document Review
label | Frequency - Each element
label | Category - IP
label | Responsibility - SE/Surveyor
label | Verifying Documents - Attach As Constructed Traffic Signal plan
date | Date Completed:
checkpoint | Final Inspection
label | On behalf of Metropolitan Roads Program Alliance, it is hereby certified that the Works represented by the item of work listed have been tested in accordance with the Project Quality Plan and conform in all respects with the requirements of the Contract.
textbox | Name:
textbox | Position:
textbox | Date Completed:
signoff | Sign ITP