## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Wall Closure Checklist 1 Rough In [A]
section | Wall Closure Checklist 1 Rough In
checkpoint | Confirm area of work is accessible & acceptable to commence (If not comment below)
checkpoint | FCU installed in right location as per mechanical layout and the model number is in accordance with latest AC schedule
checkpoint | FCU installed at right height to ensure grille is centred into the bulkhead & 5% slope towards drain point
checkpoint | Thermostat control cabling has been installed
checkpoint | Thermostat location is correct as per RCP
checkpoint | Drains have been run to Tundish
checkpoint | Drains tested and witnessed by Broad Air
checkpoint | All wiring including interconection wiring to condenser & branch box are roughed without defect
checkpoint | Refrigeration pipes have been installed and all refnets are sealed and hard to soffit and don’t impede on ceiling height
checkpoint | Refrigeration insulation is not damaged. Refrigeration pipe supports have been installed maximum 2m apart
checkpoint | Where refrigeration lines insulated and supported pipe clamps have been installed to avoid damage to insulation
checkpoint | Exhaust Vent & Make up Air boxes are installed as per drawings and sealed
checklist | Ceiling Closure Checklist 1 Rough In [B]
section | Air Conditioning:
checkpoint | Air Conditioning
textbox | Inspection Date:
checkpoint | FCUs are installed and other services are not impeding access to fan coil
checkpoint | FCU filter track and filters are installed and nearby service is not impede filter access
checkpoint | Wiring connected to indoor unit electrical box
checkpoint | Condensate drainage is in correct location & height.
checkpoint | Condensate line has 2% fall towards the tundish and has support every 1m-1.5m
checkpoint | Branch Box are installed correctly and pipework is connected to the right connection points
checkpoint | All FCU flexible ducts installed and supported by intact load spreader
checkpoint | All flexible ducts connections to air terminals and spigots have been air tight & secured by using fixing ties/cables ties & duct tape
checkpoint | Supply boxes are installed and supported at correct location in the middle of bulkhead height
checkpoint | Sheetmetal attenuating ductwork has been installed as per documented drawings
section | Ventilation:
checkpoint | Ventilation
textbox | Inspection Date:
checkpoint | Fans installed within ceiling areas are in the correct location as per Mechanical Drawings
checkpoint | Fans Installed correctly with rubber isolation pads
checkpoint | All Flex has been run to correct location
checkpoint | All flex are hung independent of other services and supported by intact load spreaders
checkpoint | All flexible ducts inner core and outer core have been mechanically secured & taped to spigots and air terminals by using duct tape & fixing/cable ties?
checkpoint | All flexible ducts have been mechanically secured to spigots and air terminals by using fixing ties
checkpoint | Flexible ducts run on the right location and not jammed?
checkpoint | Butterfly dampers are installed to the fan as per mechanical drawings and they are in a fully opened position and air tight sealed
checkpoint | PVC sleeves has been installed in wet area walls
checkpoint | PVC ducts have been hung and supported indicidually by using hanging straps
checkpoint | Flatpack flexible joiner connected to façade & installed air tight & water tight as per mechanical drawings
checkpoint | Fresh air to apartment including fire dampers & non return dampers installed as per drawings
section | Access Panel:
checkpoint | Access Panel
textbox | Inspection Date:
checkpoint | Access Panel location has been marked on floor as per RCP
checkpoint | Access panel location allows sufficient access equipment
checkpoint | All other other services do not impede access
checklist | Duct Installation Checklist [C]
section | Duct Installation Checklist
checkpoint | Are drawings on site the latest issue
checkpoint | Are plant and equipment location correct
checkpoint | Fan in the duct run has been installed
checkpoint | Model of the fan is correct as per latest Fan Schedule
checkpoint | Fan components checked before and after installation?
checkpoint | Duct size and location correct
checkpoint | Material and gauge correct
select | Material: | CVD,NRDs,Flex,Canvass
checkpoint | Is correct support method being used - Risers are supported at each level.
checkpoint | Is correct jointing method being used
checkpoint | Are joints completed and cleated installed on flanges
checkpoint | Is correct joint sealant being used
checkpoint | Has the spacer been placed between the fan and the silencer, and the splitter orientation rotated by 90°?
checkpoint | Is 1 diameter of straight duct between pod attenuator and fan inlet been allowed to ensure impeller obtains even flow?
checkpoint | Is adequate distance between attenuator and fans been maintained?
checkpoint | Are the attenuator splitters in the plane of the bend ?
checkpoint | Are transitions close to attenuators gradual?
checkpoint | Is a settling duct between volume control dampers and attenuators allowed?
checkpoint | Are fire dampers installed and break away joint complete
checkpoint | Are flexible ducts installed, supported and connected to spigot by approved method using duct tape on internal core and cable tie on outer core
checkpoint | Are flexible connections to equipment sealed and aligned
checkpoint | Is ductwork insulation as per drawings
checkpoint | Is ductwork fire rating complete
checkpoint | Are all spigots installed and dampers fully open
checkpoint | Are all access panels for fire damper access installed and closed
checkpoint | Is ductwork installation complete
checklist | Common Area Fit-Off Checklist [D]
section | Common Area Fit-Off Checklist
checkpoint | Lobby supply grilles fitted
checkpoint | Lobby exhaust grilles fitted
checkpoint | Lobby Relief VCD is installed and the motorised actuator is fitted of and wired
checkpoint | Lobby relief grilles fitted
checkpoint | Stair pressurisation grilles in the stair shaft fitted
checkpoint | Stair pressurization VCD / OBD is installed
checkpoint | Carpark supply grilles fitted
checkpoint | Carpark supply VCD / OBD is installed and the motorised actuator is fitted of and wired (if applicable)
checkpoint | Carpark Exhaust grilles fitted
checkpoint | Carpark Exhaust VCD / OBD is installed and the motorised actuator is fitted of and wired (if applicable)
checkpoint | Garbage Exhaust grilles fitted
checkpoint | Garbage Exhaust VCD/ OBD is installed
checkpoint | General Exhaust grilles fitted
checkpoint | General Exhaust VCD / OBD is installed
checkpoint | Loading Dock grilles fitted
checkpoint | Loading Dock VCD / OBD is installed
checkpoint | Pump Room supply grilles fitted
checkpoint | Pump room supply VCD / OBD is installed
checkpoint | Toilet Exhaust grilles fitted c/w OBD
checkpoint | Bike room grilles fitted
checkpoint | Bike room VCD / OBD installed
checkpoint | Comms room supply grilles fitted
checkpoint | Comms room VCD / OBD installed
checkpoint | Main Switch room Supply grilles fitted
checkpoint | Main Switch room Supply VCD / OBD installed
checkpoint | Storage room Supply grilles fitted
checkpoint | Storage room Supply VCD/ OBD installed
checkpoint | Bin room grilles fitted
checkpoint | Bin room VCD / OBD installed
checklist | Apartment Fit-Off Checklist [E]
section | Apartment Fit-Off Checklist
checkpoint | AC grille to living room installed with no defect
checkpoint | AC grille to bedroom installed with no defect
checkpoint | Return Air grille installed as per RCP drawings
checkpoint | Range hood duct connected and taped to ensure air tight
checkpoint | AC Controller installed as per RCP drawings
checkpoint | Condensation drain is connected to Tundish point 10 mm air gap is provided at the connection point
checkpoint | Ensuite exhaustfans installed and pluged in as per mechanical drawings
checkpoint | Toilet exhaust fans installed and pluged in as per mechanical drawings
checkpoint | Ensuite exhaust grilles installed
checkpoint | Toilet exhaust grilles installed
checkpoint | Laundry exhaust fans installed and pluged in as per mechanical drawings
checkpoint | Laundry exhaust grilles installed
checkpoint | Access panels placed as per drawings
checkpoint | Condenser unit installed, refrigeration pipes are connected , all gaps to insulation is sealed and pipes are not kinked
checkpoint | External louvers installed all gaps sealed between plenum box and wall/ louver flange to wall , photo evidence provided for below 1.Box sealed internally and the gap between the box and wall is sealed 2.Louver flanges sealed to the external box
checklist | A/C Checklist Commissioning [F]
section | A/C Checklist Commissioning
checkpoint | Refrigeration lines have been pressurised and have maintained pressure for more than 24hrs?
checkpoint | Refrigerant lines have been vacuumed to 500 microns and maintained the vacuum?
checkpoint | Indoor unit drains have been terminated to the tundish point?
checkpoint | Outdoor unit drains have been terminated to the tundish point?
checkpoint | Indoor unit flare connection has been properly insulated with specified insulation?
checkpoint | Indoor unit drain connection point has been securely fastened and sealed?
checkpoint | A/C System Flows checked as per mechanical drawings
checklist | Ventilation Checklist Commissioning [G]
section | Ventilation Checklist Commissioning
checkpoint | Fan has been tested and is operational?
checkpoint | Adequate flow has been achieved in bathroom 1?
checkpoint | Adequate flow has been achieved in ensuite?
checkpoint | Adequate flow has been achieved in laundry?
checkpoint | Range hood has been tested and is operational?
checklist | Fire Damper Checklist [H]
section | Fire Damper Checklist
checkpoint | Penetration details have been captured
checkpoint | Gaps between the fire damper and wall no greater than 25mm and is filled with Lorient Intumescent Sealant with no cracking visible
checkpoint | Lorient fire rated mastic has been applied to entire perimeter of fire damper cell on both sides. No evidence of cracking.
checkpoint | Casing perimeter is sealed with Lorient intumescent sealant. No evidence of cracking.
checkpoint | Mechanically fix the branch to the vertical riser with steel screws or pop rivets
checkpoint | Sheet metal thickness is 0.7mm or greater.
checkpoint | Ductwork is connected to either side of the casing with nylon bolts on the flanges as per the AS1682.2 break away joint method. Bolts do not exceed an 8mm diameter.
checkpoint | Access panel is provided to conveniently access fire damper for visual and/or maintenance inspections.
checkpoint | Fire damper labelling in accordance with AS1682.2 has been placed and clearly identifies the fire damper
checkpoint | Pictures attached
checkpoint | Signature (Contract/Subcontractor Assessor)
checkpoint | Signature (Builder Representative)
checklist | Smoke Damper Checklist [I]
section | Smoke Damper Checklist
checkpoint | Smoke damper must be placed in the duct work so the closed blades are with 610 mm of the smoke barrier and before any duct inlets or outlets (See photo attached)
checkpoint | When joining or fastening the damper to duct work, dampers shall be fastened with M6 bolts or M5 screws. Fasteners shall be spaced a maximum of 305 mm center to center with a minimum of two fastners per side.
checkpoint | Smoke dampers must be sealed between the damper frames and duct work. The sealant shall be pressed in place to dispel any air and shall be applied to one side of the damper's face. Use the minimum amount of the material to completely seal the joint.
checkpoint | Access Panel for Actuator and wiring according code and regulations
checklist | Lobby Area [J]
section | Lobby Area
checkpoint-no-value | Lobby Area
textbox | Inspection Date:
checkpoint | Other services installed are not impeding access to fan coil
checkpoint | All Ductwork passing block walls are flushed and sealed
checkpoint | Transfer duct installed at Accessible toilet wall and penetration flushed and sealed
checkpoint | Where passing the block wall flexible ducts has been equipped with Sleeve and penetration sealed
checkpoint | Refrigerant pipes passing through fire rarted walls are sealed at wall penetratiobn by using approved material
checklist | Ducting-Common Area [K]
section | Ducting-Common Area
checkpoint | Riser
checkpoint | Are drawings on site the latest issue
checkpoint | Are plant and equipment location correct
checkpoint | Duct size and location correct
checkpoint | Material and gauge correct
checkpoint | Is correct support method being used - Maximum vertical support to be 3600mm using AS 4254 approved method
checkpoint | Is correct Joining method being used
checkpoint | Are joints completed and cleated installed on flanges
checkpoint | Is correct joint sealant being used
checkpoint | Is ductwork installation complete
checklist | Jet Fans [L]
section | Jet Fans
checkpoint | Are drawings on site the latest issue?
checkpoint | Are plant and equipment location installed correctly as per drawings?
checkpoint | Model of the fan is correct as per latest Fan Schedule?
checkpoint | Is the fan attached to the ceiling structure of the carpark with hardware appropriate to the size and weight of the units (Typically 8mm fasteners)?
checkpoint | Are the correct anti-vibration mounts being used ?
checkpoint | Is the Fan discharge parallel to beams?
checkpoint | Do we have sufficient Clearance?
checkpoint | Is the obstruction too close?
checkpoint | Is the fan installation site coordinated between trades to avoid clashes with pipe work, signage and other obstructions?
checklist | Ventilation Checklist Commissioning [M]
section | Ventilation Checklist Commissioning
checkpoint | Visual survey of installed area. Are all items secured, compliant and no loose elements?
checkpoint | Fan has been tested and is operational?
checkpoint | Adequate flow has been achieved through the grille / outlet?
checkpoint | Does the fan comply to work with control strategy as per the spec?
checklist | Sign Off | [5 empty] | Sign Off
section | Sign Off
checkpoint | Sign-Off Completed as per below (Pass once complete)
textbox | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)
checklist | Sign Off | [5 empty] | Sign Off (Fire Dampers)
section | Sign Off
checkpoint | All fire dampers provided with an access panel as per mechanical drawings
checkpoint | Sign-Off Completed as per below (Pass once complete)
textbox | Inspection Date
bool | Contract/Subcontractor Assessor Sign Off
bool | Builder Representative Sign Off
holdpoint | Request Sign-Off(s) + Click to Add Signature(s)