## Resources
Rich Type | Id | Warnings | type | name | values | prefix | postfix | Usage Count | User Addable | Template Name | Template Id
checklist-sectioned |  |  | checklist | Ventilation - Second fix |  |  |  |  | Yes | Ventilation - Second fix | 0e51ad6e-2044-40da-ae10-56e5e940c6ed
checkpoint-group |  |  | section | Grilles
checkpoint-status |  |  | checkpoint | All internal grilles are fitted off
checkpoint-status |  |  | checkpoint | Air inlet is fitted off and sealed
checkpoint-group |  |  | section | Testing/Commissioning
checkpoint-status |  |  | checkpoint | Fan switch is fitted off
checkpoint-status |  |  | checkpoint | Fan switch is labelled
checkpoint-status |  |  | checkpoint | Fan works on switch (switch is up the right way)
checkpoint-status |  |  | checkpoint | Air flow felt through all supply grilles.
checklist-sectioned |  |  | checklist | First Fix |  |  |  |  | Yes | First Fix | 28af6648-2417-4468-b864-71d18deac79d
checkpoint-group |  |  | section | Level 1 Installation of New SAF1-1
checkpoint-status |  |  | checkpoint | Louvre supplied to builder to to be boxed out
checkpoint-status |  |  | checkpoint | Square to round transition installed and lined
checkpoint-status |  |  | checkpoint | Filter box installed
checkpoint-status |  |  | checkpoint | Fan Installed
checkpoint-status |  |  | checkpoint | Duct heater Installed
checkpoint-status |  |  | checkpoint | Main ducting installed
checkpoint-status |  |  | checkpoint | Flexible duct installed
checkpoint-status |  |  | checkpoint | Seismic Installed (if required)
checkpoint-status |  |  | checkpoint | Builder advised of hatch location if required
checkpoint-status |  |  | checkpoint | New Electrical feed run to Fan (Speed Control if required)
checkpoint-status |  |  | checkpoint | New Electrical feed run to Electrical Duct heater
checkpoint-status |  |  | checkpoint | Drawings marked up for as builts
checkpoint-group |  |  | section | Level 1 - Install Wire and flush box for controllers (1500mm from floor)
checkpoint-status |  |  | checkpoint | AC 1-1 - AC 1-17
checkpoint-group |  |  | section | Ground floor - Install wire and flush box for controllers (1500 from floor)
checkpoint-status |  |  | checkpoint | AC G-1 - AC G-23
checkpoint-group |  |  | section | Ground Floor - Finish Pre pipe for G-14 ducted
checkpoint-status |  |  | checkpoint | Install Duct work into Bulk Head
checkpoint-status |  |  | checkpoint | Install Grille Boots into Bulk head
checkpoint-group |  |  | section | Ground Floor - Observation CCTV Hi-Wall
checkpoint-status |  |  | checkpoint | Pump Down VRV system and remove Excess Refrigerant
checkpoint-status |  |  | checkpoint | Run new pipe work control cable and power feed into wall
checkpoint-status |  |  | checkpoint | Install drain Hose to drain connection
checklist-sectioned |  |  | checklist | Highwall Prepipe |  |  |  |  | Yes | Highwall Prepipe | 2fb84f85-2d0b-4e25-9659-33e7b57ecfd9
checkpoint-group |  |  | section | Top Plate
checkpoint-status |  |  | checkpoint | Top plate stiffeners x2
checkpoint-group |  |  | section | Pair coil pipe run
checkpoint-status |  |  | checkpoint | Pipes run straight down wall
checkpoint-status |  |  | checkpoint | Pipes secured at indoor unit and bent at right height
checkpoint-status |  |  | checkpoint | Supports are in place on pipework
checkpoint-status |  |  | checkpoint | Interconnect fixed at 300 centres/taped to pipework
checkpoint-group |  |  | section | Exterior pipework
checkpoint-status |  |  | checkpoint | Has tradeseal and pipe protection been installed for exterior pipes
checkpoint-group |  |  | section | Drain installation
checkpoint-status |  |  | checkpoint | Indoor taped to bottom of pipes
checkpoint-status |  |  | checkpoint | Has drain got significant fall from indoor to outdoor
checkpoint-status |  |  | checkpoint | Exterior brought through building paper with protection pipe and tradeseal
checkpoint-group |  |  | section | Powersupply
checkpoint-status |  |  | checkpoint | Feed located at switchboard
checkpoint-status |  |  | checkpoint | Isolator loop with tradeseal
checkpoint-status |  |  | checkpoint | Tail brought out with pipework
checkpoint-status |  |  | checkpoint | Has power supply been clipped every 300mm and is clipped on side of trusses. If ran with pipe work is this every 300mm also
checkpoint-group |  |  | section | Pipes Pressurized
checkpoint-status |  |  | checkpoint | Have internal pipes been looped and welded together
checkpoint-status |  |  | checkpoint | Have external pipes been welded and Schrader installed
checkpoint-status |  |  | checkpoint | Please show pipes holding 400PSI Minimum (this can be greater than 400PSI)
checkpoint-status |  |  | checkpoint | Have we got photos of stickers on internal and external pipes advising this
checkpoint-group |  |  | section | Additional Photos
checkpoint-status |  |  | checkpoint | Additional photos (if applicable)
checklist-sectioned |  |  | checklist | Second Fix - Level 1 |  |  |  |  | Yes | Second Fix - Level 1 | 572148f1-f674-40fe-a9d3-a9ceaa5b8837
checkpoint-group |  |  | section | Level One - Re install of grilles that were removed
checkpoint-status |  |  | checkpoint | Install of grilles for walls Around Teams Meeting room
checkpoint-status |  |  | checkpoint | Install of grilles around Office 01 & 02
checkpoint-status |  |  | checkpoint | Install of grilles aorund Staff room
checkpoint-status |  |  | checkpoint | Install of grilles around Physicians Office 01 and 02
checkpoint-status |  |  | checkpoint | Install of grilles around Physicians Office 03, 04 and 05
checkpoint-status |  |  | checkpoint | Install of grilles around 101 Meet Rooms
checkpoint-group |  |  | section | Level One - SAF1-1
checkpoint-status |  |  | checkpoint | Fit grilles for New Fresh air system
checkpoint-group |  |  | section | Level One - Sever Room AC Fit off
checkpoint-status |  |  | checkpoint | Fit off Indoor unit
checkpoint-status |  |  | checkpoint | Fit Drain Pump
checkpoint-status |  |  | checkpoint | Test Drain Pump
checkpoint-status |  |  | checkpoint | Pipes Connected and Capping
checkpoint-status |  |  | checkpoint | Pressure tested to 400PSI
checkpoint-status |  |  | checkpoint | Pipes in vacuum - Add additional chargre (if required)
checkpoint-status |  |  | checkpoint | Unit wired and ready for commissioning
checkpoint-status |  |  | checkpoint | Outdoor unitsecured
checkpoint-status |  |  | checkpoint | Outdoor unit Level
checkpoint-status |  |  | checkpoint | Capping insalled
checkpoint-status |  |  | checkpoint | Model and serial recorded
checkpoint-group |  |  | section | Level 1 Controllers
checkpoint-status |  |  | checkpoint | Install AC controllers AC 1-1 - AC 1-17
checkpoint-group |  |  | section | Ground floor Duct and grille install
checkpoint-status |  |  | checkpoint | SAF G-1 Install and flexi ducting and grilles
checkpoint-status |  |  | checkpoint | SAF G-2 Install and flexi ducting and grilles
checkpoint-status |  |  | checkpoint | AC G-7 Install supply and return ducting and grilles
checkpoint-status |  |  | checkpoint | AC G-14 Install supply and return ducting and grilles
checkpoint-status |  |  | checkpoint | AC G-22 Install supply and return ducting and grilles
checkpoint-status |  |  | checkpoint | AC G-24 Install supply and return ducting and grilles
checkpoint-group |  |  | section | Ground Floor Controllers
checkpoint-status |  |  | checkpoint | Install AC controllers AC G-1 - G23
checkpoint-group |  |  | section | Ground Floor - Observation CCTV Hi-wall fit off
checkpoint-status |  |  | checkpoint | Install Hi-Wall
checkpoint-status |  |  | checkpoint | Wire indoor unit
checkpoint-status |  |  | checkpoint | Install Drain (Drain Pump if required) and test
checkpoint-status |  |  | checkpoint | Pressure test VRF system to 500PSI for 24 Hours
checkpoint-status |  |  | checkpoint | Vac System to 100 Microns
checkpoint-status |  |  | checkpoint | Work out if any Additional refrigerant needs adding
checkpoint-status |  |  | checkpoint | Add extra refrigerant that was taken out of system
checklist-flat |  |  | checklist | Walkthrough |  |  |  |  | Yes | Walkthrough Checklist | 5bced69f-bc4f-4810-970f-037b8a570886
checkpoint-status |  |  | checkpoint | Power outlet locations confirmed and marked
checkpoint-status |  |  | checkpoint | Light switch locations confirmed and marked
checkpoint-status |  |  | checkpoint | Switchboard locations confirmed and marked
checkpoint-status |  |  | checkpoint | Bathroom outlet locations confirmed and marked
checkpoint-status |  |  | checkpoint | Bathroom outlets vertical or horizontal
checkpoint-status |  |  | checkpoint | Towel rail locations confirmed and marked
checkpoint-status |  |  | checkpoint | Interior light locations confirmed
checkpoint-status |  |  | checkpoint | Exterior light locations confirmed and marked
checkpoint-status |  |  | checkpoint | Exterior fan grills soffit mount or wall mount
checkpoint-status |  |  | checkpoint | CCTV locations confirmed
checkpoint-status |  |  | checkpoint | CCTV soffit mount or wall mount
checkpoint-status |  |  | checkpoint | Aerial locations confirmed
checkpoint-status |  |  | checkpoint | Aerial cabling location confirmed and marked
checkpoint-status |  |  | checkpoint | Plans updated with changes
checklist-sectioned |  |  | checklist | Second Fix |  |  |  |  | Yes | Small Commercial - Second Fix | 5e5f4365-da04-4207-8686-ebec44bb34d2
checkpoint-group |  |  | section | Outdoor AC units
checkpoint-status |  |  | checkpoint | AC Units Pipes connected, pipe run and capping.
checkpoint-status |  |  | checkpoint | AC Units Pressure tested to 500psi 24 hrs
checkpoint-status |  |  | checkpoint | AC Units vaced to,100mirons and precharge with extra charge
checkpoint-status |  |  | checkpoint | Units wired and ready for Commissioning
checkpoint-status |  |  | checkpoint | Units fixed with stainless fixings
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | Indoor AC units
checkpoint-status |  |  | checkpoint | AC Units Higwall Pipes, drain and cabling is connected
checkpoint-status |  |  | checkpoint | AC Units are level
checkpoint-status |  |  | checkpoint | Units are left clean and any marks on walls are removed
checkpoint-status |  |  | checkpoint | Remote controls are mounted to wall in agreed locations or handed to client
checkpoint-status |  |  | checkpoint | Units fixed with stainless fixings
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | Fit Off Grills
checkpoint-status |  |  | checkpoint | AC Ducted unit grills fitted
checkpoint-status |  |  | checkpoint | AC Unit covers fitted
checkpoint-status |  |  | checkpoint | Toilet extract grills fitted
checkpoint-status |  |  | checkpoint | Fresh air grills fitted
checkpoint-status |  |  | checkpoint | Photos
checklist-sectioned |  |  | checklist | Project Completion |  |  |  |  | Yes | Small Commercial - Project Completion | 66dda3b5-c0da-4e2e-8dd5-458805b22a89
checkpoint-group |  |  | section | Compliance Information
checkpoint-status |  |  | checkpoint | Airflow test results submitted
checkpoint-status |  |  | checkpoint | Warranty completed and submitted
checkpoint-status |  |  | checkpoint | Producer statements completed and submitted
checkpoint-status |  |  | checkpoint | COC submitted
checkpoint-status |  |  | checkpoint | As builts updated and submitted
checkpoint-status |  |  | checkpoint | Photos uploaded
checkpoint-group |  |  | section | Manuals
checkpoint-status |  |  | checkpoint | Manual info compiled
checkpoint-status |  |  | checkpoint | Manual Structure and descriptions completed in word document
checkpoint-status |  |  | checkpoint | Word document converted to PDF snd relevant info added to each section
checkpoint-status |  |  | checkpoint | Manual submittied to client
checklist-sectioned |  |  | checklist | After Project |  |  |  |  | Yes | Small Commercial - After Project | 6dff2e4e-952e-46f2-afb7-713d698f1234
checkpoint-group |  |  | section | Customer Follow up
checkpoint-status |  |  | checkpoint | Follow up with customer on installation and training with in 2 weeks of occupation
checkpoint-status |  |  | checkpoint | Set up maintenance agreement and submit for approval.
checklist-sectioned |  |  | checklist | Ducted Prepipe |  |  |  |  | Yes | Ducted Prepipe | 7427c985-f347-4f2b-941f-88d771d26952
checkpoint-group |  |  | section | Indoor Unit
checkpoint-status |  |  | checkpoint | Hung level (all axis)
checkpoint-status |  |  | checkpoint | Threaded rod/nuts tight and secure
checkpoint-status |  |  | checkpoint | Supply plenum installed
checkpoint-status |  |  | checkpoint | Top plate stiffener
checkpoint-status |  |  | checkpoint | Indoor unit model and serial number
checkpoint-group |  |  | section | Pair coil pipe run
checkpoint-status |  |  | checkpoint | Pipes run straight down wall
checkpoint-status |  |  | checkpoint | Pipes supports through roof cavity to indoor unit
checkpoint-status |  |  | checkpoint | Pipes supported down wall to exterior
checkpoint-status |  |  | checkpoint | Pipes brought out exterior in protective pipe with tradeseal
checkpoint-status |  |  | checkpoint | Pipes brought up to indoor, connected and insulated
checkpoint-group |  |  | section | Drain
checkpoint-status |  |  | checkpoint | Drain trap is installed
checkpoint-status |  |  | checkpoint | Drain has fall the length of run
checkpoint-status |  |  | checkpoint | Drain exits exterior wall with tradeseal
checkpoint-group |  |  | section | Power supply/cabling
checkpoint-status |  |  | checkpoint | Interconnect is supported by pipes and/or pin clips
checkpoint-status |  |  | checkpoint | Indoor feed at switchboard
checkpoint-status |  |  | checkpoint | Outdoor feed at switchboard
checkpoint-status |  |  | checkpoint | Indoor isolator
checkpoint-status |  |  | checkpoint | Indoor electrical connections
checkpoint-status |  |  | checkpoint | Outdoor feed at switchboard
checkpoint-status |  |  | checkpoint | Outdoor isolator loop with tradeseal
checkpoint-status |  |  | checkpoint | Controller cable run and brought out through flushbox
checkpoint-group |  |  | section | Return grille(s)
checkpoint-status |  |  | checkpoint | Framed in on 2 sides
checkpoint-status |  |  | checkpoint | Framing is above gib line
checkpoint-status |  |  | checkpoint | Neck adapter installed
checkpoint-group |  |  | section | Ducting
checkpoint-status |  |  | checkpoint | Supply ducting installed
checkpoint-status |  |  | checkpoint | Return ducting installed
checkpoint-status |  |  | checkpoint | Grille locations marked on plan
checkpoint-status |  |  | checkpoint | Photos
checklist-sectioned |  |  | checklist | Ventilation - First fix |  |  |  |  | Yes | Ventilation - First fix | 76c7a1d9-847e-4928-9dee-b66c3b78ef5c
checkpoint-group |  |  | section | Fan
checkpoint-status |  |  | checkpoint | Suspended in accessible location
checkpoint-status |  |  | checkpoint | Sitting level
checkpoint-status |  |  | checkpoint | Power Supply brought up to surface mount powerpoint
checkpoint-status |  |  | checkpoint | Power supply run to switch as shown on plan.
checkpoint-status |  |  | checkpoint | Filter
checkpoint-status |  |  | checkpoint | Filter box installed in accessible location
checkpoint-status |  |  | checkpoint | Filter inside filter box
checkpoint-group |  |  | section | Ducting
checkpoint-status |  |  | checkpoint | Ducting run to locations shown on plan
checkpoint-status |  |  | checkpoint | Air inlet is brought out in correct location
checkpoint-status |  |  | checkpoint | Air inlet has tradeseal
checkpoint-status |  |  | checkpoint | All joins are taped
checkpoint-status |  |  | checkpoint | Grille locations marked on plan
checklist-sectioned |  |  | checklist | Pre Start Stage |  |  |  |  | Yes | Pre Start Stage | 7ece44b4-2dfc-476c-91e6-eae596eae021
checkpoint-group |  |  | section | Drawings
checkpoint-status |  |  | checkpoint | Saved Drawings into Simpro
checkpoint-status |  |  | checkpoint | Read through Specification
checkpoint-status |  |  | checkpoint | Programe received and saved in job
checkpoint-status |  |  | checkpoint | Units/plant Noted on drawings
checkpoint-status |  |  | checkpoint | AC Pipe Sizes Shown on drawings
checkpoint-status |  |  | checkpoint | Ducting sizes shown on drawings
checkpoint-status |  |  | checkpoint | Penetraions to wall and roof are detailed with sizes
checkpoint-status |  |  | checkpoint | Condensate connestions points marked on drawings
checkpoint-group |  |  | section | Health and Safety
checkpoint-status |  |  | checkpoint | SSSP Have been produced
checkpoint-status |  |  | checkpoint | SSSP Has been Giving to Lead technican or dropped tosite office
checklist-sectioned |  |  | checklist | Commissioning |  |  |  |  | Yes | Commissioning | 7f640d1f-07c9-4a12-bc9c-c84ed54533dc
checkpoint-group |  |  | section | Commission AC units
checkpoint-status |  |  | checkpoint | Power on, units vacced and cracked
checkpoint-status |  |  | checkpoint | AC G-7 balancing and airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | AC G-22 balancing and airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | AC G-24 balancing and airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | Unit operated in heating and cooling
checkpoint-status |  |  | checkpoint | Commissioning sheet filled out
checkpoint-group |  |  | section | Commissioning Ventilation Systems
checkpoint-status |  |  | checkpoint | Level 1 SAF 1-1 Airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | SAF G-1 Airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | SAF G-2 Airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | EAF-4-2 Airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | OAF-1 Airflows commissioned +10% of design airflow
checklist-sectioned |  |  | checklist | Demolition |  |  |  |  | Yes | Demolition | 96a66e7c-bfef-465c-ba1c-1e0656b7cb40
checkpoint-group |  |  | section | Removal of Grilles fro builder work Level One
checkpoint-status |  |  | checkpoint | Removal of grilles for walls Around Teams Meeting room
checkpoint-status |  |  | checkpoint | Removal of grilles around Office 01 & 02
checkpoint-status |  |  | checkpoint | Removal of grilles aorund Staff room
checkpoint-status |  |  | checkpoint | Removal of grilles around Physicians Office 01 and 02
checkpoint-status |  |  | checkpoint | Removal of grilles around Physicians Office 03, 04 and 05
checkpoint-status |  |  | checkpoint | Removal of grilles around 101 Meet Rooms
checklist-sectioned |  |  | checklist | Project Completion |  |  |  |  | Yes | Project Completion | 96df43cc-dae3-41cf-a6f5-83ae59ec2c2f
checkpoint-group |  |  | section | Compliance Information
checkpoint-status |  |  | checkpoint | Airflow test results submitted
checkpoint-status |  |  | checkpoint | Warranty completed and submitted
checkpoint-status |  |  | checkpoint | Procedure statements completed and submitted
checkpoint-status |  |  | checkpoint | As builts updated and submitted
checkpoint-status |  |  | checkpoint | Photos uploaded
checkpoint-group |  |  | section | Manuals
checkpoint-status |  |  | checkpoint | Manual info compiled
checkpoint-status |  |  | checkpoint | Manual Structure and descriptions completed in word document
checkpoint-status |  |  | checkpoint | Word document converted to PDF and relevant info added to each section
checkpoint-status |  |  | checkpoint | Manual submitted to client
checklist-sectioned |  |  | checklist | First Fix |  |  |  |  | Yes | Small Commercial - First Fix | a1e2d843-b3e8-46a9-a250-7f9642910178
checkpoint-group |  |  | section | Penetrations
checkpoint-status |  |  | checkpoint | Penetrations are marked out on roof and walls
checkpoint-status |  |  | checkpoint | Penetrations being done by builder. Builder has been infomed of our requirements
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | AC Preppies and prewire
checkpoint-status |  |  | checkpoint | AC Units (Ducted or Cassette) Units have been hung and siesmically restrained
checkpoint-status |  |  | checkpoint | AC Units refrigeration pipe and interconnect cable runs between indoor and outdoor. Connected at indoor if cassete or ducted
checkpoint-status |  |  | checkpoint | AC Units Condensate drains have been run to agreed connection point by plumber or outside.
checkpoint-status |  |  | checkpoint | AC Units Power feed to indoor and out door run
checkpoint-status |  |  | checkpoint | AC units Pipe work put under pressure 500 PSI and leak checked. Label added to pipework at outdoor location.
checkpoint-status |  |  | checkpoint | AC Units (Ducted) solid and flexible ducting has been run and restrained
checkpoint-status |  |  | checkpoint | Photos
checkpoint-status |  |  | checkpoint | Drawing marked up for as builts.
checkpoint-group |  |  | section | Toilet Extract Systems first fix
checkpoint-status |  |  | checkpoint | Toilet extract fans installed
checkpoint-status |  |  | checkpoint | Toilet extract cowl supplied to builder
checkpoint-status |  |  | checkpoint | Solid nude extract duct installed
checkpoint-status |  |  | checkpoint | Toilet extract cowl installed
checkpoint-status |  |  | checkpoint | Flexible ducting installed and connected
checkpoint-status |  |  | checkpoint | Extract grill boots installed
checkpoint-status |  |  | checkpoint | Fan is pre wired and connected
checkpoint-status |  |  | checkpoint | Builder advised of hatch location and size
checkpoint-status |  |  | checkpoint | Builder advised of undercuts to doors required
checkpoint-status |  |  | checkpoint | Builder advised of door grill location and size for penetration to the door
checkpoint-status |  |  | checkpoint | Drawing marked up for as built
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | Fresh Air Systems first fix
checkpoint-status |  |  | checkpoint | Fresh air iline fan installed (if applicable)
checkpoint-status |  |  | checkpoint | Fresh air roof mount fan installed (if applicable)
checkpoint-status |  |  | checkpoint | Fresh air in take cowl or lourve installed (if applicable)
checkpoint-status |  |  | checkpoint | Fresh air filter box and filter installed or filter in roof mount fan dropper (if applicable)
checkpoint-status |  |  | checkpoint | Fan / heaterbank is pre wired and connected
checkpoint-status |  |  | checkpoint | Builder advised of hatch locations and sizse
checkpoint-status |  |  | checkpoint | Grill boots installed
checkpoint-status |  |  | checkpoint | Grill Locations mark on plan
checkpoint-status |  |  | checkpoint | Flexible ducting installed and connected to grill boot
checkpoint-status |  |  | checkpoint | Drawings marked up for as builts
checkpoint-status |  |  | checkpoint | Photos
checklist-sectioned |  |  | checklist | Pre start stage |  |  |  |  | Yes | Small Commercial - Pre start stage | b7c467ac-88c5-4f8d-9d85-c9f2fe5c0165
checkpoint-group |  |  | section | Drawings
checkpoint-status |  |  | checkpoint | Drawings saved in job
checkpoint-status |  |  | checkpoint | Unit/plant selections labelled on drawings
checkpoint-status |  |  | checkpoint | AC pipe sizes shown on drawings
checkpoint-status |  |  | checkpoint | Ducting sizes shown on drawings
checkpoint-status |  |  | checkpoint | Penetrations to wall and roof are shown (with sizes)
checkpoint-status |  |  | checkpoint | Condensate connection points marked on drawings
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | Purchasing
checkpoint-status |  |  | checkpoint | All plant has been ordered for first fix
checkpoint-status |  |  | checkpoint | All plant has been ordered for second fix (check Programme)
checkpoint-status |  |  | checkpoint | Photos
checkpoint-group |  |  | section | Health and Safety
checkpoint-status |  |  | checkpoint | SSSP has been produced
checkpoint-status |  |  | checkpoint | SSSP has been dropped to site office
checklist-sectioned |  |  | checklist | Commissioning |  |  |  |  | Yes | Small Commercial - Commissioning | d48ffc48-1239-4dba-94f3-4367e49eac3a
checkpoint-group |  |  | section | Commission AC units
checkpoint-status |  |  | checkpoint | AC Units, Power on, units vacced and crackecd
checkpoint-status |  |  | checkpoint | Units operated in heating and cooling
checkpoint-status |  |  | checkpoint | Airflows balance for AC Ducted - Design airflow obtained +10%
checkpoint-status |  |  | checkpoint | Commissioning sheet filled out
checkpoint-status |  |  | checkpoint | AC Units model and serial numbers recorded and photographed
checkpoint-group |  |  | section | Commissioning Ventilation Systems
checkpoint-status |  |  | checkpoint | Fresh air systems, airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | Extract systems, airflows commissioned +10% of design airflow
checkpoint-status |  |  | checkpoint | Ventilation commissioning sheet filled out
checklist-sectioned |  |  | checklist | Highwall Fitoff |  |  |  |  | Yes | Highwall Fitoff | e6d1c454-2617-4635-9c88-3f4e183946c2
checkpoint-group |  |  | section | Pipes Pressurized
checkpoint-status |  |  | checkpoint | Are pipes still under pressure
checkpoint-group |  |  | section | Indoor unit
checkpoint-status |  |  | checkpoint | Installed level
checkpoint-status |  |  | checkpoint | Drain fitted and secured
checkpoint-status |  |  | checkpoint | Pipes insulated
checkpoint-status |  |  | checkpoint | Wiring correct
checkpoint-group |  |  | section | Outdoor unit
checkpoint-status |  |  | checkpoint | Unit is level
checkpoint-status |  |  | checkpoint | Unit is on feet
checkpoint-status |  |  | checkpoint | Isolator installed with correct terminations
checkpoint-status |  |  | checkpoint | Have we installed silicone behind the isolator
checkpoint-status |  |  | checkpoint | Wall penetration is sealed
checkpoint-status |  |  | checkpoint | Wall cap and trunking installed
checkpoint-status |  |  | checkpoint | Pipe connections correct
checkpoint-status |  |  | checkpoint | Electrical connections are correct
checkpoint-status |  |  | checkpoint | Has the system held a VAC (minimum 500 microns)
checkpoint-group |  |  | section | Drain
checkpoint-status |  |  | checkpoint | Securely fitted off + tested
checkpoint-group |  |  | section | Unit details
checkpoint-status |  |  | checkpoint | Indoor unit plate
checkpoint-status |  |  | checkpoint | Outdoor unit plate
checkpoint-group |  |  | section | Power Supply
checkpoint-status |  |  | checkpoint | MCB fitted off
checkpoint-status |  |  | checkpoint | Switchboard labelled
checkpoint-status |  |  | checkpoint | Test results
checkpoint-status |  |  | checkpoint | COC completed
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Run unit in cooling + measure tempretures (record below)
checkpoint-status |  |  | checkpoint | Run unit in heating + measure tempretures (record below)
checkpoint-status |  |  | checkpoint | Remote and instruction book left on site
checkpoint-status |  |  | checkpoint | Ampt sticker on outdoor unit
checkpoint-group |  |  | section | Additional Photos
checkpoint-status |  |  | checkpoint | Additional photos (if applicable)
checklist-sectioned |  |  | checklist | Ducted fit off |  |  |  |  | Yes | Ducted fit off | eb99a3ad-d3b3-46f5-89bc-81312eb5ad99
checkpoint-group |  |  | section | Outdoor unit
checkpoint-status |  |  | checkpoint | Sitting on feet
checkpoint-status |  |  | checkpoint | Sitting level
checkpoint-status |  |  | checkpoint | Isolator installed
checkpoint-status |  |  | checkpoint | Have we installed silicone behind the isolator
checkpoint-status |  |  | checkpoint | Sealed penetration
checkpoint-status |  |  | checkpoint | Wall cap installed
checkpoint-status |  |  | checkpoint | Pipe connections complete
checkpoint-status |  |  | checkpoint | Electrical connections complete
checkpoint-status |  |  | checkpoint | Ampt sticker on unit
checkpoint-status |  |  | checkpoint | Drain
checkpoint-status |  |  | checkpoint | Fitted off appropriately with a cobra clamp (using screws)
checkpoint-group |  |  | section | Return grille(s)
checkpoint-status |  |  | checkpoint | Fitted into neck adapters
checkpoint-status |  |  | checkpoint | No gaps evident around flange
checkpoint-group |  |  | section | Supply grilles
checkpoint-status |  |  | checkpoint | All installed
checkpoint-status |  |  | checkpoint | Clean
checkpoint-group |  |  | section | Power Supply
checkpoint-status |  |  | checkpoint | Fitted off at MCB
checkpoint-status |  |  | checkpoint | Labelled in switchboard
checkpoint-status |  |  | checkpoint | Testing complete
checkpoint-status |  |  | checkpoint | COC filled in
checkpoint-group |  |  | section | Commissioning
checkpoint-status |  |  | checkpoint | Commisioning sheet completed
checkpoint-status |  |  | checkpoint | Air coming from all grilles
checkpoint-status |  |  | checkpoint | Instruction manual left on site
checkpoint-status |  |  | checkpoint | Outdoor unit model and serial number
checkpoint-status |  |  | checkpoint | Photos