## Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | resource
Pre start stage |  |  |  | Pre start stage
Demo Works |  |  |  | Demo Works
First Fix |  |  |  | First Fix
Second Fix |  |  |  | Second Fix
Commissioning |  |  |  | Commissioning
Project Completion |  |  |  | Project Completion
After Project |  |  |  | After Project

## Checklists
type | name | values | prefix | postfix | Template Name
Check List | Pre Start Stage
Section | Drawings
Check Point | Saved Drawings into Simpro
Check Point | Read through Specification
Check Point | Programe received and saved in job
Check Point | Units/plant Noted on drawings
Check Point | AC Pipe Sizes Shown on drawings
Check Point | Ducting sizes shown on drawings
Check Point | Penetraions to wall and roof are detailed with sizes
Check Point | Condensate connestions points marked on drawings
Section | Health and Safety
Check Point | SSSP Have been produced
Check Point | SSSP Has been Giving to Lead technican or dropped tosite office
Check List | Demolition
Section | Removal of Grilles fro builder work Level One
Check Point | Removal of grilles for walls Around Teams Meeting room
Check Point | Removal of grilles around Office 01 & 02
Check Point | Removal of grilles aorund Staff room
Check Point | Removal of grilles around Physicians Office 01 and 02
Check Point | Removal of grilles around Physicians Office 03, 04 and 05
Check Point | Removal of grilles around 101 Meet Rooms
Check List | Firt Fix
Section | Level 1 Installation of New SAF1-1
Check Point | Louvre supplied to builder to to be boxed out
Check Point | Square to round transition installed and lined
Check Point | Filter box installed
Check Point | Fan Installed
Check Point | Duct heater Installed
Check Point | Main ducting installed
Check Point | Flexible duct installed
Check Point | Seismic Installed (if required)
Check Point | Builder advised of hatch location if required
Check Point | New Electrical feed run to Fan (Speed Control if required)
Check Point | New Electrical feed run to Electrical Duct heater
Check Point | Drawings marked up for as builts
Section | Level 1 - Install Wire and flush box for controllers (1500mm from floor)
Check Point | AC 1-1 - AC 1-17
Section | Ground floor - Install wire and flush box for controllers (1500 from floor)
Check Point | AC G-1 - AC G-23
Section | Ground Floor - Finish Pre pipe for G-14 ducted
Check Point | Install Duct work into Bulk Head
Check Point | Install Grille Boots into Bulk head
Section | Ground Floor - Observation CCTV Hi-Wall
Check Point | Pump Down VRV system and remove Excess Refrigerant
Check Point | Run new pipe work control cable and power feed into wall
Check Point | Install drain Hose to drain connection
Check List | Second Fix - Level 1
Section | Level One - Re install of grilles that were removed
Check Point | Install of grilles for walls Around Teams Meeting room
Check Point | Install of grilles around Office 01 & 02
Check Point | Install of grilles aorund Staff room
Check Point | Install of grilles around Physicians Office 01 and 02
Check Point | Install of grilles around Physicians Office 03, 04 and 05
Check Point | Install of grilles around 101 Meet Rooms
Section | Level One - SAF1-1
Check Point | Fit grilles for New Fresh air system
Section | Level One - Sever Room AC Fit off
Check Point | Fit off Indoor unit
Check Point | Fit Drain Pump
Check Point | Test Drain Pump
Check Point | Pipes Connected and Capping
Check Point | Pressure tested to 400PSI
Check Point | Pipes in vacuum - Add additional chargre (if required)
Check Point | Unit wired and ready for commissioning
Check Point | Outdoor unitsecured
Check point | Outdoor unit Level
Check point | Capping insalled
Checkpoint | Model and serial recorded
Section | Level 1 Controllers
Check Point | Install AC controllers AC 1-1 - AC 1-17
Section | Ground floor Duct and grille install
Check Point | SAF G-1 Install and flexi ducting and grilles
Check Point | SAF G-2 Install and flexi ducting and grilles
Check Point | AC G-7 Install supply and return ducting and grilles
Check Point | AC G-14 Install supply and return ducting and grilles
Check Point | AC G-22 Install supply and return ducting and grilles
Check Point | AC G-24 Install supply and return ducting and grilles
Section | Ground Floor Controllers
Check Point | Install AC controllers AC G-1 - G23
Section | Ground Floor - Observation CCTV Hi-wall fit off
Check Point | Install Hi-Wall
Check Point | Wire indoor unit
Check Point | Install Drain (Drain Pump if required) and test
Check Point | Pressure test VRF system to 500PSI for 24 Hours
Check Point | Vac System to 100 Microns
Check Point | Work out if any Additional refrigerant needs adding
Check Point | Add extra refrigerant that was taken out of system
Checklist | Commissioning
section | Commission AC units
checkpoint | Power on, units vacced and cracked
checkpoint | AC G-7 balancing and airflows commissioned +10% of design airflow
checkpoint | AC G-22 balancing and airflows commissioned +10% of design airflow
checkpoint | AC G-24 balancing and airflows commissioned +10% of design airflow
checkpoint | Unit operated in heating and cooling
checkpoint | Commissioning sheet filled out
section | Commissioning Ventilation Systems
checkpoint | Level 1 SAF 1-1 Airflows commissioned +10% of design airflow
checkpoint | SAF G-1 Airflows commissioned +10% of design airflow
checkpoint | SAF G-2 Airflows commissioned +10% of design airflow
checkpoint | EAF-4-2 Airflows commissioned +10% of design airflow
checkpoint | OAF-1 Airflows commissioned +10% of design airflow
checklist | Project Completion
section | Compliance Information
checkpoint | Airflow test results submitted
checkpoint | Warranty completed and submitted
checkpoint | Procedure statements completed and submitted
checkpoint | As builts updated and submitted
checkpoint | Photos uploaded
section | Manuals
checkpoint | Manual info compiled
checkpoint | Manual Structure and descriptions completed in word document
checkpoint | Word document converted to PDF and relevant info added to each section
checkpoint | Manual submitted to client