## Structure
Tier 1 | Tier 2 | Tier 3 | Tier 4 | resource
Pre start stage |  |  |  | Pre start stage
First Fix |  |  |  | First Fix
Second Fix |  |  |  | Second Fix
Commissioning |  |  |  | Commissioning
Project Completion |  |  |  | Project Completion
After Project |  |  |  | After Project

## Checklists
type | name | values | prefix | postfix | Template Name
Check List | Pre Start Stage
Section | Drawings
Check Point | Saved Drawings into Simpro
Check Point | Read through Specification
Check Point | Programe received and saved in job
Check Point | Units/plant Noted on drawings
Check Point | AC Pipe Sizes Shown on drawings
Check Point | Ducting sizes shown on drawings
Check Point | Penetraions to wall and roof are detailed with sizes
Check Point | Condensate connestions points marked on drawings
Section | Health and Safety
Check Point | SSSP Have been produced
Check Point | SSSP Has been Giving to Lead technican or dropped tosite office
Check List | Firt Fix
Section | AC Pre Pipe - Hi-Walls 1-3 and 5-8
Check Point | Install Pipe work from indoor location to BC Box indoor unit location secured
Check Point | Install Drain
Check Point | Top Plates installed x7
Check Point | Communication wiring installed
Check Point | Electrical power feeds to indoor unit installed
Section | Pre-pipe of Cassette
Check Point | Hang cassette with seicmic restraints
Check Point | Install pipe work to BC box
Check Point | Install drain
Check Point | Communication wiring installed
Check Point | Electrical power feed to indoor installed
Section | Pre Pipe of BC box
Check Point | Hang BC box with seismic restraint
Checkpoint | Weld and insulate BC box pipe work
Checkpoint | Install pipe work from BC box to Outdoor location
Check Point | Install Drain
Check point | Communication wiring installed
Check Point | Electrical power feed inststalled
Check Point | Pipe work under pressure 500PSI
Section | Outdoor AC
Check Point | Pipes to oudoor
Check Point | Electrical power feed installed
Section | EAF-1/RC2 Workshop Extract
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof Cowel Installed
Checkpoint | Fan Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Grille boots installed
Checkpoint | Drawing Marked up for As-Builts
Section | EAF-2 General Extraction Fan
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof Mount Fan Given to builder/roofer
Checkpoint | Roof Mount fan Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Grille boots installed
Checkpoint | Flexible Duct installed
Checkpoint | Drawing Marked up for As-Builts
Section | EAF-3 General Extraction Fan
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof Mount Fan Given to builder/roofer
Checkpoint | Roof Mount fan Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Grille boots installed
Checkpoint | Drawing Marked up for As-Builts
Section | EAF-4 Server Extraction Fan
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof Mount Fan Given to builder/roofer
Checkpoint | Roof Mount fan Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Grille boots installed
Checkpoint | Flexible Duct installed
Checkpoint | Drawing Marked up for As-Builts
Section | OAF-1 Outdoor Air Fan
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof Mount Fan Given to builder/roofer
Checkpoint | Electrcial duct heater installed
Checkpoint | Filter and filter box installed
Checkpoint | Roof Mount fan Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan, Electrcial duct heater and connected
Checkpoint | Mark out Grilles If required
Checkpoint | Flexible Duct installed
Checkpoint | Drawing Marked up for As-Builts
Section | TEF-1 Toilet Extract
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof mount fan installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Flexi duct installed
Checkpoint | Grille boots installed
Checkpoint | Drawing Marked up for As-Builts
Section | TEF-2 Toilet Extract
Checkpoint | Roof Penetrations Marked out
Checkpoint | Roof mount fan installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Electrical feed run to fan and connected
Checkpoint | Flexi duct installed
Checkpoint | Grille boots installed
Checkpoint | Drawing Marked up for As-Builts
Section | RC2 Toilet Vent
Checkpoint | Roof Penetrations Marked out
Checkpoint | Relief cowel Installed
Checkpoint | Ducting installed
Checkpoint | Seismic installed
Checkpoint | Grille boots installed
Checkpoint | Drawing Marked up for As-Builts
Check List | Second Fix
Section | Hi-Wall fit off 1-3 and 5-8
Check Point | Installed Level
Check Point | Drain fitted installed and tested
Check Point | Pipes insulated
Check point | Wall controller installed
Check Point | Wiring indoor unit
Section | Fit off of cassette
Checkpoint | Install face Plate and level unit
Checkpoint | Wall controller installed
Section | Fit off outdoor unit
Checkpoint | Install pipe work
Checkpoint | Pressure test system to 500PSI for 24 Hours
Checkpoint | Vac System to 100Micorns
Check point | Calculate and add Additional charge
Checkpoint | Outdoor unit Level and secured
Checkpoint | Unit Wired and ready for commissioning
Section | Install grilles
Check point | EAF-1 -Grilles installed
Checkpoint | EAF-2 -Grilles installed
Checkpoint | EAF-3 -Grilles installed
Checkpoint | EAF-4 -Grilles installed
Checkpoint | OAF-1 -Grilles installed
Checkpoint | TEF-1 -Grilles installed
Checkpoint | TEF-2 -Grilles installed
Checkpoint | RC2 Toilet Vent Installed
Checklist | Commissioning
section | Commission AC units
checkpoint | Power on, units vacced and cracked
checkpoint | Units operated in heating and cooling
checkpoint | Commissioning sheet filled out
checkpoint | Models and serials recorded
section | Commissioning Ventilation Systems
checkpoint | EAF-1 Airflows commissioned +10% of design airflow
checkpoint | EAF-2 Airflows commissioned +10% of design airflow
checkpoint | EAF-3 Airflows commissioned +10% of design airflow
checkpoint | EAF-4-2 Airflows commissioned +10% of design airflow
checkpoint | OAF-1 Airflows commissioned +10% of design airflow
checkpoint | TEF-1 Airflows commissioned +10% of design airflow
checkpoint | TEF-2 Airflows commissioned +10% of design airflow
checkpoint | KEF-1 and KMF-1 interlock connected and works
checkpoint | Ventilation commissioning sheet filled out
checkpoint | Models and serials recorded
checklist | Project Completion
section | Compliance Information
checkpoint | Airflow test results submitted
checkpoint | Warranty completed and submitted
checkpoint | Procedure statements completed and submitted
checkpoint | As builts updated and submitted
checkpoint | Photos uploaded
section | Manuals
checkpoint | Manual info compiled
checkpoint | Manual Structure and descriptions completed in word document
checkpoint | Word document converted to PDF and relevant info added to each section
checkpoint | Manual submitted to client