## Cladding Template
INSPECTION AND TEST PLAN
SITE INSTALLTION | [7 empty] | ITP No. |  |  | Revision No. | REV02
ITP Name | SCN-117 3mm alum parapet backpan and capping |  | Elevation or Area : building A&B East and North
Project | New Footscray Hospital |  | Module. No or Item : SCN-117
Building Ref. | building A&B East and North |  |  |  | Refer to O&M Manual for Project for maintneance and care proceedures for cladding types
Check / Inspection Required |  | Responsibility | Acceptance Criteria |  | Reference Document / IFC Shop Drawing Number AS1562.1-2018 | Frequency of Testing and Inspections | Client | Date | Facadex | Date | Comments
IFC Shop Drawings Approved |  | MPX | MPX / Architect Sign Off
Material Approval |  | MPX | MPX / Architect Sign Off | [7 empty] | Check colour is correct as per shop drawings
(Panels/Bolts/Screw/Washers) delivered to site free of damage and deformation |  | Facadex | Facadex sign off. | [7 empty] | Check colour is correct as per shop drawings
Parapet wall has been installed for cladding |  | Facadex | Facadex sign off. | [7 empty] | If installed off site no gridline available
25x50x1.15 BMT galvanied Z450 top hat has been fixed to the back of the Parapet with M6 anchors @500mm CTS |  | Facadex | Facadex sign off.
3mm alum panel planter gap cover has been installed where there is a planter at the back of the parapet |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
15x50 1.15BMT galvanized Z450 top hat has been installed with blue screws at top of the parapet for the capping |  | Facadex | Facadex sign off.
3mm alum capping (dulux electro bronze flat) has been installed to the top of the parapet |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
3mm Alum back pan in dulux electro bronze flat has been installed to the back of the parapet |  | Facadex | Standard Cladding Tolerance: +/- 3mm for all elements panel to panel, horizontal and vertical up to 2400mm +/- 4mm for all elements panel to panel, horizontal and vertical up to 3000mm +/- 6mm for all elements panel to panel, horizontal and vertical up to 13000mm Expansion & Contraction: +/- 3mm @ every 1000mm in length & height
bottom shroud has been installed to the bottom with M8x60 anchor bolts @500mm CTS |  | Facadex | Facadex sign off.
all silicone joint has been caulked uniformly |  | Facadex | Facadex sign off.
Panel has no scratches/dents/damages to the finish |  | Facadex | Facadex sign off.
HOLD POINT- All Criteria above must be signed off before proceeding
Client inspection of installed product with Facadex representative. Any sighted defects (incurred during installation) to be recorded and subcontractor to be notified within 24 hours of installation. |  | Facadex / Builder | Defect notification via email or chosen coorespondece
Evidence of close out / rectification
(SI / Photographic record & evidence of close out to be attached to this ITP for each wall type)
Sign of only once agreed that wall is defect free
AUTHORITY TO PROCEED
Foreman – Checklist Completed |  |  |  | Date / Time
Coordinator – Checklist Completed |  |  |  | Date / Time
In signing the above the Facadex Construction and Named parties are confirming that all works have been completed in accordance with all the relevant Design Documentation & Specifications.
Facadex Construction located at 13-14 Adams Court Sunshine West, VIC 3020