## res
type | name | values | prefix | postfix | usage count | user addable | template name
checklist | ITP031 - AGL Luminaires Installation | itp |  |  |  | Yes | ITP031 - AGL Luminaires Installation | b92cb116-529f-4d5a-91ef-b8d8e72a6715
section | 1.0 Preliminary Works
checkpoint | 1.1 - Check for correct documentation
note | Frequency: Prior to commencing any activity
note | Acceptance Criteria:
note | • Ensure that all employees and subcontractors are using the latest and complete set of drawings
note | Reference Documents:
note | • IFC Drawings
note | • Appendix K- AGL Specification
note | Inspection/ Test Method: Verify
note | Record of conformity: Drawings
note | IP
note | Responsibility: Site Engineer/Subcontractor Representative
textbox | Date Completed:
checkpoint | 1.2 - Implementation of all measures and controls
note | Frequency: Prior to commencing any activities
note | Acceptance Criteria:
note | • All necessary measures and controls are being implemented, that is PSP, EMP, TMP, SWMS & WP.
note | Reference Documents:
note | • PSP
note | • EMP
note | • TMP
note | • JSEA
note | • SWMS
note | • WP
note | Inspection/ Test Method: Verify
note | Record of conformity: Site and Office Inspection
note | HP*
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 1.3 - Material/Equipment Approvals and Certification
note | Frequency: Prior to Start
note | Acceptance Criteria:
note | • All materials shall be proven to meet contractual requirements prior to acceptance.
note | – Light Bases: The inset light bases must be compliant with the mechanical requirements for load and flange torque tests as detailed in FAA AC 150/5345- 42J for Type L-868 Class 1A light bases.
note | – Secondary cable entry: The cable entry must be arranged to provide side entry of both secondary and earth cables through the base (for termination to FAA style connecting socket and tail within the light base). A separate entry must be provided for each cable.
note | – Earth connection: Bases must be equipped with earth cable connections, supplied with proprietary stainless steel screws.
note | – Fixing stud: The shallow bases must incorporate stainless steel fixing studs cast or screwed into stainless steel thread inserts e.g. “helicoil”. The studs must include self-locking nuts and/or “vibration proof” washers.
note | – Anti-rotation pins: The shallow base must incorporate stainless steel anti rotation pins or other fixtures to prevent rotation of the light top assembly.
note | – Light canisters: Canisters must meet the requirements of the FAA AC 150/5345 – 42J for Type L-868 Class 1A light bases.
note | Reference Documents:
note | • Appendix K- AGL Specification Section 2.3.3 Section 2.4 Section 2.5
note | Inspection/ Test Method: Verify
note | Record of conformity: Datasheet / Material Submission
note | HP*
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 1.4 - Luminaire Foundation Installation
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Installed and Backfilled in accordance to drawings.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E038
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Aconex Reference of ITP submission for Foundation Install
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 2.0 Installation of AGL Luminaires
checkpoint | 2.1 - Setting out of Airfield Luminaires
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Surveyor to confirm location of AGL with IFC drawings and confirm alignment of luminaires.
note | • Existing lights shall be reinstated following the overlay works in their existing location and at their existing orientation utilising the survey data captured prior to their removal before the overlay works commencing.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Appendix K- AGL Specification Section 2.16.1
note | Inspection/ Test Method: Verify
note | Record of conformity: SCP
note | IP
note | Responsibility: Site Engineer / Surveyor
textbox | Date Completed:
checkpoint | 2.2 - Coring
note | Frequency: Each Light
note | Acceptance Criteria:
note | • The core position must be accurately surveyed and marked before commencement of the core cutting process
note | • The core centre must not be removed until immediately prior to installation of the inset light unit base. The core centre must be removed avoiding damage to the surrounding pavement.
note | • As required, Core asphalt to depth as per subcontractor ITC for relevant Method.
note | • Ensure conduits are cleaned after coring of light base and conduit coupling and connections are intact.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Appendix K- AGL Specification Section 3.16.3
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.3 - Installation of Inset light
note | Frequency: Each light
note | Acceptance Criteria:
note | • A jig must be used to install, locate and level the inset light unit base in position in the core hole and maintain the base in position during the curing of the epoxy grout.
note | • Ensure correct light is installed in correct position as per the IFC drawings, this ITP and ITC
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Appendix K- AGL Specification Section 3.16.3
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.4 - Installation of light top assembly
note | Frequency: Each light
note | Acceptance Criteria:
note | • Base to be cleaned of all materials by vacuum process.
note | • Light tops to be installed as detailed on the drawings. Connect the 2 pin FAA style plug and socket as appropriate to connect the secondary conductors.
note | • Nuts and screws must be tightened to the torque to 40N.m prior to returning a pavement area back into service. Measure and record the applied torque for each light.
note | • Records of torque applied to be submitted to Contract Administrator for each installed light prior to returning a pavement area back into service.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | • Appendix K- AGL Specification Section 3.16.4
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC with records of torque applied
note | HP
note | Responsibility: Contract Administrator/Site Engineer
textbox | Date Completed:
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 2.5 - Gap between the light base and pavement
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Gap between light base and pavement to be as per IFC drawings i.e. For Method 3 lights, ensure gap between new light base and pavement not less than 7mm and not more than 19mm (Aconex BecaCPL-CONTIN-000077).
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.6 - Grouting
note | Frequency: Each Light
note | Acceptance Criteria:
note | • The light fitting bases must be fixed using Masterflow 618 epoxy grout or approved equivalent.
note | • The inset light unit base must be maintained properly orientated and level, as specified, throughout the epoxy curing process.
note | • Before opening the work area to traffic the Manufacturer’s recommended epoxy curing time must be allowed.
note | Reference Documents:
note | • Appendix K- AGL Specification Section 3.16.3
note | Inspection/ Test Method: Verify
note | Record of conformity: This ITP Signed & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.7 - Recess Sealing
note | Frequency: Each light
note | Acceptance Criteria:
note | • The final level of the epoxy is a minimum 10 mm below the level of the pavement.
note | • Seal top of recess around light base with Dowsil 888 in concrete
note | • Sealant in asphalt as detailed in IFC Drawing
note | Reference Documents:
note | • IFC Drawings 12554937-E033
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP / ITC/As-Built Documentation
note | IP
note | Responsibility: Site Engineer / Site Supervisor
textbox | Date Completed:
checkpoint | 2.8 - Installation of secondary and Earthing Cable
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Each fitting shall have earthing cable provided
note | – Earthing to be 6mm2 single core green/yellow PVC cable.
note | – Twin secondary cable to be 4mm2 each.
note | Reference Documents: -
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 2.9 - Series Isolation transformer
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Each luminaire / fitting shall be connected to a series isolation transformer in closest SIT duct pit/ junction can.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 2.10 - Luminaire Circuit
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Each luminaire fitting shall be installed on the appropriate circuit as specified in the construction drawings.
note | Reference Documents:
note | • IFC Drawings 12554937-E031 to 12554937-E037
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP / As-Built Documentation
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
section | 3.0 Post Construction
checkpoint | 3.1 - Equipment Survey
note | Frequency: Each Light
note | Acceptance Criteria:
note | • Accurately survey the location of airfield lighting equipment. The survey plan, endorsed by a registered surveyor, must identify the location of all installed equipment in relation to permanent site features and other underground Services.
note | • The survey must also capture all installation details such as the orientation and rotation of visual aids, colour pattern, constructed foundations, etc.
note | Reference Documents:
note | • Appendix K- AGL Specification Section 3.4
note | Inspection/ Test Method: Verify
note | Record of conformity: This Signed ITP & Sub-contractor ITC
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | 3.2 - As-Built
note | Frequency: Each Lot
note | Acceptance Criteria:
note | • Submission of surveyed luminaire position to superintendent prior to practical completion
note | • The final installed orientation of the centre line of the output beam of the inset light unit must be within plus or minus 0.5 degree of the designed orientation.
note | • Light bases must be installed such that the light is installed within 0.25 degrees of level.
note | Reference Documents: Specifications Section 3.16.2
note | Inspection/ Test Method: Verify
note | Record of conformity: SCP
note | IP
note | Responsibility: Site Engineer
textbox | Date Completed:
checkpoint | Final Inspection
note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
textbox | Print Name:
textbox | Position:
textbox | Date: