## Structure
Id | Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier 6 | Checklist Template
fo:a9cb6af6-601b-4368-99ac-66b3f2d87225 | Enabling Works
fo:2979384e-6b95-4b5d-96ac-85dfba7740bf | Enabling Works | Watermain
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works | Watermain | ITP-0001 (old version) |  |  |  | ITP-0001 - DI Watermain
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain) |  |  |  | ITP-0002 - PE Watermain
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain) |  |  |  | ITP-0001 - DI Watermain
fo:909934ee-a52a-42f8-baa1-3f59cfb1e69d | Enabling Works | Ducting
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas) |  |  |  | ITP-0003 - Ducting
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone) |  |  |  | ITP-0003 - Ducting
fo:69e270e6-77be-43ab-9ee3-27115f9a1565 | Zone 1
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 |  |  |  |  | ITP-1001 - Installation of Manhole - FSMH-A2
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 |  |  |  |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B |  |  |  |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B |  |  |  |  | ITP-1004 - Installation of Manhole - WCMH-2B
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A |  |  |  |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A |  |  |  |  | ITP-1006 - Installation of Manhole - WCMH-2A
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 |  |  |  |  | ITP-1007 - Installation of Manhole - FSMH-A1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 |  |  |  |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 |  |  |  |  | ITP-1009 - Installation of Manhole - WCMH-1
fo:379a6e6f-8f87-4ead-bc2d-24b8a207ebdd | Zone 2
fo:8da39b9e-a8d9-43be-83d8-f1bccdc0920d | Zone 3
fo:84c8e888-edda-4ab4-ae29-8b147854e947 | Zone 4
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection |  |  |  |  | ITP-4001 - Brick Barrel Corbel Connection
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 |  |  |  |  | ITP-4002 - WCMH-5
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 |  |  |  |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4
fo:9df11b22-9025-4194-a698-512b0aab5aa1 | Zone 5

## Checklists
Id | Location | Checklist Name | Status | Checklist Template | Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier 6
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | In progress | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | In progress | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | In progress | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | In progress | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | In progress | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | In progress | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | In progress | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | In progress | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | In progress | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | In progress | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | In progress | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | In progress | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | In progress | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | In progress | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | In progress | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | In progress | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | In progress | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4

## Checkpoints
Checklist Id | Location | Checklist Name | Section Name | Checkpoint Name | Checkpoint Status | Signoff Status | Checklist Template | Tier 1 | Tier 2 | Tier 3 | Tier 4 | Tier 5 | Tier 6
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Ductile Iron Pipe Installation | Not started |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Embedment zone | Not started |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Backfill and Compact | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Pressure Testing (non-PE pipeline) | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Disinfection | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - As-Built | Not started | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5fb3577-6026-414a-9589-be5283d6ae1a | Enabling Works > Watermain | ITP-0001 (old version) | SECTION 6 - COMMENTS | Customer Release Granted | Not started |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | ITP-0001 (old version)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Passed | Approved | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Pipe Installation | Passed |  | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Embedment zone | Passed |  | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Backfill and Compact | Passed | Open | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Pressure Testing (PE pipeline) | Passed | Open | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Disinfection | Passed | Open | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - As-Built | Not started | Open | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:f5d66454-0dc5-4e52-a58a-b67304eefdef | Enabling Works > Watermain | 561466-DOW-ITP-0002 (ridermain) | SECTION 6 - COMMENTS | Customer Release Granted | Not started |  | ITP-0002 - PE Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0002 (ridermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Passed | Approved | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Ductile Iron Pipe Installation | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Embedment zone | Passed |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Backfill and Compact | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Pressure Testing (non-PE pipeline) | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Disinfection | Passed | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - As-Built | Not started | Open | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:ad727b3e-fbf5-4d9c-8f00-2d2859c946a3 | Enabling Works > Watermain | 561466-DOW-ITP-0001 (watermain) | SECTION 6 - COMMENTS | Customer Release Granted | Not started |  | ITP-0001 - DI Watermain | Enabling Works | Watermain | 561466-DOW-ITP-0001 (watermain)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Passed | Approved | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Duct | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Embedment zone | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Backfill and Compact | Passed | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - As built | Not started | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:3b817f8e-2823-4f6d-b1b5-b819a04c0755 | Enabling Works > Ducting | 561466-DOW-ITP-0003 (Gas) | SECTION 6 - COMMENTS | Customer Release Granted | Not started |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0003 (Gas)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | In progress | Approved | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Duct | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Embedment zone | Passed |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Backfill and Compact | Passed | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - As built | Not started | Open | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:63f1d066-3c90-4ed6-9b7b-9187529ce5ba | Enabling Works > Ducting | 561466-DOW-ITP-0004 (Vodafone) | SECTION 6 - COMMENTS | Customer Release Granted | Not started |  | ITP-0003 - Ducting | Enabling Works | Ducting | 561466-DOW-ITP-0004 (Vodafone)
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | In progress | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill / Bedding Material | Not started |  | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Passed |  | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - MH Installation | In progress | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Not started | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:29b9a329-1b4b-4f87-9778-4ed8e4d1c69b | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Red pen markups | Not started | Open | ITP-1001 - Installation of Manhole - FSMH-A2 | Zone 1 | 561466 -DOW-ITP-1001 - FSMH-A2
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill Material | Not started |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Pipe | Passed |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Laterals connections and installation | Not started |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Passed |  | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - CCTV | Not started | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Leak testing | Passed | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:f72b5030-8f8c-4c3f-b36d-cba2f23bcedd | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - Red pen markups | Not started | Open | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | Zone 1 | 561466-DOW-ITP-1002 - FSMH A2-A1
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Passed |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | In progress | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill Material | Not started |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Passed |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Pipe | Not started |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Laterals connections and installation | Not started |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Not started |  | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - CCTV | Not started | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Leak testing | Not started | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:3ee1d906-e6d2-455c-8b11-7afeecb926c7 | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - Red pen markups | Not started | Open | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | Zone 1 | 561466-DOW-ITP-1003 - WCMH 3A-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | In progress | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill / Bedding Material | Not started |  | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Passed | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Passed |  | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - MH Installation | Passed | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Not started | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:791456cd-cfec-463b-b2b5-3c3df31c946b | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Red pen markups | Not started | Open | ITP-1004 - Installation of Manhole - WCMH-2B | Zone 1 | 561466-DOW-ITP-1004 - WCMH-2B
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill Material | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Pipe | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Laterals connections and installation | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Not started |  | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - CCTV | Not started | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Leak testing | Passed | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:93cade8e-424b-4409-b1f2-ee857adda8d2 | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - Red pen markups | Not started | Open | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | Zone 1 | 561466-DOW-ITP-1005 - WCMH 2B-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Passed | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill / Bedding Material | Not started |  | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | In progress |  | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Not started |  | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - MH Installation | Not started | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Not started | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:820c8840-5570-4ffa-ae25-4d6cf4b7e719 | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Red pen markups | Not started | Open | ITP-1006 - Installation of Manhole - WCMH-2A | Zone 1 | 561466-DOW-ITP-1006 - WCMH-2A
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill / Bedding Material | Not started |  | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Not started |  | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - MH Installation | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:68d373a1-632e-4870-a79b-5902ad606bdd | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Red pen markups | Not started | Open | ITP-1007 - Installation of Manhole - FSMH-A1 | Zone 1 | 561466-DOW-ITP-1007- FSMH-A1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill Material | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install Pipe | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Laterals connections and installation | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Not started |  | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - CCTV | Not started | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Leak testing | Not started | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:dbffd4d7-279a-4d6d-89a7-5ea87230f14f | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - Red pen markups | Not started | Open | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | Zone 1 | 561466-DOW-ITP-1008 - WCMH 2A-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 3 - RECEIVING INSPECTIONS | 3.3 - Backfill / Bedding Material | Not started |  | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Not started |  | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - MH Installation | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:17ae9e0f-2e4b-4e46-998a-f2b35c9d7029 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Red pen markups | Not started | Open | ITP-1009 - Installation of Manhole - WCMH-1 | Zone 1 | 561466-DOW-ITP-1009 - WCMH-1
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | In progress |  | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | Not started | Open | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Install corbell | In progress |  | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Install Pipe | In progress |  | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Not started |  | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:cb42921c-17a2-4eac-a8d0-00d7fa65ecc6 | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - As built | Not started | Open | ITP-4001 - Brick Barrel Corbel Connection | Zone 4 | ITP-4001 - Brick Barrel Corbel Connection
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | In progress |  | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Foundation | In progress |  | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Bedding | Passed |  | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Chamber Installation | Passed |  | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Benching | Passed | Open | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Backfill and Compact | Passed | Open | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - Leak Testing | Not started | Open | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:173e7572-cb6a-4d4c-a5e2-351f439e6735 | Zone 4 | ITP-4002 - WCMH-5 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - As built | Not started | Open | ITP-4002 - WCMH-5 | Zone 4 | ITP-4002 - WCMH-5
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 3 - RECEIVING INSPECTIONS | 3.1 - Material Delivery | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 3 - RECEIVING INSPECTIONS | 3.2 - Set out | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.1 - Trench Excavation | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.2 - Geotextile | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.3 - Foundation | In progress | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.4 - Install Pipe | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.5 - Embedment zone | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.6 - Bacfill and Compact | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.7 - Reinstatement - 326 Floor | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.8 - Reinstatement - Carrigeway | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.9 - Reinstatement - Footpath | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 4 - IN-PROCESS INSPECTIONS | 4.10 - Reinstatement - Kerb and Channel | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.1 - CCTV | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.2 - Leak Testing | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.3 - Red pen markups | Not started |  | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4
cl:92424d1c-4057-48c0-92ab-0c9c96a626bc | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4 | SECTION 5 - FINAL INSPECTION AND HANDOVER | 5.4 - As built | Not started | Open | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | Zone 4 | ITP-4003 - WCMH-5 - WCMH-4

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name | Usage Count | Resource Id
/1 | checklist | Installation of FSMH | itp | Installation of FSMH | 0 | 101e7a70-5cf6-49e2-9986-bd77c7bda164
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
806abcb6-a4fb-5349-9283-a2536c8bc7cc | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
8669d3f7-b6d6-5939-90d9-c12c0b0b1805 | note | Acceptance Criteria - Items are approved as per contract specification
084674f2-8ece-5416-b6b2-a6bd25b79931 | note | ○ DCC approved
8496239c-b7dc-5ab1-a142-bf9b50bc09ed | note | Verifying Document - Photos, delivery docket
6ec60bff-375a-55c9-9471-852b0e2d9cf1 | note | Frequency - On Delivery
33b800ec-d486-54ad-b320-c81e2e03e6c0 | note | Inspection Type (Visual, other) - Visual
beb6820b-eadd-5301-b91e-1fc9f3ba0aae | note | Inspection: Key - C
85e1e50b-119a-54bf-b55b-4ab7a294adeb | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
239bdc79-e281-5263-be7a-c007f446e2f2 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
4789a771-1312-53e1-bfbc-913c4e8e9f34 | note | Acceptance Criteria - Allignment set out matches drawing C4400 or aggreed with the Engineer
1cc5fe31-66bd-5642-9ed2-1174cadd9bb7 | note | Verifying Document - Survey marks, photos
7ef3b481-1d15-540f-a3b7-fc41d9528d2b | note | Frequency - Prior to commencement of works
445bd94e-354d-51f7-a3fa-83abdb0c8278 | note | Inspection Type (Visual, other) - Survey
d2630a7c-41e0-5a4d-8b79-1849e680b9d9 | note | Inspection: Key - H
fdbc06bb-29e7-5dbe-bb16-30c52a361fad | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
04555d56-2a87-5bd2-b3a4-c63fd90661f0 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
6ffc00f4-a4b5-50e2-8ed8-cf4bb471fa66 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
08b60273-975b-59d9-991e-db2d5f154800 | note | Verifying Document - Delivery dockets, photos
4d5669ff-3a40-564a-b367-1229d5b29869 | note | Frequency - On Delivery
f4c1bc6f-a6b9-5282-b3c2-9ee0ec888446 | note | Inspection Type (Visual, other) - Visual
8849bef0-2894-5b1f-aa47-ab272fe6b3e0 | note | Inspection: Key - C
2d348209-830a-533c-b2cb-33a9176baef1 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
18e9a7a2-b731-5832-b156-742c33b5f4b0 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4400
5fea94fd-37d8-58d9-adcc-4b0960a0f2a4 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
7f43a1f4-eced-585a-9848-277a5413e3f8 | note | ○ Floor of Trench to be even across width and length
7dac419b-a2c1-5061-8eb3-8e2fe0f69030 | note | Acceptance Criteria - As per 561467-TW-04-DRW-02
3baf211e-25b2-5839-95a8-e35a0bcee911 | note | Verifying Document - Photos, measurement checks
d78f00b3-2675-51ff-9e82-dcc18b43a443 | note | Frequency - During Installation
656f4ca1-bf71-5ceb-a2ee-a47a43478424 | note | Inspection Type (Visual, other) - Visual
709665d1-1aa0-5554-8850-81d901359ae9 | note | Inspection: Key - V
39450a6a-1d07-5a05-bfce-094a739c248d | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
7a0456fa-aeea-5401-9aa3-1c17816e1e58 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
920e8675-2abc-55fa-8cca-11f1aed26ce4 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
8e48f1fd-c1de-5185-bc84-70d2c5a3db1a | note | Verifying Document - Test results
1953cef0-a40e-57f9-890e-b357ef9b6583 | note | Frequency - During installation, per 20m
e22adcef-e4cf-53c3-99d9-6a420799ecf0 | note | Inspection Type (Visual, other) - Visual, On site test
98ae311a-245f-57e1-9fad-1b8e8892ad56 | note | Inspection: Key - H
e97f1f00-2966-5efb-ae0c-9922fc4b2702 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
78ed13b0-8a03-5ee3-8997-781459559776 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
6d649f94-08f9-5be0-aae1-c24bd7d10a6f | note | Acceptance Criteria - Bedding to comply with requirements
437508f5-7db2-5df2-b967-ab7a7b5911cc | note | Verifying Document - Photo
591a1b3d-ba00-5677-a48d-cc67323c7135 | note | Frequency - During installation
65c94e26-7882-5acb-b501-ff35a8beac81 | note | Inspection Type (Visual, other) - Visual, Measurement Check
a808f533-8169-5d4d-848c-37053220432e | note | Inspection: Key - C
f7b3c87b-e466-57a0-9aeb-6595fae363bd | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
c9a4cad1-f83d-5de0-a1bb-6f12bd0511f3 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
332d8a9c-647e-5a81-ab6a-3730b0c64c7e | note | Acceptance Criteria - Final levels are in accordance with the C4400 or within tolerance and agreed with the Engineer
0b230306-490b-5f77-a62e-ae7640a5da13 | note | Verifying Document - Photos, As-built
dbf55a3e-102b-5a1f-a5c3-b5a2ab8bcaed | note | Frequency - During installation
8f0f9f10-3d98-5f69-8152-c9645eccac27 | note | Inspection Type (Visual, other) - Survey
fe0ba045-d981-561d-bc8e-08fe2b5543ac | note | Inspection: Key - H
939ac9c7-32fe-53a7-ac5e-e793731a72bb | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
4790fff2-db43-59c7-a38d-41ee5396ecba | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
4955340a-15fb-506b-8eba-865e7f8fa33c | note | ○ Benching shape to have smooth transitions at bends and junctions
0ee5c2bd-cc2f-516a-9e2a-0a7711bb7917 | note | Acceptance Criteria - Benching built up to the specifications
ad316f58-4c66-5233-8bfd-fb82efe1f5de | note | Verifying Document - Photos
f9c8dc7f-a2b1-5f24-a55d-661207c48279 | note | Frequency - During benching contruction
8a4b059a-2f36-50b8-894d-b677f6684b9c | note | Inspection Type (Visual, other) - Visual, Test Results
efc5144c-0215-5565-87e1-b8c3dc5a8ce2 | note | Inspection: Key - H
506e0f61-82db-50e5-8dc3-96132d1fb8c9 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
ddff2752-76d7-5533-ac35-92ff0d581551 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
f5a055c0-29a5-55e2-ae7b-c249238206c5 | note | ○ Compaction testing one test every two layers as required
8566b8f9-00b8-5641-9d03-1e99cea4b1cf | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
13201b33-ba4e-57e6-905c-279fc74ff298 | note | Verifying Document - Photos, Compaction test results
87f5eddc-01fa-5da9-9b24-56561ecac1ee | note | Frequency - During Installation
f65b7fd7-4f7a-53a0-bfce-8e9708847b2b | note | Inspection Type (Visual, other) - Visual, On Site test
5acf7857-6691-5b91-8a24-1f549c56f0cf | note | Inspection: Key - H
9d6c98ca-ef73-5c98-b50c-07dfd8224d13 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
850b2fac-0fce-5340-b346-95d1164e4540 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
789b91bc-5d07-5632-bb3e-756b9fb335ab | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
20baa76e-1cdd-5bc3-a7af-3b663a7d2ed2 | note | Verifying Document - Photos, test records
a8d70236-5974-5188-bb6a-994031c4c6b5 | note | Frequency - For every manhole
222d4908-3230-5033-8976-f6891d4b6579 | note | Inspection Type (Visual, other) - Test, visual
455f92d4-5ceb-564b-abd0-779b3e829fa4 | note | Inspection: Key - H
b0c3feb3-70e6-5129-95ca-d2996b5e6c7e | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
eee18487-5694-52f0-aa6e-e837caa7b0dd | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
2a89bca2-b19f-5b5d-9bb4-652fa178e835 | note | Acceptance Criteria - Signed ITP
6635c531-831b-5fce-9f78-37e20c29636a | note | Verifying Document - Red pen markup drawings
99eef058-390a-528a-a588-71d1b784d1bf | note | Frequency - After installation of FSMH
736baeb7-d8e6-5c5c-a6e3-e6fd6697687e | note | Inspection Type (Visual, other) - Document
8af5d5ba-4f8e-5ff0-8612-c2ba6ceb4ca1 | note | Inspection: Key - H
b7578470-37a7-50d1-b577-b49b5b6ac24b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of PVC FS Pipe - 150 | itp | Installation of PVC FS Pipe - 150 | 0 | fe284491-7fe6-4cd1-9710-1531ab29d18b
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
d1aad332-a1e4-5c39-844c-e5a5db1b946b | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
08906e01-3edd-5a32-bf96-8a63463d2fea | note | Acceptance Criteria - Pipes shall be DN150 SN16 PVC-U rubber ring jointed
19f70051-bb22-5246-b249-04823dd54164 | note | ○ Items are approved as per contract specification
ffc18c0a-f4c8-5000-8ec4-6c728b7b34a1 | note | ○ DCC approved
2c3e2f33-433e-585c-b9b4-feaeab334465 | note | Verifying Document - Photos, delivery docket,
cdab3b7d-f88d-5534-8375-04239f26c08a | note | Frequency - On Delivery
bde35e1c-2b2c-5cd7-a12a-d0717b72750e | note | Inspection Type (Visual, other) - Visual
a5defbc7-54f9-52fd-8952-667792c62ba4 | note | Inspection: Key - C
d412b73e-071d-5798-864a-69e9b4999fd7 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
5a3750d4-f0ab-582f-8ae9-365dc5ffaa45 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
2d7aa9d8-eefd-5e68-b7c1-0920e0e0f373 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
d732b190-59c8-5d7c-bb18-712d7019346f | note | Verifying Document - Survey marks, photos
64513892-b9c5-583b-b8ab-5445d2c12816 | note | Frequency - Prior to commencement of works
74988986-50c0-5e87-a7f8-feab8d0ea615 | note | Inspection Type (Visual, other) - Survey
21cd077f-24db-5d62-be68-e39d2404bc90 | note | Inspection: Key - H
fdb00da6-e3e8-58c1-a74b-a1ae997c6134 | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
5d5514d5-f35b-5d19-a6c2-bb7635574d43 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
d6d7df0f-681c-5c83-9d8b-94a329605502 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
8638483e-fb18-5f24-9771-47c051477342 | note | Verifying Document - Delivery dockets, photos
e0cec859-ecdd-5bcf-8de3-8c634e32fbe4 | note | Frequency - On Delivery
0cc98695-3b0b-5b10-b316-d6dfb3b50011 | note | Inspection Type (Visual, other) - Visual
4a30abf2-72f4-57db-89cd-5ea7efd1fcc8 | note | Inspection: Key - C
2a235a1d-20d1-5b84-be40-0300428003bb | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
4c545968-ce42-59c3-88e9-d5dcb91cf538 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4400
afb22747-7c5e-537d-bfbd-7228967cae94 | note | ○ Floor of trench to be even across width and length
d41a8945-f0b7-562a-ade3-92edd0b303a4 | note | Acceptance Criteria - Allow 100mm for bedding
690e8899-db70-5aca-a2de-a2ba28ef8a0b | note | Verifying Document - Photos, measurement checks
7d74d50f-d80d-5a05-b72b-6cd89c476caa | note | Frequency - During Installation
e4fd7dc0-a6c2-5ce7-b0e8-8c0ead4a5869 | note | Inspection Type (Visual, other) - Visual
9108c120-35a7-551d-b711-6f3692b97191 | note | Inspection: Key - C
96e5c263-5c25-5633-b80d-5b8411228027 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
3ff3d881-17a9-50f0-a76a-4be464556374 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
f9e3f89a-7c33-5d11-aa60-218f862d7ae2 | note | Acceptance Criteria - minimum of 2 blows per 100mm
7294c653-5f07-5c36-9879-e23dc1b88423 | note | Verifying Document - Test results
d11573f0-0135-571d-a103-7179a80cfaad | note | Frequency - During installation, per 20m
797aefd0-8417-5c87-b215-84adf4229ba3 | note | Inspection Type (Visual, other) - On site test
9d20aea3-94b6-520a-ba02-0991b40186ae | note | Inspection: Key - H
58c63fc1-ebf3-5cf2-8885-08fe3ef7ceb3 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
c21aaf6b-79ad-5523-ab69-50b92abefd9d | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4400
bcedd707-a37c-5770-a7eb-df17d52c7ee3 | note | Acceptance Criteria - Pipe not damaged during installation
f729b3a2-0cae-59df-8f88-503e02178574 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
ac3e7c85-d5a2-5acb-8ed1-e84830d5b23d | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
9c1aa135-688c-58a7-9647-29eebd1a4fc1 | note | Frequency - During installation
6a34eb34-6056-5975-a526-322924302587 | note | Inspection Type (Visual, other) - Visual, Survey
e18435ea-5f0c-531f-9044-c06d6195de55 | note | Inspection: Key - C
466946ed-56aa-5d43-a15c-b03f9e2a153a | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
e8b73336-f841-5961-bd80-a303d97615c1 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4410
09db0af5-5a9a-548c-8da8-0a113619b9c7 | note | Acceptance Criteria - – Lateral connection as per drawing C4410 and DCC standard details and project specs.
4bb5e8ba-bf6d-5fd2-b2f5-581e6e021add | note | Verifying Document - Photos, measurement checks
ab662e7e-5df7-553c-90b7-a70c1feec6bb | note | Frequency - Every Lateral
3e68bdf2-1245-5120-86c2-8db823537b3a | note | Inspection Type (Visual, other) - Visual, Survey
fa1f488e-28d7-5f8b-a825-8bb5e3abf06a | note | Inspection: Key - C
4cc804c9-4144-5482-95c4-bb617138f338 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
403bda69-8a2b-5ef9-a64d-70524fce083c | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
3edd7308-c2ec-587d-9692-3b0043c58768 | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
266de0d8-aaa1-5d42-a1d2-b178ddd0a870 | note | Acceptance Criteria - min 100mm bedding
70417d05-ba6f-52e4-be3f-2c7c793c09fa | note | ○ 100mm overlay
2d8e0c5b-9e92-5392-8ce4-436bcc6c2e14 | note | Verifying Document - Photos
ac6a73de-7a60-58d4-8ee3-e932f03611c2 | note | Frequency - During Installation
5adae2a0-228a-5fa0-88d1-6d8ddc3d6bc5 | note | Inspection Type (Visual, other) - Visual, measurement check
7511f525-9622-5f4a-8a6a-d6c85a7ca071 | note | Inspection: Key - C
860e9474-eaf7-5b77-a98d-2fdf15180016 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
6f4518fa-1b94-5d4e-9f43-b258bf746f67 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
6ebf806e-3685-5296-a896-26d43b97121b | note | ○ Compaction testing one test every two layers as required
522a916a-1ab1-59b7-b329-215c0f40e2cb | note | ○ Conductive signal strip to be laid at 300mm above pipe
ecbe7e15-b6cc-55b0-bdac-87babc8df58b | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
dc739e52-c139-5128-a4d1-b490ffc2b1c3 | note | Verifying Document - Photos, Compaction test results
034a091f-7cdd-5fc1-91e8-d4cd84cc5cad | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
c73294a0-192c-5ec7-8823-15ecaea7d536 | note | Inspection Type (Visual, other) - Visual, On Site test
8b6ff501-430a-57ec-82c0-b15449013063 | note | Inspection: Key - H
97f02921-cd86-5d4d-b9d2-af7e17a754a5 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
eaadebb7-45cd-5dd8-a29a-39e7c5aa7fb4 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
8a34e87e-a923-579f-8e18-d35a653266dc | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
2345c5f0-5fd1-552a-a9c7-ed11f5fe37aa | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
cc4137a5-c9a8-5f5d-a97a-43d62fa9fedc | note | ○ Dips or ponding of water inside the pipe
6d30c3f7-90bf-52e4-a4a5-79d600cf2e92 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
49cb21a3-de6e-51ec-9705-1b2a3e63ecb3 | note | Verifying Document - Test Records, CCTV footage
eb2ff74e-5ce0-5451-b8a3-61a7e80aa74e | note | Frequency - Every section of pipe completed
07e98b8b-c796-50bc-8dc4-c9160bac8bad | note | Inspection Type (Visual, other) - On-Site Test
898e5ab4-e8d1-5c1c-b690-1b3a409bed13 | note | Inspection: Key - H
69ea4496-262b-5221-90a1-6dee803d97b1 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
eaf5206b-5d0e-52e6-9ca3-250de72ec2d5 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
cf7323ce-7fca-5a31-91fb-a212cd63d68a | note | Acceptance Criteria - Engineer Approval
ba01b728-4b76-5913-a9fc-2734f8c1ad2c | note | Verifying Document - Test Records
4eb9f351-bedb-5b8c-978c-158a1247885a | note | Frequency - Every section of pipe installed
46ac5859-38c0-52cc-b9c3-66cdbe8a1971 | note | Inspection Type (Visual, other) - On-Site Test
cf30a5b0-afaa-5143-8342-fdd3bfcaf7d1 | note | Inspection: Key - H
63c10304-4d76-5b6d-9141-d409b43113f1 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
1573bc5a-6804-5629-b663-fd7fe2d616e1 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
c16b0873-5fb4-5e48-a305-46b862d5f8b6 | note | Acceptance Criteria - Signed ITP
458164e3-1c01-56ac-9ed9-645c5dbe40ea | note | Verifying Document - Red pen markup drawings
6c53d47d-5f5c-5b3e-933f-0f7147a17ecc | note | Frequency - After completion of pipe section
ad9fb923-1d3f-5f35-b7b7-3781a4487621 | note | Inspection Type (Visual, other) - Document
9e04318c-c4cd-5bf4-abec-f2eec42da214 | note | Inspection: Key - H
671ab8c5-63b6-5bc8-a5ed-a61cbf6a08d8 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of PVC SW pipe - 300 zone 5 | itp | Installation of PVC SW pipe - 300 zone 5 | 0 | 481f77fe-f8b0-4c6d-9dd1-884aa3d307a4
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
082f7a77-32ee-5678-bf70-b98d2b1e41d4 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
221d00fe-073f-5356-84e4-b92489cd202c | note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
37b41a01-a2aa-5086-aceb-ba2ba130976a | note | ○ Items are approved as per contract specification
9f7321c8-ac91-5618-8110-1ad509ab548f | note | ○ DCC approved
7925cac6-5c26-566b-bd42-43e3dc4095b9 | note | Verifying Document - Photos, delivery docket,
9a6c8770-1206-5e73-a9f0-69534aa307f5 | note | Frequency - On Delivery
fa55f892-b264-5612-a32a-fba44c504023 | note | Inspection Type (Visual, other) - Visual
694c9c1b-1dad-591b-91b4-0f8126b99741 | note | Inspection: Key - C
981eec10-c19e-5ff4-b63d-6cb2ef5ba999 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
5942be0f-2a89-5529-9ca8-15a91e2da718 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
43272ed3-bbe7-57de-9ffb-52c2d3338584 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
70e3bd63-d394-5312-a09b-0aca850ee8cb | note | Verifying Document - Survey marks, photos
548fa1d7-60e1-557a-8eac-7386ad20fae4 | note | Frequency - Prior to commencement of works
43c6d0c1-4a31-5e81-a857-aa5cf0949e52 | note | Inspection Type (Visual, other) - Survey
4d3994c9-dec9-54b9-ab44-6cc6f4a21a37 | note | Inspection: Key - H
7fd60017-7f37-58f7-8374-d0a07d24978b | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
f818c324-1ce7-5843-a34a-d2318a0a0613 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
67029215-521d-53a6-9988-b7b60c84c144 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
23f7f3fe-78ef-565f-9a11-3aa44565c9be | note | Verifying Document - Delivery dockets, photos
9d69f3b6-5a61-5e66-aad7-b7583f7fa9c7 | note | Frequency - On Delivery
b26ccdf5-d51d-58cc-8941-70cd2eefc032 | note | Inspection Type (Visual, other) - Visual
687014ca-6d3d-5ee7-a3b4-3f2e63eb36ac | note | Inspection: Key - C
497c112d-2cfd-53cb-804d-65a564289c81 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
c15e3c80-0188-5218-8592-04f348f39241 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4300
7c8cae7d-d902-5616-bb21-c02c0fe7899c | note | ○ Floor of trench to be even across width and length
d2e14a49-a995-5866-aa27-14493becaa76 | note | Acceptance Criteria - As per 561467-TW-04-DRW-02
2cb54749-2ca0-5362-8f55-eb186b65e6f0 | note | Verifying Document - Photos, measurement checks
02cb6e4f-edc8-538c-95a7-73251c4e0908 | note | Frequency - During Installation
e9387f38-6e62-536b-bfb7-3c57a5e6b59e | note | Inspection Type (Visual, other) - Visual
65c33a04-af56-5042-b8db-77203e78c2b5 | note | Inspection: Key - V
fba71d85-047b-5da9-b433-3dfab6b063b0 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
9f8cd69b-c98b-5137-a03f-9d7678a32a1b | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
f8460167-cc1a-54c5-bc2c-9666cd7164b4 | note | Acceptance Criteria - minimum of 2 blows per 100mm
d6659f5f-7940-5ee8-b13a-e9c09ec40adc | note | Verifying Document - Test results
04c28beb-04cc-51fa-ac1f-38fe47ecb400 | note | Frequency - During installation, per 20m
13985794-9ba9-5d68-b93b-313f528a4451 | note | Inspection Type (Visual, other) - On site test
6ba7bfd4-e76d-5f62-8642-9c83b915e666 | note | Inspection: Key - H
b5b42030-f357-5f23-a44a-ef13ef6d4b90 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
440247ea-0972-59d1-8773-c40be43a353d | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4300
ada453b3-de9f-5385-b115-78b6db73483f | note | Acceptance Criteria - Pipe not damaged during installation
de836f33-e231-593f-ae0c-5ff109197794 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
1c95aabe-26e1-5713-b094-73e183e5e7aa | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
dbfe38c2-eacc-533b-b52e-bd8ea7d2b0ed | note | Frequency - During installation
d2cb5ff1-bb8e-59e8-96c6-e9b9b5ed2deb | note | Inspection Type (Visual, other) - Visual, Survey
9a516002-76e2-56b5-972c-108e9a43a1de | note | Inspection: Key - C
07f27bff-03de-51f1-aee2-16fbc708a188 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
fbadf51f-a182-50fd-b5d9-2cf0e500b74c | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
7f204ec0-c71c-5ca9-b0d2-70ad396a7538 | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
cebd21a4-18d4-563c-be42-54abd7537b3d | note | Verifying Document - Photos, measurement checks
9616ff6c-f492-5832-ae42-5edaf8b01bd3 | note | Frequency - Every Lateral
1aaae5de-8e62-5afc-bfed-82ec89554c59 | note | Inspection Type (Visual, other) - Visual, Survey
ff1ef6fe-8e1c-58cd-b958-43747e687507 | note | Inspection: Key - C
e2fad69a-4625-58a4-b404-d9aa02657a95 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
53b576f8-cd9c-520d-ab4f-7ae4351bb6d4 | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
cab874b0-6b0a-59c5-9391-e6004ad6e79b | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
98ceec9a-2712-5e4c-8be8-d32bc4767d0a | note | Acceptance Criteria - min 100mm bedding
8ddaa936-8b6f-51f9-b9d5-9599ce60bb6e | note | ○ 100mm overlay
4ad8c588-ba8c-5a0b-aaae-32cbb8aa0055 | note | Verifying Document - Photos
404ff335-a86c-58ca-9e0e-87d4a83d5e89 | note | Frequency - During Installation
46455dc0-a9f9-5516-810d-b01131a1152e | note | Inspection Type (Visual, other) - Visual, measurement check
1e6bbd63-fdc6-5717-947f-a602e956d059 | note | Inspection: Key - C
3b076346-8070-5c4a-8e6a-b82445a87714 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
72852d2d-368c-53b8-8ef5-d3edfa97c28b | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
6225a35e-f0a9-5f39-900d-76a50fd70211 | note | ○ Compaction testing one test every two layers as required
629257da-2f65-5dde-99f2-722ea55c75f9 | note | ○ Conductive signal strip to be laid at 300mm above pipe
1470fd82-c5f0-5f6d-b13a-80603d656507 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
11e4e1ad-b3ae-5185-9158-0a52a4474015 | note | Verifying Document - Photos, Compaction test results
0078595a-bcbe-50f4-8cb6-4ba6733fc415 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
517c3b25-cf6a-5f2b-8d90-3cf3c27f4374 | note | Inspection Type (Visual, other) - Visual, On Site test
bac512fc-b019-5468-beb9-2cabfb96dca8 | note | Inspection: Key - H
5ff82f1a-eb48-5d20-896c-f39de3a7d473 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
f74bb165-be50-5a2e-87e6-2ae421cab33c | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
935a1062-a002-5e89-b07d-a1bddbb51581 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
e59a2812-95ad-50da-8bc3-1fa63740b336 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
9364810a-e30f-5f71-9f87-ee5d357d34df | note | ○ Dips or ponding of water inside the pipe
6975c4c0-ba28-5e54-a2bd-9bbd93fa33b0 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
d2796cf0-565a-5bb3-9f9a-624623921183 | note | Verifying Document - Test Records, CCTV footage
8dc9e19e-9e1c-55ef-a7c4-e9d7b784cbac | note | Frequency - Every section of pipe completed
15642883-fe08-5b86-a9bf-919c42da9052 | note | Inspection Type (Visual, other) - On-Site Test
aecebb0d-2053-5471-bf68-d393190eaacc | note | Inspection: Key - H
3409cb06-4dcf-51e6-b3c6-3163dcbb26d9 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
b4ea17e0-164c-5437-9a7a-c05c2f738c7d | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
b143bb35-c05b-58bd-9f8c-b0c5c4f1e2c3 | note | Acceptance Criteria - Engineer Approval
b013c573-56b4-55b4-b0b4-ab1109d595e9 | note | Verifying Document - Test Records
0a05ab94-1f23-5abe-89a8-4926dd9fc480 | note | Frequency - Every section of pipe installed
bc781055-8c55-59ee-9d1f-b22856bf000e | note | Inspection Type (Visual, other) - On-Site Test
68c722f4-ef45-5d53-812e-fb9961688e3c | note | Inspection: Key - H
5582bf5d-f95b-57d1-a6c5-c7eeaecaa98f | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
f5814cdd-613b-5df4-a2a5-774b78d70ac0 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
19ad8db1-95a9-5ec3-aac8-e2b19fd43d5c | note | Acceptance Criteria - Signed ITP
0d357fb1-5add-5a99-b9ca-0190ccb6ad7a | note | Verifying Document - Red pen markup drawings
2bef6e69-c151-59d0-818e-43adb230a4aa | note | Frequency - After completion of pipe section
e4152d81-da6a-54c9-a9ce-93d87bf55759 | note | Inspection Type (Visual, other) - Document
82299ef6-c2f8-532d-94a0-6d5f3ba9563d | note | Inspection: Key - H
dee59dea-0d6a-543f-8c1e-9b21ae7a1cdd | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of PVC SW pipe - 300 zone 6 | itp | Installation of PVC SW pipe - 300 zone 6 | 0 | 20386149-5e99-44c3-98e9-cf36035fd499
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
94759e22-9702-5cdc-abb0-967cfd626285 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
76c2779c-8099-5c7b-a0d3-3e4708db38dd | note | Acceptance Criteria - Pipes shall be DN300 SN16 PVC-U rubber ring jointed
7d3e3d69-a359-531d-8ba6-373279970774 | note | ○ Items are approved as per contract specification
e6a84143-6fb0-5c46-bed1-d7fc68c43daa | note | ○ DCC approved
e4ada77d-10a9-5612-99fb-a8901e748c6d | note | Verifying Document - Photos, delivery docket,
a6019c6a-0e21-5114-8792-76cb8f4edc59 | note | Frequency - On Delivery
be3e1089-6f70-5d43-8a5c-17d27b4acc42 | note | Inspection Type (Visual, other) - Visual
57222b96-a926-5b63-b3af-85afe223cd31 | note | Inspection: Key - C
9026e36c-3b2c-5dcb-93e0-d3f3a35b1eef | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
a4c97ba7-9839-5241-8fe1-81d3d1524c8c | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
c1dfe21b-deb8-5905-b324-abf49b2115ea | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
efaa9208-605a-5a3d-b495-ab5654e4e210 | note | Verifying Document - Survey marks, photos
3e552ee5-1b39-5cd2-a35a-df1dc8891288 | note | Frequency - Prior to commencement of works
63f09636-2b7f-5228-9b95-13b096486c7d | note | Inspection Type (Visual, other) - Survey
9daaf9f8-1d54-5ec2-93c6-b451677c8920 | note | Inspection: Key - H
e142972d-ed5e-5085-856f-f3c3b749f88a | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
af97564f-41a0-5b01-a833-397ca3e5a831 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
fda6308f-d8a2-5a20-b431-da78c495e598 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
7daf7c0b-2e99-5140-8652-f84af64dd951 | note | Verifying Document - Delivery dockets, photos
29865ee5-40a3-566c-abac-a6a388cfbd5f | note | Frequency - On Delivery
26a9d3d3-f695-5fd9-afe4-eca5a322291c | note | Inspection Type (Visual, other) - Visual
3f8c2402-ffd9-5f3d-b21e-de17cd97ad9e | note | Inspection: Key - C
e1e5f8e5-6a16-5d9a-9495-218c64ccedb0 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
b713b4a4-837f-55f7-982e-dac70371db8c | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4301
b6cd4112-23c8-5511-967b-6922d6001820 | note | ○ Floor of trench to be even across width and length
ab85098c-b764-5384-9c47-8a6293f49a1e | note | Acceptance Criteria - As per 561467-TW-04-DRW-02
fc8a7e0c-e0ad-5a29-bd27-ec97096fb88d | note | Verifying Document - Photos, measurement checks
07c2058e-06b2-59e2-9ced-aa3557753ede | note | Frequency - During Installation
694a9ca8-3e9b-59be-99f8-0cf906821b60 | note | Inspection Type (Visual, other) - Visual
988c8acf-b7b3-5efc-a23b-6833e8b97978 | note | Inspection: Key - V
f3b5a650-c147-516c-b12c-a7e80b01ff0a | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
35dec44e-7ec8-5428-a146-44e4f2f2a26e | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
cec294a8-037e-596c-b810-effcaf3c5ac0 | note | Acceptance Criteria - minimum of 2 blows per 100mm
59813bb1-763a-5852-84a3-f697434bb726 | note | Verifying Document - Test results
c20c105b-9c6d-505c-8f87-e5244ffa9e8e | note | Frequency - During installation, per 20m
162e6b99-9617-5ea2-88cd-28ceee360bfd | note | Inspection Type (Visual, other) - On site test
7b8b4125-b3cf-5f0d-90cf-3fac34def982 | note | Inspection: Key - H
0cb616ec-0eb0-5390-a256-ae455c44f4d2 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
34a43318-3a15-5ad6-ace7-19925fd984c0 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4301
607cfb8c-d999-547a-80aa-7c29b733cd13 | note | Acceptance Criteria - Pipe not damaged during installation
57fdbc37-61c1-5dbc-b7f0-f61995ecbdbb | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
d2608011-9421-588e-a16a-edc59d88b11c | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
2be33ea0-360b-5d54-a3bc-4f7af42e0109 | note | Frequency - During installation
525ed10d-9e6b-5a47-85c5-3d691404a033 | note | Inspection Type (Visual, other) - Visual, Survey
b8cd5ddb-a0e4-5a0f-aa24-733f59ee560f | note | Inspection: Key - C
7f265a80-c67a-58e6-9d88-b6e4fb3820e3 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
21d299a7-35c3-564c-874b-ff7749a7fb12 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
0521c1f1-a8e4-5c72-95f8-5707514e4f6e | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
45c7a0bf-5b1a-5ac5-b4fa-b82a44ff4c91 | note | Verifying Document - Photos, measurement checks
bbb7db39-121a-5c42-a088-797abcce8bf8 | note | Frequency - Every Lateral
55a91b12-d578-57b9-98ed-599a6326d7fe | note | Inspection Type (Visual, other) - Visual, Survey
64e270be-6fa0-5397-a40d-069f41db3efe | note | Inspection: Key - C
75383c99-545e-5bf8-9146-941e0d21b290 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
d282f54a-36a5-5cb8-8d4d-a408d45dd3dc | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
4c968b71-9746-53aa-add8-14c0fd29d17b | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
bb4623bf-f0e1-55d6-b100-a0829f0b8cf5 | note | Acceptance Criteria - min 100mm bedding
32d1696b-ede2-5fa3-83c2-35007661df82 | note | ○ 100mm overlay
9006d5c8-28ba-535c-917b-7721f70d8475 | note | Verifying Document - Photos
c28712bd-1306-58f0-9449-d440a1298248 | note | Frequency - During Installation
db754c2d-2210-5efc-a543-d1ae2f710703 | note | Inspection Type (Visual, other) - Visual, measurement check
5d26c296-7992-5a35-a832-df8101368083 | note | Inspection: Key - C
066627ca-9e6d-5ebc-ae30-cfee0fe9d241 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
c36e3c75-2235-5041-b28b-ef657b7ada02 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
9e32dba4-c238-5993-9496-3e5681176723 | note | ○ Compaction testing one test every two layers as required
7dd42f64-3129-5549-876d-5f8c0cae4a85 | note | ○ Conductive signal strip to be laid at 300mm above pipe
1b4c7398-424c-5f1c-b39a-eaf3bac2f020 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1bc9fd6a-0dc8-5071-a1e3-58d6048dbcc5 | note | Verifying Document - Photos, Compaction test results
13177338-6eb9-52fb-b075-d7acb14d825d | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
7154fa08-223f-59e0-8852-0d413c95d016 | note | Inspection Type (Visual, other) - Visual, On Site test
8beb6da6-0d39-5cdb-9532-19363d0fdd6e | note | Inspection: Key - H
ca458392-693e-50bc-be34-9ac0b6342bac | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
4d7b175c-bf4f-556f-905b-470e91a393b0 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
fe7c2571-b7d3-51aa-806f-7332757b98a7 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
53345005-89ce-5e01-a68c-5591a82e615b | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
8e0257ac-43b7-53ef-88ee-428273f291d2 | note | ○ Dips or ponding of water inside the pipe
330fb122-0dfc-5380-814c-c47be0a1a3a3 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
35680c52-e2a3-5e4b-ba43-3e576dd41aed | note | Verifying Document - Test Records, CCTV footage
5b0fd348-a3d5-5845-98e9-c722ce5f7215 | note | Frequency - Every section of pipe completed
715dc3db-bb66-53c3-8a86-300adc5d614c | note | Inspection Type (Visual, other) - On-Site Test
67d46a99-1cbd-5ce5-9368-d93279e895d6 | note | Inspection: Key - H
9a72346a-b1a8-57bd-9a4c-b119ce9fe218 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
690982af-1979-5d88-aa10-b329e2ae083d | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
1cd211c3-1ad6-5445-a36c-d2d453c49500 | note | Acceptance Criteria - Engineer Approval
49ed5472-a786-5c5d-a19f-2b9e891accfd | note | Verifying Document - Test Records
42ebfc8d-1293-502d-8a7b-48272cf19cba | note | Frequency - Every section of pipe installed
9d87c615-cff5-561e-9feb-c92c3892171a | note | Inspection Type (Visual, other) - On-Site Test
f5a07e5d-5673-56d7-ba40-967459eb672d | note | Inspection: Key - H
99d328be-feb9-50cd-8145-ff9ad957d16b | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
503c3cd2-44e2-5151-a965-8fd6f72c0d27 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
4db2d133-6734-5e6d-a89a-d1a9efff86f2 | note | Acceptance Criteria - Signed ITP
8ad0927c-221a-521d-b6d2-a46f56d21f99 | note | Verifying Document - Red pen markup drawings
a54b9d58-1c3f-56cc-96b3-5c85cc160308 | note | Frequency - After completion of pipe section
d1a7f610-0ea4-50bf-949c-f2c7b8c38abe | note | Inspection Type (Visual, other) - Document
210ab3de-64d3-53e0-9451-eed610a19e19 | note | Inspection: Key - H
7e89dc59-f344-58a1-b49d-8151bd7aaddf | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of RCRRJ SW pipe - 750 | itp | Installation of RCRRJ SW pipe - 750 | 0 | 49c89139-1959-4ba4-917a-80be062add06
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
1c8413d4-b49c-5ecd-895d-6e8dc34d3aad | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
1383bd8a-f453-5e31-8d6e-fd2f2e96585a | note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
1c9456e3-137c-5752-bc5d-d1fe1001efbf | note | ○ Items are approved as per contract specification
4176ac9b-cdc3-509d-9240-493bf1558f32 | note | ○ DCC approved
dca21b48-acb1-52cc-be2f-b48c9b1cf891 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
17ac7831-564a-53ac-b023-f3d1d14ffac2 | note | Frequency - On Delivery
7c26fe2e-bb17-55fb-8261-d950aecb88a1 | note | Inspection Type (Visual, other) - Visual
fd7b3979-3b83-5294-a29d-58f2fe5e2ad9 | note | Inspection: Key - C
30d3edf6-2e7b-5ff8-9458-7685050c5fae | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
61bffec7-4f86-5c4c-9901-47a91bc1176c | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
36872f76-f637-5c7f-8e19-8aa1b0d2c9f5 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
7312edd8-9db0-517d-80c6-e771b970ec62 | note | Verifying Document - Survey marks, photos
7a6bbb2c-7425-5a54-b6e4-980724ea38d5 | note | Frequency - Prior to commencement of works
7460d51d-d62b-5ffa-b9d9-b1fd2a41a865 | note | Inspection Type (Visual, other) - Visual, Instrumental
f267761b-2b65-57e8-8005-c9abf5bb1f5d | note | Inspection: Key - H
e3a12127-602d-538b-9a3b-0987c5b7e5f2 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
4b1368db-64ed-5b05-b4f8-f35fe33c66d7 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200
92f40e2a-3e8b-58d2-ac2e-58445be6b7e4 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
23ef9991-c787-5eb7-8ad7-fddbce7da849 | note | ○ Floor of Trench to be even across width and length
acb01e09-3324-5570-9445-ed1c84bf8271 | note | Acceptance Criteria - Allow 100mm for bedding
d8192ce5-099c-51b6-af51-ad9cdda30615 | note | ○ Allow for minimum cover of 750mm.
f66a6b0b-29eb-5e90-8625-1c496c09597a | note | Verifying Document - Photos, measurement checks
ffb2785c-8fa4-54d0-b5ac-ab71d23fa4cf | note | Frequency - During Installation
c73ffc0d-eacc-5bd3-9486-cfe1a943ff64 | note | Inspection Type (Visual, other) - Visual
3b725088-351e-5f8e-9c03-f43c9b43f47b | note | Inspection: Key - C
1d3776f7-b383-5414-994c-4a8a9ff58335 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Geotextile
f7fa959d-9af0-5e81-922e-258547621ff4 | note | Inspection Point: Quality Control Activity - Install Bidim A29 or approved equivalient around bedding, haunch, overlay zone and trench fill up to the subbase.
b441a8b7-7a6c-5e2a-a07c-bd72c8aca36d | note | Acceptance Criteria - Geotextile not damged during pipe installation and backfilling
766027c4-3762-556e-bd6e-84a3495fdd3f | note | Verifying Document - photos
8e45ca11-887c-588c-8e1c-94f524637d63 | note | Frequency - During Installation
8940d78f-c79c-58a7-9e63-eef2cb53ef81 | note | Inspection Type (Visual, other) - Visual
9333cf37-0d3b-5ed6-b0a0-501390db274d | note | Inspection: Key - C
6634a5e9-cab8-5f3e-b3a1-d67a3e9375b3 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Foundation
0d6e3f03-f6ba-5cf7-83df-680b559852bf | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
f21397e3-44b6-5d0b-94c1-71a9bad014f1 | note | Acceptance Criteria - minimum of 2 blows per 100mm
5f9f1e94-4e0c-5bdc-aab3-e705f2846a85 | note | Verifying Document - test results
56073d98-c143-5f83-9be0-b73a96e0be12 | note | Frequency - During installation, per 20m
2d7f812e-54bb-5451-8e48-9954ae287d1f | note | Inspection Type (Visual, other) - Visual, On site test
7365e944-2831-51b6-be32-1a616f0a4004 | note | Inspection: Key - H
6c5425ae-f6d2-563d-8923-c4896051347c | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.4 - Install Pipe
a175a676-cba4-5ebe-a4a7-5c24a4c32089 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
93192164-4413-5d0c-afa8-49cbe4c9a914 | note | Acceptance Criteria - Pipe not damaged during installation
13d510cd-79cb-5e69-a736-7463e24d3f14 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
d8a5e96c-933c-53c0-aff8-d9b6a98e4a77 | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
98512020-1d9f-5306-867b-b4e82e486936 | note | Frequency - During installation
4cc3ec20-4772-539f-bbbe-3e8a93c7d78a | note | Inspection Type (Visual, other) - Visual, instrumental
6fd11b74-4fef-5ead-8bcd-6af73eefb409 | note | Inspection: Key - C
402b29b6-7f2d-596d-862f-70e15af4754e | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
9181bf02-569c-59e6-b1a7-e7d91a7e07ec | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
8fc5c3a4-5f71-579e-814b-150825f8e283 | note | Acceptance Criteria - min 100mm bedding
53d84064-d7c7-5513-87dc-45a6ac7d8871 | note | ○ 150mm overlay
b58cfaac-65ef-564c-b8e7-d1ba68427085 | note | Verifying Document - Photos
a0ea93b0-c253-57df-afd2-d68a9f085ff6 | note | Frequency - During Installation
a662130a-9b76-5c91-85db-5449738e9c15 | note | Inspection Type (Visual, other) - Visual, measurement check
46c8ca14-992d-5957-ac3d-3770caa1d722 | note | Inspection: Key - C
6ce13b07-c091-59c5-93d9-0ad917cc133b | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
b741e121-2949-564a-bbaa-3084b82614c7 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
443ae367-641e-5a44-8148-30ed538f6839 | note | ○ Compaction testing one test every two layers as required
39d32f23-91fe-53b6-b664-ae1e2bceb2c3 | note | ○ Conductive signal strip to be laid at 300mm above pipe
57f495c5-1146-594e-b94a-3e391be7fd19 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
c80dec45-330a-5f2d-b81b-048c713aa44f | note | Verifying Document - Photos, Compaction test results
be9cfd05-01a7-5c67-aa27-fec741928abe | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
0d6fd44f-627a-5d48-8145-8aaff4afb404 | note | Inspection Type (Visual, other) - Visual, On Site test
b1ba0e61-439c-5e0e-9bd4-3e768b02e71e | note | Inspection: Key - H
ca6f3efe-4e43-58b7-a279-335858b9360e | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
97d9c1ed-1cd9-5de3-af01-19e04372d7aa | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
64b76d55-996e-51dc-b438-7670b9e1dce3 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
3f2df9b4-b37a-5265-ac39-6d3b7ac07632 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
799e8383-a58a-5107-9f0f-dbdf59d6ff5e | note | ○ Dips or ponding of water inside the pipe
1ee3db4a-d177-5262-bc72-e9081eb8c87c | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
829f20ef-ffa1-55bd-a373-e73e2761c91a | note | Verifying Document - Test Records, CCTV footage
2b977660-4633-5a0f-ab14-baeccb4af843 | note | Frequency - Every section of pipe completed
aab05216-c53d-566b-b232-1f33992221c4 | note | Inspection Type (Visual, other) - On-Site Test
4876659b-7b7d-5dfa-a0dd-5c1c99a542e9 | note | Inspection: Key - H
d9205ae1-0fa6-5591-8c31-cbdb9ce62b1e | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak Testing
064372e9-a5cb-5f88-9a16-7433171a49d2 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
4789d8ed-c120-52f3-b394-6d742f8c187a | note | Acceptance Criteria - Engineer Approval
c0609867-5893-5d01-bd88-672335e3e5cf | note | Verifying Document - Test Records
ed7599e5-d75c-59de-a701-d8342df80204 | note | Frequency - Every section of pipe installed
108de5e4-4539-53d4-a804-cf54c4ba803d | note | Inspection Type (Visual, other) - On-Site Test
6e8f6ec5-c2ba-525f-8f7d-12368a53518c | note | Inspection: Key - H
055ee4bc-ff22-5969-a134-bd857fdbe4b9 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
76aae70f-9e34-5e15-a889-cc909be3af62 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
0e60ddb8-92fb-5aa9-b7a4-0bcb5748ae89 | note | Frequency - After completion of pipe section
363bce3c-159c-5eda-beed-dd99a07210b5 | note | Inspection Type (Visual, other) -
fdb1c74c-0d95-514d-a33e-9bc169218ea8 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 5.4 - As built
bdabd3da-0281-53d5-96c2-685cb17fa0e8 | note | Acceptance Criteria - Engineer Approval
76182177-46f8-587a-a560-d96a07838efc | note | Verifying Document - QA records
25a35515-e8e8-529e-bf4e-8bc275df2962 | note | Frequency - at completion
a1e7b9df-d9ed-5d92-ad35-05c8b32e9322 | note | Inspection Type (Visual, other) - Asbuilt drawings
50bdcbe8-47e2-5fc8-af33-63599ae1adaa | note | Inspection: Key - H
22711ea8-98b7-59b9-90fc-ee3ff855dba2 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT
/1 | checklist | Installation of SW Manhole Zone 2 | itp | Installation of SW Manhole Zone 2 | 0 | 454a247c-01dd-4d8c-be1d-06d23ff39815
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
a29fa978-018e-5910-9fd9-c2abe424bd81 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
44efb122-50da-5184-83a1-6644b0832b49 | note | Acceptance Criteria - Items are approved as per contract specification
a124ccac-63a5-5037-856e-82e28b828765 | note | ○ DCC approved
47495e5a-2e59-5328-bee0-afa8c2600cb2 | note | Verifying Document - Photos, delivery docket
f46f0672-2f07-5b75-9e4f-b19280511cf4 | note | Frequency - On Delivery
e5b649a2-bb85-505a-b168-29565677b11b | note | Inspection Type (Visual, other) - Visual
93724b38-b58b-5e0a-8907-3d27aaaf3bff | note | Inspection: Key - C
44e7eb58-f566-5b26-8f65-382bc031671b | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
cde0254e-3d81-5145-a5f5-b167f165675d | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
8ac22761-b102-5445-b4e5-d748803ce00a | note | Acceptance Criteria - Allignment set out matches drawing C4200 or aggreed with the Engineer
a38188ae-cf50-5764-9c9e-8928dc9f70b4 | note | Verifying Document - Survey marks, photos
cbeb97b3-d914-54ee-be83-a43349a2644e | note | Frequency - Prior to commencement of works
b195fc0e-79d6-5601-8369-29a7d84dd517 | note | Inspection Type (Visual, other) - Survey
8c2190d1-61d2-5c28-bc53-b0d2d35cd974 | note | Inspection: Key - H
21bf25ec-ef39-58c5-936c-ebe802f410d1 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
4fdeb654-361b-550a-bd23-2c1a788a000a | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
2f6223a9-cd8d-5f0f-9586-4e5cd6477c22 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
d36f3eb0-8591-59b9-8412-9ae07635780f | note | Verifying Document - Delivery dockets, photos
0b7a5cbb-1b66-56c9-b022-2292d4ec06e6 | note | Frequency - On Delivery
b3a71a87-9b26-5e89-acce-e66e7be47dde | note | Inspection Type (Visual, other) - Visual
45aefde4-eae5-5f28-b5f3-61c88fa056b3 | note | Inspection: Key - C
318833e9-18d3-53b9-862e-6bb7ae53ee4b | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
85810065-8af2-5887-a763-6cbdc24251ee | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
75bce559-fa6a-5b26-b9e3-c23642b9f6ee | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
b7573bb5-9bb8-5b52-9332-16e014daedbb | note | ○ Floor of Trench to be even across width and length
4afa819a-40f1-5da1-b982-f49d4a0dcb1f | note | Acceptance Criteria - As per 561467-TW-04-DRW-002
b909a50e-3378-5033-994a-7778c9763473 | note | Verifying Document - Photos, measurement checks
44f14b9b-54f8-50d8-81f1-cd5d78cecea8 | note | Frequency - During Installation
ec891f0e-557c-5255-866d-4714aedf5957 | note | Inspection Type (Visual, other) - Visual
ea5c0f7e-b252-5353-9309-777a291c8ac7 | note | Inspection: Key - V
0fd76793-a9c3-5f0a-83e9-e11ad583b2fe | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
3e20161c-8141-576b-b480-8c2a015ca0da | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
a21b6503-1a26-5dd7-b8f3-edbe7e271855 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
96bf97eb-b433-5abe-878a-0518dec5b47a | note | Verifying Document - Test results
40b0f187-926a-59b0-82a0-178400a6f9d7 | note | Frequency - During installation, per 20m
416d7c62-2c7d-5f7a-9cd6-6a441a862892 | note | Inspection Type (Visual, other) - Visual, On site test
92dcf30b-7722-5237-8101-585ecc864b8c | note | Inspection: Key - H
a438f15f-858b-56d5-8ff1-704c4dda68f4 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
e314dd11-5ac5-5869-8fa0-50ae611dedae | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
e8e97747-7eff-534b-888b-60b7d89951f0 | note | Acceptance Criteria - Bedding to comply with requirements
94216d61-6a6e-5818-bb12-5f2a7fd2480b | note | Verifying Document - Photo
73cea6ff-8e6d-5440-abf2-9076e94302de | note | Frequency - During installation
fb62cdfa-bb79-5fef-8ce6-18b77a02d1f8 | note | Inspection Type (Visual, other) - Visual, Measurement Check
0cf46c90-ef08-5ebf-a70a-ea532642c4ae | note | Inspection: Key - C
76949fd5-e485-5834-8f36-7af1c69eede4 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
1043390d-4d96-5ba3-a3e8-5d91e2d79668 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
917349a0-72bb-51b7-a8ad-2407d4fb5cf9 | note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
5a3b78e5-3f8a-5935-bc1f-5e27c15bf893 | note | Verifying Document - Photos, As-built
79551e70-7982-580a-a212-202f0c9d78c0 | note | Frequency - During installation
16d4994a-ae8c-58d6-b7ec-03d55d4e8ded | note | Inspection Type (Visual, other) - Survey
9a5a94f0-a19c-5050-9200-9e5145dbdd23 | note | Inspection: Key - H
56b7bcf5-daaa-5436-a5c4-e1ff0672ec68 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
bdb5e955-ee00-5aea-a87e-f51af8efac94 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
b7f1fe5d-8830-58d5-ad3b-4d87a6381f01 | note | ○ Benching shape to have smooth transitions at bends and junctions
56b7b1c6-79d9-5246-b6eb-bd62ce32fec8 | note | Acceptance Criteria - Benching built up to the specifications
a81ffc2a-a985-5824-a556-df665fcaeb0c | note | Verifying Document - Photos
a1cc689c-ebad-540b-ae7a-b7bb52abdc8e | note | Frequency - During benching contruction
94caab6a-0498-56a5-81c6-182cb6991e77 | note | Inspection Type (Visual, other) - Visual, Test Results
fbfdf55e-d05d-5b82-8499-8043d8ed3ab8 | note | Inspection: Key - H
50ac113d-709a-557e-a000-5ac0326d796b | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
321614b0-d678-5730-b64b-c2cb6c96f595 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
9f30fc69-192a-5107-9db8-85030d994a69 | note | ○ Compaction testing one test every two layers as required
580fb56a-7cd2-5978-bbd8-41558b175288 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
5c48bacb-fa13-5ca5-9e42-f34caad1a86d | note | Verifying Document - Photos, Compaction test results
6dd2cb8d-5da2-57c9-8c62-9e589ff9d48a | note | Frequency - During Installation
a9206fb2-cd51-5a53-972a-89814436f002 | note | Inspection Type (Visual, other) - Visual, On Site test
a721cf59-d417-51e5-918d-bf63d99a5298 | note | Inspection: Key - H
98c15240-9448-5f0f-ae49-13f210498d57 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
15f3d890-0034-56f1-ba76-4f668b84605d | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
06caffeb-7355-5e8c-a39d-fa40586c5eab | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
2b0342c0-b78e-5995-8a97-7f75ac1f6e0f | note | Verifying Document - Photos, test records
9cba5859-ad8b-5aa5-8273-dc9ebfb61205 | note | Frequency - For every manhole
5e7c398d-85cd-5a63-8934-e9b513ffa03f | note | Inspection Type (Visual, other) - Test, visual
4d9bd547-f318-5391-a6c7-d85049fa66ff | note | Inspection: Key - H
ebfcd9e0-30cb-56a2-9029-e038a0b33ce1 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
492c3ef5-ac79-5405-bbaf-d7c78682dc05 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
8b4571f3-25ce-5633-bd22-8a1331c7671b | note | Acceptance Criteria - Signed ITP
c6a1071d-f5c0-5d7a-b09a-886c254c49f6 | note | Verifying Document - Red pen markup drawings
636e8c50-b853-5ae2-a93a-71449df33dcf | note | Frequency - After installation of FSMH
014f1139-c4b0-53ca-85e7-7332eae7669f | note | Inspection Type (Visual, other) - Document
b73a7f1e-c135-56f5-bdb4-62f11bea8078 | note | Inspection: Key - H
6a8c3dbe-52c9-5996-a92d-fdd1e16dadad | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | Installation of SW Manhole Zone 5 | itp | Installation of SW Manhole Zone 5 | 0 | 0584f785-5a13-4fe1-95f7-447416245fbf
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
ed48456d-38dc-53e2-a8dd-4094c1c77905 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
940d6822-78c1-54a1-b072-b45abc31ef0e | note | Acceptance Criteria - Items are approved as per contract specification
48e1bf1d-9157-518b-bcaf-0f4165da3672 | note | ○ DCC approved
81333b7f-873e-5540-ad8e-190bcc21ca64 | note | Verifying Document - Photos, delivery docket
54538da7-bbb2-52a6-af6f-1af4cbdeaf38 | note | Frequency - On Delivery
06200a2b-b312-5b2d-84b8-8ddc5010df73 | note | Inspection Type (Visual, other) - Visual
92089b0f-4845-54de-b429-30298e2c4e75 | note | Inspection: Key - C
69451d80-0f1b-508b-8e34-c0c64827545f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
8d5aea69-e70f-5e40-9ed9-0890911f45f4 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
1f893f9e-fde9-5f3d-9647-d7c33b05dc37 | note | Acceptance Criteria - Allignment set out matches drawing C4300 or aggreed with the Engineer
4bea244c-8ffb-54f7-8933-2b4ae4f0838c | note | Verifying Document - Survey marks, photos
7cb5e75b-8216-5240-9a3b-d21a00d6e012 | note | Frequency - Prior to commencement of works
3c104ae4-1c1d-5a8c-8d12-7deb5249e0e2 | note | Inspection Type (Visual, other) - Survey
cc1add3c-020c-5ec7-8282-37a531bbc22c | note | Inspection: Key - H
1678b6c5-57a1-546e-8872-d3ad6ffa4456 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
f3b0d134-b8c7-58c3-a6da-1c12ca276411 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
4c6de11c-2e6a-5d80-b8c6-552fd47a4797 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
4d0ef22a-52c6-52df-a9db-8b285dcf4098 | note | Verifying Document - Delivery dockets, photos
7bbf9e74-26d5-5de7-acb4-3e2540a00ef0 | note | Frequency - On Delivery
eb239277-f7a2-5140-9f65-5907b5defc82 | note | Inspection Type (Visual, other) - Visual
68c5559d-57c5-5a03-afd6-d3a5db61df25 | note | Inspection: Key - C
e0e933a0-60ac-5e00-8d6d-4bf04ea05abb | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
8c537452-2139-5018-8d3e-8716c5fb1ebc | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4300
8c021eae-6672-5070-ba44-8cb0ce2670f9 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
a2508ce8-8a02-5b8b-9ad2-2e510313918f | note | ○ Floor of Trench to be even across width and length
ba7ec9ba-e82b-5057-b13a-0e35ccc2b0d6 | note | Acceptance Criteria - As per 561467-TW-04-DRW-002
6dc3d543-ea24-5f79-8aa7-543853943ebc | note | Verifying Document - Photos, measurement checks
e5430870-d58f-5ee6-ad76-b56c45763918 | note | Frequency - During Installation
71c8d5d0-4d95-5db0-8209-3e7d9efd0a39 | note | Inspection Type (Visual, other) - Visual
86b3fd0b-c273-5bd6-84e4-5ab8a80e2d62 | note | Inspection: Key - V
ff35bc3a-e1fc-5cfd-ac96-4bcbbc8b5c00 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
e6569354-8ad1-58d0-8634-3c90d90112fd | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
d7c4c73c-fb74-5dc0-bc51-3893c0cce08e | note | Acceptance Criteria - Minimum of 2 blows per 100mm
7dac7bb5-615a-5797-925d-732bc9e1fcad | note | Verifying Document - Test results
42d183cf-3cea-51f1-a638-9c825b0b166d | note | Frequency - During installation, per 20m
168a7e5e-aef1-525e-8ccc-28befb765c2a | note | Inspection Type (Visual, other) - Visual, On site test
52c7e5e0-3afd-5a95-8a34-b791a43972e3 | note | Inspection: Key - H
3211b1a6-d126-5ed3-9aa3-ad8f6daa76ac | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
3b371ec9-d0bc-57e7-abd7-82cfd80d15a7 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
2dba87ba-e387-584a-a564-a627bc16821b | note | Acceptance Criteria - Bedding to comply with requirements
223534c4-e7a7-557d-985f-4609ffe26a9e | note | Verifying Document - Photo
2e991094-ff11-57c3-910c-b6e3af232e90 | note | Frequency - During installation
fd860daf-ba5c-5521-9d86-c640f887f7df | note | Inspection Type (Visual, other) - Visual, Measurement Check
407baf7c-7a67-5aa0-80fc-5b45a9b9e8f2 | note | Inspection: Key - C
97d64a4c-1c20-5681-903b-1c6f81706802 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
f0fa5038-0455-5d94-be60-5b6d914bee57 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
61227a69-9080-5a93-82ea-4f7fa4b79db6 | note | Acceptance Criteria - Final levels are in accordance with the C4300 or within tolerance and agreed with the Engineer
10ee9b99-dfb2-5e3c-b674-be146a75f287 | note | Verifying Document - Photos, As-built
9f0aed31-b3d0-583c-a64e-4fb7dd397bd5 | note | Frequency - During installation
ad0e7df7-25c0-5cf8-9608-fae46736342b | note | Inspection Type (Visual, other) - Survey
1e6dcba3-5ceb-5b3e-b248-0eec6c1b52b7 | note | Inspection: Key - H
439831af-1bf4-5ff1-b37c-3540270470fa | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
6932a6a3-de5c-5834-ae16-4c426800e72d | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
ed25f9fc-3649-595f-a96c-eed3eec03db0 | note | ○ Benching shape to have smooth transitions at bends and junctions
ab7f8f5c-a323-5e1d-8410-b19893986134 | note | Acceptance Criteria - Benching built up to the specifications
bca6b58e-6a47-5f1d-bf34-cfc86cbee1fd | note | Verifying Document - Photos
9340d5bf-e9aa-5bee-a610-6bff54e8b32c | note | Frequency - During benching contruction
b741d3fd-d2cd-5598-ab85-00ccdaaa5f77 | note | Inspection Type (Visual, other) - Visual, Test Results
786d8327-f5e6-50a9-b284-5f34e63661f9 | note | Inspection: Key - H
a31b2973-433d-5355-8ed3-148a46341116 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
c61ecf00-3e11-5596-97cf-845bad86bef4 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
80b60513-67e0-5a0a-af66-20eeef941d7e | note | ○ Compaction testing one test every two layers as required
e9241055-4c50-5231-97b3-6c448fe50ebb | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
a2177977-2e33-5d08-84d6-1f7438b20e4c | note | Verifying Document - Photos, Compaction test results
37978736-88a0-5c3c-bc2f-6a6f1f0bebd4 | note | Frequency - During Installation
946e4f80-994f-5b7d-a083-6f16c152f507 | note | Inspection Type (Visual, other) - Visual, On Site test
e4ea17e0-fe34-5626-ae8a-37581cba4c8f | note | Inspection: Key - H
d2c96eb6-5cd7-5c6e-be19-518dc03addeb | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
049602c4-082d-58c0-815f-9353d52a8237 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
07d6e719-7af1-5959-a371-3e35d446a2ce | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
4e834d6a-82c2-5c5a-88b9-661c0c4f0079 | note | Verifying Document - Photos, test records
d45618b8-4d32-561c-827b-0c6eb5ce2e74 | note | Frequency - For every manhole
32e69d25-16cf-5b46-891e-8963d563c185 | note | Inspection Type (Visual, other) - Test, visual
512a17a6-c120-5843-86e2-c926ed47be04 | note | Inspection: Key - H
743c5a7c-bab4-5bf1-9605-b717bfedb758 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
6ed2c482-71f7-592d-92c7-697f90303735 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
e3cd0e18-db98-5139-a859-2b1af7c48a01 | note | Acceptance Criteria - Signed ITP
c360fa1f-3f2e-50ee-b109-8534b4b9f5f2 | note | Verifying Document - Red pen markup drawings
4e6158ff-dcd6-5c55-b75b-e121f2a1ee77 | note | Frequency - After installation of FSMH
161d3515-e1d8-542c-98c9-175b6b287715 | note | Inspection Type (Visual, other) - Document
346718c5-98b6-5799-88fb-deb5cb8e425f | note | Inspection: Key - H
0a8ccab2-b39d-50c7-bcfd-166efe1420d3 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-0001 - DI Watermain | itp | ITP-0001 - DI Watermain | 2 | 767915b5-898d-42a5-95b5-d535a75b7515
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
95f0052a-c399-5b13-b0b9-382fd441a454 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
70dfd956-df25-5b7f-86f0-7193b5662c5f | note | Acceptance Criteria - DI Pipes shall be DN150 PN35 with cement mortar or concrete lining
dcb55c98-9f9d-58ec-ade2-b287fbeeb0f0 | note | ○ Material and fittings are approved as per contract specification
1e329314-d334-5eac-ac9e-6cb29ff28813 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials
6a900a08-cf3a-5a34-986b-8d6abbd14ea0 | note | Frequency - On Delivery
8fc40037-93e4-5baf-b841-9b67d77c2c6d | note | Inspection Type (Visual, other) - Visual
807e8f18-403e-57d4-aa8b-df95aa6912b4 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
299af1f6-b465-5cf7-837b-e19ce4fc81d1 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
314918e2-3f45-55aa-8f18-6e5e59f44ed0 | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
e44535bb-5a5b-5708-8ccc-9e5e4c02dbbe | note | Verifying Document - Survey marks, photos
cb3c9eea-9691-54df-b7ba-490d3f53f66c | note | Frequency - Prior to commencement of works
3bfa345e-a230-5232-aa4e-aff9d673994b | note | Inspection Type (Visual, other) - Visual, Instrumental
9433c7f8-1e69-50c6-9616-f12667fdc477 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
59010ff7-a58b-5930-a62f-f7f1aee9fefc | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
7b767845-458a-5cf4-9389-5d9975f8ab65 | note | ○ Floor of trench to be even across width and length
f027339a-c927-5cae-a105-e737961ad5c9 | note | Acceptance Criteria - Allow 100mm for bedding
48b68b52-d794-5a42-b9be-298f7bb284fa | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
81016198-c266-5a3e-aefb-51cf2e8133a4 | note | Verifying Document - Photos
fa9aff56-159a-53fb-a2a3-8cbfa9603454 | note | Frequency - During Installation
4d5a8c12-b117-5105-aea3-4f3537b97130 | note | Inspection Type (Visual, other) - Visual
245cff37-160f-5a3a-892d-c2664137d75f | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
857be670-bc35-536b-a536-03b584ae17ed | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
bce46be0-68f3-5dca-9796-bf7345159e9f | note | Acceptance Criteria - minimum of 2 blows per 100mm
1e8e82ea-d609-5ab8-acbf-c589247e8cba | note | Verifying Document - test results
2b85e972-d27a-5e78-ad4f-7dc08f0d5ee3 | note | Frequency - During installation, per 20m
b149e75b-9ad3-5a32-9894-e58a4acdfae3 | note | Inspection Type (Visual, other) - Visual, On site test
69645629-13c6-51f9-8c76-3ea0f4ba9fc9 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Ductile Iron Pipe Installation
27a1ac53-6186-56a6-b519-35fb8e1c8e7a | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
c4695230-3e9e-52d6-9063-dfc8677fdfaa | note | Acceptance Criteria - Pipe not damaged during installation
dcab95bf-dea1-550d-9902-18556550594c | note | ○ Pipe is centrally located within trench
f7bcbd19-1d01-557d-9316-879d969b6514 | note | ○ Pipe levels are within tolerance and according to the drawings
93e01d6b-2cde-5cc8-b34d-cd87c14b9e4c | note | Verifying Document - Photos, Survey of position for asbuilt
19863c04-fad6-59cc-bce6-0e5f7ad6ae83 | note | Frequency - During installation
6bb84f5f-54d1-5950-84d3-7eb8bd47d653 | note | Inspection Type (Visual, other) - Visual
0ae62b89-b361-51b9-ba5a-211bc7b40731 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
809c1018-e052-592c-8094-c6940702520d | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
3a8be8d3-5271-5443-8885-e836871f838c | note | Acceptance Criteria - Min 100mm bedding
436329b5-94f9-59e1-8dc8-818d7c7cb4b4 | note | ○ 100mm overlay
4cd20966-44a6-569d-93f2-71b0efca2daa | note | Verifying Document - Photos
5584e74a-6509-5ee8-9cea-73acbd196731 | note | Frequency - During Installation
62aaf457-6c46-5554-9926-7e38143346ac | note | Inspection Type (Visual, other) - Visual
fa488abc-db7f-5f8b-8e62-9fe565493efc | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
daaaf144-0ceb-539a-8599-9ae01570e671 | note | Inspection Point: Quality Control Activity - Backfill material shall be AP65
8c67a3f8-1833-50d7-8f4c-f72d9f195f93 | note | ○ Backfill in 200mm layers of compacted material
025b65db-01cf-5584-8039-85fa20e47d3f | note | ○ Compaction testing one test every two layers as required
34c7cce5-59c1-54f8-837a-34ae28ffd96c | note | ○ Conductive signal strip to be laid at 300mm above pipe
474037b9-3d34-5285-82c0-e42f0771aeae | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
32e0dff3-54b2-5883-944c-d5b33858cfc2 | note | Verifying Document - Photos, Compaction test results
dbc37c94-5497-55f6-a47a-7b11fe4236ae | note | Frequency - During Installation, compaction testing per 50m of pipeline
c6157455-9d54-53de-9422-3ae10fb80541 | note | Inspection Type (Visual, other) - Visual, On Site test
43763bde-2eee-599c-87cb-3f1c815a649a | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Pressure Testing (non-PE pipeline)
57ead7f5-36b5-593e-9441-93539912cf78 | note | Inspection Point: Quality Control Activity - Non PE pipelines to be tested in accordance with specifications
b62d67ac-924b-56d9-b8d0-88474c05ea4a | note | Acceptance Criteria - Specification WM 4.6.1: No Thrust block failures, No visible leaks, Do not exceed make-up water limit.
f4b5f43d-7068-547f-a2b9-021a2f91888c | note | Verifying Document - Test Records
3cff9625-4950-5871-a68d-f4e816b21ece | note | Frequency - Before commisioning
cdc40938-3c80-5010-94ad-97c0058da5ad | note | Inspection Type (Visual, other) - On-Site Test
d968d8cb-2885-5a1e-bcaf-d01096beba67 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.2 - Disinfection
4a784473-5f0a-5c40-9386-b5aed470a608 | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
d3be427f-204c-584b-aef1-07069bd4f5b7 | note | Acceptance Criteria - Specification WM 4.11:
716f865d-16f4-52ff-9840-cede1d671e85 | note | Verifying Document - Test Records
a7d1aec7-09c8-50cb-baf6-987c379f0dad | note | Frequency - Before commisioning
34f71a4f-7a08-5861-96da-ccac84ee8382 | note | Inspection Type (Visual, other) - On-Site Test
6fdf1c8c-1d03-5aa7-8875-29064814b7c2 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.3 - As-Built
23f9b5c9-96b0-573e-b1fc-7fe29078b8cc | note | Acceptance Criteria - Engineer Approval
f7fa94e0-15a2-56ec-900b-6ede2571580c | note | Verifying Document - QA records
51c92772-3f69-59c9-a227-d29c46abbc7b | note | Frequency - At completion
28e83814-cc29-5f0d-8ea1-2be2402fecf5 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
27096ed5-7ed3-5ae7-835d-594e7d6f8960 | textbox | Certificate Number:
f3465670-ba4d-5743-98fe-c26ba105d920 | date | Date:
/1 | checklist | ITP-0002 - PE Watermain | itp | ITP-0002 - PE Watermain | 1 | 9834426f-1a5f-47db-983e-6e40f3d0e12e
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
2db0b0ce-8e5c-5fbe-93c8-ac0e778e3993 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
2fd06242-83c9-568c-9e57-3058d29bd0a7 | note | Acceptance Criteria - Pipes shall be DN63 PN16 PE80
8a530a5b-b19d-5b80-a024-b6a0a3107801 | note | ○ Material and fittings are approved as per contract specification
41036e47-785f-5a27-863b-8b426772dbf4 | note | Verifying Document - Photos,delivery docket, MDD results for backfill materials
fdb7957b-1d37-58c0-a66d-bafe66ae53fa | note | Frequency - On Delivery
1767c647-cc30-5c2e-8660-a6ab563654ff | note | Inspection Type (Visual, other) - Visual
a13e224d-dd93-5322-8734-9af4a4037369 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
02cfc7b8-03d2-505a-a322-0eaf3645cf93 | note | Inspection Point: Quality Control Activity - Allignment set out completed by an approved surveyor marked allignment
4e841cb8-1c5f-5108-8458-12fe12a4187c | note | Acceptance Criteria - Set out matches drawings, 2D data and linework provided or aggreed with the Engineer
659acb46-0359-5c53-9dd0-9f650ea6a039 | note | Verifying Document - Survey marks, photos
3f62f40b-f52a-5f30-ac8c-a5459c532fde | note | Frequency - Prior to commencement of works
fbaab756-18a9-583b-be7f-558fd1e0a12b | note | Inspection Type (Visual, other) - Visual, Instrumental
497ae945-d0d1-5bc5-97c5-e153337d57da | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
0e61c345-756e-5b6a-880f-ea58638ca6e4 | note | Inspection Point: Quality Control Activity - Excavate to acheive required depth to invert as per drawing C4500
c1e6df37-3058-50df-9a08-e80d142f2cd8 | note | ○ Floor of trench to be even across width and length
cea94ee6-ec87-5ab5-a2b9-fdc4d191a6df | note | Acceptance Criteria - Allow 100mm for bedding
6f04a03c-6ed7-53f7-9515-f1a6b3a561de | note | ○ Allow for minimum cover of 750mm. Max cover not exceeding 1000mm unless shown on Drawings C4500
61c232e1-4be1-55ca-a956-f06ea936a3c1 | note | Verifying Document - Photos
4251ad0f-a1a5-5ce3-bc01-df379f5125b4 | note | Frequency - During Installation
3759decc-3445-5c6c-a501-1234b1685534 | note | Inspection Type (Visual, other) - Visual
eb7e49ed-4f12-570c-9fa1-dde834716dbf | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
ad5eb550-15dc-56cf-ace7-ab9a959a30f5 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
61ccfc23-29cc-551b-b0ad-c99158fc1679 | note | Acceptance Criteria - minimum of 2 blows per 100mm
38b92c67-1b58-5259-9164-83fd0c1d9cd0 | note | Verifying Document - test results
636e9912-a1ec-5d7e-a283-bcccc04da6df | note | Frequency - During installation, per 20m
72aa5685-db82-5c87-848f-90f2f58b2f86 | note | Inspection Type (Visual, other) - Visual, On site test
72d3e610-6bf4-5f9d-8f0b-c0714cc59497 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Pipe Installation
28c9ca0a-f8cc-5a59-9cb5-2cc5009916fc | note | Inspection Point: Quality Control Activity - Pipes installed and positioned as per design
77affdb4-367f-5448-bb0a-ce3f82baea4e | note | Acceptance Criteria - Pipe not damaged during installation
801c4c87-d32c-55f5-b98e-38ed7551e50e | note | ○ Pipe is centrally located within trench
8a37136d-6e12-59e3-87eb-0b96df871a55 | note | ○ Pipe levels are within tolerance and according to the drawings
ec1537b4-baf7-541b-ae01-35e230dd7b19 | note | Verifying Document - Photos, weld records (if required), Survey of position for asbuilt
d914efd2-344e-5f29-b0ac-643a116cb1d2 | note | Frequency - During installation
0d892a48-e70a-5a4f-ae68-d4ba83a99eb3 | note | Inspection Type (Visual, other) - Visual
17d84d09-354c-57fd-9460-425db729d5f5 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
14662422-d3ab-5a21-9f78-c1b5fb118de8 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
5b6f5399-560a-5b3f-b398-8770fe3088c3 | note | Acceptance Criteria - Min 100mm bedding
4cfcc987-3a20-5b9a-ab89-6f10fa9e251b | note | ○ 100mm overlay
13553891-0ce7-59f7-905f-f0f4e45f9c12 | note | Verifying Document - Photos
b777e6ad-f4e2-551b-9780-4747ddb5f39d | note | Frequency - During Installation
369c27a6-6265-5c04-8c8c-a17f09a6aca1 | note | Inspection Type (Visual, other) - Visual
b1a317ae-c537-5434-8d9a-1d168d1c0e96 | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
c4ed0ba1-45cd-5f87-8bb3-a94300e5252c | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
58d78ea6-92a5-55e3-aa6b-5fdf5c91c0fa | note | ○ Compaction testing one test every two layers as required
1bbadaa9-d47c-52a7-abd6-5ab1b3e4dec3 | note | ○ Conductive signal strip to be laid at 300mm above pipe
90381076-357d-5bcd-9ee2-36d58687dedc | note | Acceptance Criteria - Passing compaction results - 95% MDD backfill - basecourse
c5049d5f-1bb7-5dbb-8328-190ea949f82d | note | Verifying Document - Photos, Compaction test results
3baf512e-9911-52c9-a9d1-bdcfe7f5cbd8 | note | Frequency - During Installation, compaction testing per 50m of pipeline
c612634a-2179-55f9-91c8-3d02e8d3c816 | note | Inspection Type (Visual, other) - Visual, On Site test
8b5d4dc5-63e7-5441-a5b1-90c8de84d468 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Pressure Testing (PE pipeline)
78f58bde-a020-5fab-840f-9364074a50cc | note | Inspection Point: Quality Control Activity - PE pipelines to be tested in accordance with specifications
ea419330-966f-526e-b149-d37a363f0816 | note | Acceptance Criteria - Specification WM 4.7.5: No Thrust block failures, No visible leaks, Do not exceed make-up water limit
d31629db-bf4d-5c9c-83b7-9aa4b43dcf26 | note | Verifying Document - Test Records
444a8ca3-e6b1-581a-9461-77721794adcf | note | Frequency - Before commissioning
dfab7f7f-dfc7-5e06-8561-e54abde1ac1e | note | Inspection Type (Visual, other) - On-Site Test
c2779745-08bd-5ff9-8f8f-3621200b77db | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.2 - Disinfection
31ebd585-0600-5105-a55b-2efd3787d67d | note | Inspection Point: Quality Control Activity - Disinfection to be completed in accordance with specifications
2bbfa808-d004-5f10-8a6a-31c5bedfb862 | note | Acceptance Criteria - Specification WM 4.11:
2abac563-d9f5-5145-bf24-61cd054ac670 | note | Verifying Document - Test Records
8b17f466-8d64-5152-9282-1658bc07d7de | note | Frequency - Before commissioning
c3590ca3-9c03-56a8-a50d-ca3b707cae79 | note | Inspection Type (Visual, other) - On-Site Test
1e13bf72-aa7c-5db8-8dcf-de1c896152d5 | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 5.3 - As-Built
9a06dea4-21a5-59c5-8a35-4e8a1d37d7fe | note | Acceptance Criteria - Engineer Approval
854cd6d9-9402-5cb7-a6b8-60693d45e3bb | note | Verifying Document - QA records
d2df897d-a9a9-5d38-abc9-e9df67d3be24 | note | Frequency - At completion
e8e231ce-2b20-5bb7-b87d-863efc08f0e3 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
24df9a0f-dd3c-547f-865e-fd17b03e5273 | textbox | Certificate Number:
dfba6ae7-ce54-54b8-a22c-0c151a65217e | date | Date:
/1 | checklist | ITP-0003 - Ducting | itp | ITP-0003 - Ducting | 2 | 782dd239-3b1b-42bc-b629-248808801d0c
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
8d902c4c-affa-553e-9f08-490e6074f82d | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
cf5edf52-5433-5344-905e-168289730e73 | note | Acceptance Criteria - Items are approved as per contract specification or as agreed by the engineer
07112d89-e4fb-5f9b-8cd2-45b02ce7fd54 | note | ○ DCC approved
8120143a-a2fd-5c99-97e9-fa8f5dc84740 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
48af411d-411d-5d79-994f-ea06e949c798 | note | Frequency - On Delivery
51064610-ff9c-5dd1-8d53-210c81058b6f | note | Inspection Type (Visual, other) - Visual
91a0b025-3ca9-5e95-b207-8deed9e4b330 | note | Inspection: Key - C
| checkpoint | 3.2 - Set out
ae066ef9-0984-5cd8-a226-1fc349b21f53 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
29a471bc-026e-50ef-bfdd-82a1f17be599 | note | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
d03b60bd-7a6a-5b8a-8f2a-261c3bb411e1 | note | Verifying Document - Survey marks, photos
8115acc6-0430-526a-bcd2-b522390e4e72 | note | Frequency - Prior to commencement of works
5a6f757d-64bf-50f1-b34e-b4a64b39b801 | note | Inspection Type (Visual, other) - Visual, Instrumental
da13be71-93e6-5c68-9559-99a4695e54ac | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
a2397ccb-6c99-525b-a9c5-b77cfec8b051 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth as per Drawing C4600,C4500
ebace46e-95ae-5388-8b10-adda14a6199d | note | ○ Floor of trench to be even across width and length
8b0f67a7-d71c-5c93-9f07-078b21ad0f88 | note | Acceptance Criteria - Allow 100mm for bedding
00c359b0-3f65-53fc-abcb-f815b8c6eec6 | note | ○ Allow for minimum cover of 600mm.
5f50eb37-df33-5a14-b10f-cbf3d6104142 | note | Verifying Document - Photos
02ae92e1-e99d-592d-b198-7379398e529b | note | Frequency - During Installation
f4505258-4ef3-5dd1-8377-5e73e51ca6ac | note | Inspection Type (Visual, other) - Visual
81c8f8e2-28db-58c2-8f50-781bc18966f2 | note | Inspection: Key - V
| checkpoint | 4.2 - Foundation
7c4cb71d-a4ba-52d9-ace5-d5d5ef95ecc1 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
e0953abd-7b7a-5a52-826b-9e5353cf1095 | note | Acceptance Criteria - minimum of 2 blows per 100mm
0b64e85b-26ac-5da8-82ff-a10d18c9758c | note | Verifying Document - test results
5e476bbe-174e-5db4-8a61-817c23738ced | note | Frequency - During installation, per 20m
89391e0a-cd85-5ee2-a490-c202c0328502 | note | Inspection Type (Visual, other) - Visual, On site test
1d9e19ed-acc9-5672-9229-1126fbfc2a3c | note | Inspection: Key - H
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Duct
d3140c32-17e8-519c-8d33-1bf7e6de6e55 | note | Inspection Point: Quality Control Activity - Ducting installed and positioned as per design
7c056b31-b6c5-517c-9d15-c274c7de8440 | note | Acceptance Criteria - Duct not damaged during installation
1accd5ae-0db7-59b9-ba98-629af29a31c4 | note | ○ Minimum of 150mm horizontal and vertical clearence from other services or as specified on Drawings C4600, C4500
a5bc5895-9ab6-5634-a130-3e5d30dd835f | note | Verifying Document - Photos, Survey of position for asbuilt, weld records (if required)
313b1e98-e95e-577d-a6fe-68886d893217 | note | Frequency - During installation
5b80d755-722e-5988-9dd0-c84e17d1ad16 | note | Inspection Type (Visual, other) - Visual
decf6a22-76b6-5ccd-8261-2ee0f90b82d0 | note | Inspection: Key - V
| checkpoint | 4.4 - Embedment zone
f76f3a6c-a88d-54ef-9698-d9cdae1da0d1 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
59a6202a-5885-5d77-849a-34dbe244afc5 | note | Acceptance Criteria - Min 100mm bedding
fc25305e-7973-546a-b8e1-a0f45f8b2303 | note | ○ 100mm overlay
4c335cb2-e8ef-5997-ae01-12952b650974 | note | Verifying Document - Photos
fe7ddae4-2304-52d4-aea7-85e2fa9796f8 | note | Frequency - During Installation
436864b6-e3e0-5ae9-8a61-ce30229de621 | note | Inspection Type (Visual, other) - Visual, measurement check
b8c9868d-7396-5851-a703-0eefd4b14fb1 | note | Inspection: Key - V
| checkpoint | 4.5 - Backfill and Compact
6f28239d-0725-58b0-9012-60710954e9a3 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
bc2bfa89-42ac-5ab9-b44b-c749bdcbc8bc | note | ○ Compaction testing one test every two layers as required
4f37897e-2756-5699-aa29-e1da630280d6 | note | ○ Conductive signal strip to be laid at 300mm above duct
b6d636d5-f794-5b49-b270-bfee37df99ee | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
224ee362-8bfc-57ae-9d94-e9608d14e307 | note | Verifying Document - Photos, Compaction test results
7d9f6647-3a2f-5542-83a4-8ede136a128b | note | Frequency - During Installation, compaction testing per 50m of pipeline
529d52b2-3d85-56ab-a4b3-e9b03517687e | note | Inspection Type (Visual, other) - Visual, On Site test
a77e93be-b2af-5473-91ba-e40b7b14b420 | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - As built
9d816568-a130-5295-b70d-6ef281625964 | note | Acceptance Criteria - Engineer Approval
6f746184-a1ff-5f91-bca3-b1dd4a4d46b5 | note | Verifying Document - QA records
c9f0114c-dd6e-509a-bdde-4dedb0b9b521 | note | Frequency - At completion
61e8da25-482b-5c7a-96a2-b5aa94691a7a | note | Inspection: Key - H
| signoff | HOLD POINT
| section | SECTION 6 - COMMENTS
| checkpoint | Customer Release Granted
c6bfe258-5cf9-5e9c-8e2a-a2346511d9ee | textbox | Certificate Number:
d99bfeec-2811-5b92-95aa-00c28d2a820e | date | Date:
/1 | checklist | ITP-1001 - Installation of Manhole - FSMH-A2 | itp | ITP-1001 - Installation of Manhole - FSMH-A2 | 1 | 2be16ac7-96aa-40fa-b96f-6326dc615acf
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
306c0cad-f080-5f4a-8125-bc0a08f3554b | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
5e5e9327-26c9-59f7-a0c4-99b8a67431c4 | note | Acceptance Criteria - Items are approved as per contract specification
64b73fde-4c6b-5dd9-bf71-c782eac57bc2 | note | ○ DCC approved
9c04f967-2974-5f90-b62d-1ea3b2dfa74c | note | Verifying Document - Photos, delivery docket
5ae2f52f-cf55-51e5-9ce9-595d53c893ba | note | Frequency - On Delivery
1ff3afcb-8a71-5ff8-8164-44363543c4cd | note | Inspection Type (Visual, other) - Visual
d5560565-7f1f-50d6-92ec-1b0164d0f3d9 | note | Inspection: Key - C
28f1a379-17f5-55bd-94fa-db9f689ee862 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
634560bd-2d69-5708-846d-83e4824de234 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
36af7152-0ebc-54aa-9fff-72c3aed35f65 | note | Acceptance Criteria - Allignment set out matches drawing C4400-2 or aggreed with the Engineer
536e8ebd-9bc6-5f46-aea4-f58bff2e201f | note | Verifying Document - Survey marks, photos
210f9cfa-cdb2-55d0-997c-d217bb5208aa | note | Frequency - Prior to commencement of works
f173228a-2625-5da9-8dc3-0f4fe40a5c96 | note | Inspection Type (Visual, other) - Survey
d4dd6ac5-9fe5-5ef8-a262-2019cd8785cc | note | Inspection: Key - H
3489559f-2cce-5044-ac1d-68336808ea4c | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
7d95440b-01a4-5e4c-8197-de8bbd98e036 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
8976d22d-ab0c-5693-bc0a-d9731cd1c680 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
3aaa88cc-82cb-5438-b429-bbe50ab25bce | note | Verifying Document - Delivery dockets, photos
da20e9a3-da29-5395-924b-b0a749585fa1 | note | Frequency - On Delivery
15be0528-629c-5f25-bc78-2861d180a933 | note | Inspection Type (Visual, other) - Visual
dbce0e37-a39c-58db-9199-89fb0acd70c5 | note | Inspection: Key - C
0a7fed2c-e9e2-566d-bcdd-6eee1bd88e1f | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
13443767-b171-52bb-9b22-bd26e7ed259f | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4400
ad0181d3-28d9-5570-98a6-0d95f6e8e56c | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4d541dba-2310-534f-991b-bb46d777fdb3 | note | ○ Floor of Trench to be even across width and length
b3273e85-f3a5-5135-848a-f9eccb508a4f | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
0ab334c8-7193-5835-8747-29e28b6275ce | note | Verifying Document - Photos, measurement checks
f085aa79-2a42-57ae-9a27-e886937a35bf | note | Frequency - During Installation
df162fd0-006e-58a2-8d74-19c37c03037c | note | Inspection Type (Visual, other) - Visual
696eaf74-89b8-5bc2-8526-6312d48fc711 | note | Inspection: Key - V
4fc783ba-64f4-56bc-bb18-f18dc704004e | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
f6777232-5b7b-5e2d-8491-8fbe2d80d2c1 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
0c0f24e6-4d36-56f1-8819-85d1e0140505 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
e1f3da71-b730-5e29-8117-8c70b079c7d8 | note | Verifying Document - Test results
49bdc67e-ab4f-5eb7-90fc-6ad8de95fc69 | note | Frequency - During installation, per 20m
d19e9046-4dcf-5b07-a0a5-7f421d037602 | note | Inspection Type (Visual, other) - Visual, On site test
1e37798f-bf41-58d2-9cdd-f54902bea504 | note | Inspection: Key - H
3d0248ad-d4c1-528c-a2e8-7c12a761c22c | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
c9d10ab0-acb0-5f97-bd7f-f97d7ca9a448 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
082d6c91-7e63-548e-a219-6421e0150690 | note | Acceptance Criteria - Bedding to comply with requirements
a4d1cd79-c590-55d1-9c74-b49b624a8f63 | note | Verifying Document - Photo
91821764-9bc8-5643-a7ba-9b166aeed9e9 | note | Frequency - During installation
52b29eea-0222-5f98-b5f6-140ee01632b0 | note | Inspection Type (Visual, other) - Visual, Measurement Check
3beafa43-a480-5e66-9f66-3762362904d0 | note | Inspection: Key - C
9ed966d4-c1d6-5720-bbcc-2acd909bd7e9 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
1a71b3f4-87ff-5889-8dc7-5fbbc4810e6d | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
517f37f2-80ad-56ca-8279-3debc8ff5fbb | note | Acceptance Criteria - Final levels are in accordance with the C4400 or within tolerance and agreed with the Engineer
bedb719e-fd92-5c4f-962a-cdc24008f4f8 | note | Verifying Document - Photos, As-built
38547d56-e31a-5647-ab1d-05a003ba8501 | note | Frequency - During installation
51beda81-7f79-5608-a8f8-bafffa0b86ee | note | Inspection Type (Visual, other) - Survey
59618335-5b2b-5d04-8b6e-117819aee945 | note | Inspection: Key - H
81f1c5e4-c3e9-53a3-b559-9b502929dd54 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
b3219cf7-d612-574b-971d-53e13f88b152 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
2dba3673-76bc-5e74-ba92-c79e40b173e3 | note | ○ Benching shape to have smooth transitions at bends and junctions
f94713f1-7653-5a86-aff6-00f68488e81a | note | Acceptance Criteria - Benching built up to the specifications
a15c7bdc-75ff-5482-88c8-28918969046e | note | Verifying Document - Photos
701a26fc-74d5-58c5-80c3-68d493129a9e | note | Frequency - During benching contruction
78af94fa-ff65-556d-9996-995449ae6c45 | note | Inspection Type (Visual, other) - Visual, Test Results
beca31e4-8016-555e-a78d-9d83c98d9a9f | note | Inspection: Key - H
935600ea-3c11-5abf-9089-a67f9fac0cc3 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
434b4f16-15f1-5e7c-8dc1-58874eb8ef09 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
c0bc7eda-6fc4-54ea-aa2d-88dc4577719b | note | ○ Compaction testing one test every two layers as required
f807d6cf-c23d-589b-a263-63eeefcc169e | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
a83baf94-efe2-52e7-9fa3-6f237ee77588 | note | Verifying Document - Photos, Compaction test results
12fec790-3c6b-562e-a35d-89a3dba9f20a | note | Frequency - During Installation
76534213-d26e-5cad-830d-4f9797e48734 | note | Inspection Type (Visual, other) - Visual, On Site test
1d68ec6b-9664-573d-bab2-ff657674e3c1 | note | Inspection: Key - H
c1380e7b-92fc-555b-8249-479f03d650aa | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
be47134a-6f1d-59c6-b01a-d0e0a9bdf53d | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
c8643ad4-11cf-5808-bd3c-3a319ba82fb0 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
87972f92-4cab-5704-8c7f-57694c7a1128 | note | Verifying Document - Photos, test records
2b8183b0-bde2-5942-b524-973de5852f1e | note | Frequency - For every manhole
b64c4dcb-02c8-5000-a126-7d418f191efd | note | Inspection Type (Visual, other) - Test, visual
edc6ade1-3864-54ae-aa53-2f459b36d81c | note | Inspection: Key - H
d19dd388-ac1e-52c8-9b3f-a26a6cf52c7c | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
d9233c77-7620-509c-8c4f-1f065171d6de | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
872447f6-1d4d-5ee4-8faa-18daf6729fdd | note | Acceptance Criteria - Signed ITP
54a0857b-d6bc-5c16-93a8-19b5a3bcfc0a | note | Verifying Document - Red pen markup drawings
e8f25ae1-573f-5de9-9e24-2d614e57d495 | note | Frequency - After installation of FSMH
4a407ac5-1fbf-59df-8133-d74aa41d0afe | note | Inspection Type (Visual, other) - Document
4995ff0f-38f6-54d0-b90a-c90a2e1f44a2 | note | Inspection: Key - H
703d6adf-1136-569e-93bc-253dc285dbad | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | itp | ITP-1002 - Installation of PVC Foul Sewer Pipes - FSMH-A2 to FSMH-A1 | 1 | 9cbefc6f-9d1e-4db5-baed-9a0ce868a2f5
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
61b5bdd8-3580-529d-bbe4-cfc6006e6666 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
219f6f39-e8b8-5f98-891e-d10fa24e67fc | note | Acceptance Criteria - Pipes shall be DN225 SN16 PVC-U rubber ring jointed
e71eddb9-520e-5749-b769-ce64bbb63db0 | note | ○ Items are approved as per contract specification
3eb04f50-2b38-5061-9a7b-03e1c6873f1e | note | ○ DCC approved
2336e534-66be-574e-b84c-e4fc229f669e | note | Verifying Document - Photos, delivery docket,
853e3f7f-7d21-58bb-8fdb-ec5c5093cf7b | note | Frequency - On Delivery
3e4d05af-f863-58ed-b509-5bb7aa8f5ab1 | note | Inspection Type (Visual, other) - Visual
e7518008-9018-5ca0-ab26-0f93321d8f0a | note | Inspection: Key - C
c6e7f05c-7da1-54db-ae6c-20911f1efc41 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
daf482b9-51b1-5c27-aff1-e81efd5ee6e9 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
0ca88955-0ef6-507a-a4f2-c1404e6f50ae | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
c0e14c1f-d06a-5c08-85e2-8ac7710ba6f8 | note | Verifying Document - Survey marks, photos
87a64616-68ea-5c81-8b89-07812677e106 | note | Frequency - Prior to commencement of works
2fecf6aa-4788-59b8-8547-e6d7f95b7c4b | note | Inspection Type (Visual, other) - Survey
561f1e6c-da2b-5695-a0e3-6a63decfb391 | note | Inspection: Key - H
f4025978-9c32-52c5-8a33-d864e7b3ced3 | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
536071d2-a4e8-52fa-8cdb-bc6b3e7d8736 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
0b3caadc-e9e1-5cfb-ad86-55af3445bafc | note | Acceptance Criteria - As per DCC code of subdiviison 10324
d68e61f2-bd4d-5b47-a2cf-2c8cc2814268 | note | Verifying Document - Delivery dockets, photos
62e62dae-474f-5cae-8604-92334547a76e | note | Frequency - On Delivery
0ad7fc0c-dcaa-5ec0-8feb-628c1ca89684 | note | Inspection Type (Visual, other) - Visual
21f12d96-e038-5544-a4ef-db9cd03b41f3 | note | Inspection: Key - C
5dd358a7-6380-50e2-b1e8-d44aedda26b3 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
9bc9463a-c701-5972-89e4-35bcfa56ffec | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4400
b64c979f-113f-58cd-84d9-09c4ff38ff48 | note | ○ Floor of trench to be even across width and length
3be77e07-51e4-5eb8-a233-b64da0fce4ae | note | Acceptance Criteria - Allow 100mm for bedding
773af6dc-dadd-5664-8746-be490f977080 | note | Verifying Document - Photos, measurement checks
92c61c43-eefd-5353-a8f2-50be6df188d3 | note | Frequency - During Installation
36ed8a86-e322-5de8-a3c1-6993a12290c3 | note | Inspection Type (Visual, other) - Visual
e5d9e884-e177-5dd0-bb11-db4b05965f46 | note | Inspection: Key - C
095c1330-360f-5aaa-ace9-8577541982b5 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
6da1e4a9-4917-57ee-af7f-34a8119c8a0a | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
fa08b9fc-08ff-5f53-a0da-718759cb48cf | note | Acceptance Criteria - minimum of 2 blows per 100mm
afeac26a-84cc-5a82-bc62-11a6a103cae6 | note | Verifying Document - Test results
ee20234f-619d-50ac-a155-e478077fcb47 | note | Frequency - During installation, per 20m
b480bf64-3da6-599a-8e6c-65a6283f99b3 | note | Inspection Type (Visual, other) - On site test
d3d48e5d-fe80-5c5f-be3d-824b6cdc46dc | note | Inspection: Key - H
b60551c7-02f7-586b-abf6-dfe1816a41a9 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
7546c15a-f4ff-5af4-8f1f-afcf14c89e50 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4400
e309f1ee-1a7f-522a-ac15-969c9eb59fab | note | Acceptance Criteria - Pipe not damaged during installation
ea2ac12a-61b7-5f37-9489-a21fbc595de4 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
ebe9206b-d043-5b4a-8df4-49154adb37af | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
99367f9d-d541-5ab6-88fd-37a151eccbd3 | note | Frequency - During installation
b0df8a58-fd24-5bb0-9b6e-bece5a78b21d | note | Inspection Type (Visual, other) - Visual, Survey
bedc309c-7732-5ca9-a2a3-47ec6d4cc1c7 | note | Inspection: Key - C
3e8b8b45-99e4-5e6b-b69d-79ea3817acd0 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
67901df4-d56d-559b-8e7d-5f878c9edf18 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4410
601c17c1-0ea4-5ba4-bdc3-5c9ef8eeed0a | note | Acceptance Criteria - – Lateral connection as per drawing C4410 and DCC standard details and project specs.
2f8e3755-0e10-5fcd-8571-7d3597df42f7 | note | Verifying Document - Photos, measurement checks
de5270c0-4716-531c-b396-11aa12e44d2b | note | Frequency - Every Lateral
a52d0961-fe8d-5e1e-857b-85a3e1c486b1 | note | Inspection Type (Visual, other) - Visual, Survey
146b6d1f-44d2-55dd-a090-a58ebeb296cc | note | Inspection: Key - C
dfebeeba-79c1-5450-a9b6-ffbb20506263 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
724d5bfd-1af8-528a-8193-eb723af36fce | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
c68d70dc-4f9a-50ae-8be3-0fd8f612412b | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
6e449d16-8127-56bf-982a-819e07e9a932 | note | Acceptance Criteria - min 100mm bedding
98aa8e3a-749a-5870-a2ae-e489ff2909ef | note | ○ 100mm overlay
6e130b15-4df7-5ba1-b641-708b1ae47c1f | note | Verifying Document - Photos
66bd14d5-c8f5-5750-adeb-11f4126cb161 | note | Frequency - During Installation
57840eb0-10b6-560c-bcca-12d653135aac | note | Inspection Type (Visual, other) - Visual, measurement check
08a782e4-0077-505b-88f1-523e2e1bdc16 | note | Inspection: Key - C
3fbeea8b-3b24-5991-9bc9-cba304e59a8a | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
28d3f21f-b7cc-5217-a1cb-2a31c14da285 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
7a49152c-59b9-5cab-ad98-fbfd41ac2bb6 | note | ○ Compaction testing one test every two layers as required
d0f0475f-2592-5b41-886a-c48a7f9e7baa | note | ○ Conductive signal strip to be laid at 300mm above pipe
74c7e632-39a2-5b72-a5e2-6c326321be48 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1628e93a-9dac-5928-b69b-c977a3c85ff3 | note | Verifying Document - Photos, Compaction test results
fd86da26-7bf4-5c3a-9451-55f7e2c484aa | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
a44531c6-7130-5caf-88fc-bff9861f75b4 | note | Inspection Type (Visual, other) - Visual, On Site test
4df90d97-80c7-55a3-95ab-3e8c43888f69 | note | Inspection: Key - H
1fbf6dae-4225-59fa-bbb1-95d4acd32440 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
4e7fdd51-c846-5cb3-8c93-46d78f7d8d3d | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
a41d7e65-bba7-5aea-bb5e-6cd6a13fac9c | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
fbcf4ffb-c0f4-5037-ab3b-001955233374 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
a31bc53d-5856-550f-af01-8072c2852630 | note | ○ Dips or ponding of water inside the pipe
3dd50374-105f-5b4a-9181-2915ac4e0d5b | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
e6a9df16-54f0-5cba-90ba-1eb928c3c4e1 | note | Verifying Document - Test Records, CCTV footage
b9c169a8-9e00-52eb-82e1-98cec35ae8cd | note | Frequency - Every section of pipe completed
0b784ad0-5cfc-5e50-b86c-ae20ae220195 | note | Inspection Type (Visual, other) - On-Site Test
321f3b08-95df-5e61-93f9-59fac32fc4fe | note | Inspection: Key - H
3a0a155a-0e6f-525d-add4-60208cd74388 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
a2cfe721-c303-515a-b61a-2730155bdf88 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
c8975b3a-64f0-50b0-93d9-3cbe0119d76c | note | Acceptance Criteria - Engineer Approval
74d1867c-b65b-5697-81d5-d00fa45c02fa | note | Verifying Document - Test Records
c0b0eeee-8795-5553-b3d0-e7aeb6aca8df | note | Frequency - Every section of pipe installed
397f7f31-99a1-5724-b9d2-12cd0ce72898 | note | Inspection Type (Visual, other) - On-Site Test
5ee889a0-053e-551d-b062-ac7e6f3addb8 | note | Inspection: Key - H
c2914af3-e5e7-5f51-9cf1-83f0c7e6da8a | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
c72817ba-6585-5485-8a04-c4aba61e66c8 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
2edebed3-9482-5f47-b389-c54c79f596e2 | note | Acceptance Criteria - Signed ITP
03e79f7d-a9d0-54e9-a25c-90c51e416c53 | note | Verifying Document - Red pen markup drawings
b02ea6fa-f6e1-5031-ade1-9256555b5511 | note | Frequency - After completion of pipe section
89773843-6247-5ff0-9b05-7b7b9bb86993 | note | Inspection Type (Visual, other) - Document
c2106e0a-964c-5e1f-b19e-d1b42d22aadc | note | Inspection: Key - H
5d05a49b-2bd1-5213-9902-a888b9671978 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | itp | ITP-1003 - Installation of pipe from WCMH-3A to WCMH-2B | 1 | dc0721e9-ffd3-4993-b963-e7e9a4b2c75f
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
13b74c26-053a-5c39-a586-797f1635c254 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
9284b471-55b6-55de-ac70-2c82ec79bbb0 | note | Acceptance Criteria - Pipes shall be DN475 SN16 PVC-U rubber ring jointed
84acdc02-e0bb-5491-8dc8-fbe19d9a4207 | note | ○ Items are approved as per contract specification
ceff9359-d81d-546c-97b9-9146c1fbe68f | note | ○ DCC approved
ee4a1268-a257-5491-90d7-27b0c6097961 | note | Verifying Document - Photos, delivery docket,
3ddce36d-5a72-5e71-a9d2-d12d0b5ab0c4 | note | Frequency - On Delivery
646390fd-b681-50f9-bb3c-04063fc27c27 | note | Inspection Type (Visual, other) - Visual
12a1fa5d-0f59-5ef7-a175-eb085b31eae2 | note | Inspection: Key - C
96f84a6f-af0d-509d-89a1-c3a6bb8023c9 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
9bbac671-99d6-5b75-8cc5-57bb6a6203e1 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
90828ae5-9932-5e27-b691-ebd484f2fa30 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
886e4424-41a8-58b2-b90e-f409a49c6617 | note | Verifying Document - Survey marks, photos
421dc5d8-9a75-5422-89a7-1b6f7fba1c1f | note | Frequency - Prior to commencement of works
382706af-0939-5c33-be0b-5a0c6f5d0928 | note | Inspection Type (Visual, other) - Survey
50fb44c8-9d6b-5e3a-a00f-76cb8e505fb8 | note | Inspection: Key - H
a0aa9287-65a0-52b3-84f7-2c56fba7812c | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
f61898e8-e94c-5e3f-b0a8-e0d7120ebc28 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
d2c50cdc-945f-5b34-9dd4-4704219f3052 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
e5a6b4fe-e74d-5588-b5c5-043a1286eb7c | note | Verifying Document - Delivery dockets, photos
e7916375-f798-5fe7-a75d-e6fb4e348f10 | note | Frequency - On Delivery
0b88f83b-5f49-58e9-940a-8ccc0d676686 | note | Inspection Type (Visual, other) - Visual
11a53bf7-7b09-5755-8f10-63c189645560 | note | Inspection: Key - C
1355b01f-5a09-57e6-aa3d-d3d4491f2c27 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
955cd150-f299-5fc2-a187-dd4fc38002ae | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4200
0574bc8d-5024-520d-92fb-c48cf809237a | note | ○ Floor of trench to be even across width and length
37cd7643-d2c7-57fc-aaf6-563cc9c8c266 | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
77a36b85-b9cf-5f94-a60c-4ad6588d756b | note | Verifying Document - Photos, measurement checks
5bfbd410-8a7c-567f-bc85-1b7af0fd51ff | note | Frequency - During Installation
fea66bfa-3997-5fc5-ba7a-df3b67dfc732 | note | Inspection Type (Visual, other) - Visual
6b65a327-1b89-5f76-8f5e-875105628501 | note | Inspection: Key - V
74835963-98f2-5442-b26d-f0809b23c391 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
af8ff430-9933-5231-b7d7-1d95304c0e84 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
a1f8f8f1-7818-5fe0-a5f5-098096b284ce | note | Acceptance Criteria - minimum of 2 blows per 100mm
1492de43-6e99-5185-91f4-32afd4d5532f | note | Verifying Document - Test results
b3082378-39b5-52ca-aea9-15679cc8fcb6 | note | Frequency - During installation, per 20m
90719ac5-625e-5a85-aa4e-98bf5cb52d48 | note | Inspection Type (Visual, other) - On site test
fc78897b-d0b9-5093-8725-5ddd0b035c0a | note | Inspection: Key - H
0756547f-733e-566c-b801-33b9ab940887 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
b7c3f0b6-80d4-5804-8039-b1d423f77516 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
71ff12d6-4cf3-5b6f-b0ab-f56350c5c25c | note | Acceptance Criteria - Pipe not damaged during installation
a813294d-4cc9-5de9-8013-acc9af340607 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
b5fa012f-be3c-5636-91d1-fdd80d368537 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
ebb1d923-d0aa-50bd-9dac-f46238764107 | note | Frequency - During installation
db7fd423-ed15-5616-a986-70a71c212cf8 | note | Inspection Type (Visual, other) - Visual, Survey
7159e17e-8d44-5d0d-845c-0e53cca1c85b | note | Inspection: Key - C
ff88a9b0-e928-5d5a-82fa-59dde51d4a4f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
04ab3a9a-384e-5529-84a7-7dea85c86652 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
d54a932b-c8ea-598b-bd5c-157b1440ff54 | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
23d3b260-127a-529b-a3b8-fbf7c3eb16fc | note | Verifying Document - Photos, measurement checks
c702bd62-1125-5801-9085-16a258c893a8 | note | Frequency - Every Lateral
5e5085e9-4c90-521f-bdfc-4a0672c90e85 | note | Inspection Type (Visual, other) - Visual, Survey
bd8ebce9-5fcb-5785-964b-09b0805bdbab | note | Inspection: Key - C
e346e155-5b90-547e-9783-a847beb34fe0 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
09b4b50e-a86b-5a4e-adb4-fa6d337ecd5b | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
8bf890d5-d8bf-5f27-b7d4-2a2ac42d69af | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
40d1536e-0e1b-59be-ba67-0dcb2d6a2776 | note | Acceptance Criteria - min 100mm bedding
72de3943-f47e-55a5-a375-ac3f113827b0 | note | ○ 100mm overlay
105fef89-3a30-57fb-a939-0f69e881b085 | note | Verifying Document - Photos
19855ea0-4dcb-5c2d-ab2b-90c9cf3a3314 | note | Frequency - During Installation
c43bf7e3-70b8-54c6-9cc7-1bed12e01a20 | note | Inspection Type (Visual, other) - Visual, measurement check
3f8dcd5f-c11d-542a-9a87-ef0a50dc3e1d | note | Inspection: Key - C
289a7157-1d60-5d7f-b9f0-9ea020f16ae2 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
6fe0cd67-fbdf-5cad-a738-64b3873ece9e | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
c47c83fa-e5ad-5ece-8c58-c236b63a0ff4 | note | ○ Compaction testing one test every two layers as required
91d46ade-8b54-527f-91ff-111dfddd2ac7 | note | ○ Conductive signal strip to be laid at 300mm above pipe
d4d31b4e-1f6e-54c0-8a8b-42c7fc9f3fc7 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
c18fa8bd-c2a7-5e2f-bb00-a48e929b4b3a | note | Verifying Document - Photos, Compaction test results
7afd1cd2-2693-5ab1-8855-1ab06da78ce8 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
27ef7f76-e5ce-5bf9-8261-6ae426368e14 | note | Inspection Type (Visual, other) - Visual, On Site test
4ea1a684-fc2a-5a63-bd5d-b4697a6256b9 | note | Inspection: Key - H
276e077a-bcc9-5ce5-9d51-5660f4c414ae | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
38d79f98-d667-5c79-92ea-4c5227d2c959 | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
b4a1cd80-8933-5082-b7d5-8348a6d1f28c | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
80ac3360-b4da-58d9-8dfc-9094a250c594 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
47ebf879-e8fb-59dd-87e9-82ef53764765 | note | ○ Dips or ponding of water inside the pipe
ad3cad01-3e37-5482-a4ab-47cd8249ca8c | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
56c76dd2-15fb-5820-a544-bf48cc0d5429 | note | Verifying Document - Test Records, CCTV footage
5e8ee003-21ae-58d0-abf7-5e5c049882fe | note | Frequency - Every section of pipe completed
33f19922-04cc-5ee4-a181-a7e91e525fae | note | Inspection Type (Visual, other) - On-Site Test
794a6e13-870a-57f3-a4c5-3d2253f62fe1 | note | Inspection: Key - H
56b3f79c-9ecf-540d-a262-0b6b2b4e1815 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
3319707f-5d8c-562a-8ef3-587361fc043c | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
1c72d0fb-0ba1-548d-8def-cd810a9de009 | note | Acceptance Criteria - Engineer Approval
968c6e86-985e-552c-8bfa-c114d8a95b7a | note | Verifying Document - Test Records
62347b10-5809-5ae0-9d15-01a823ba023c | note | Frequency - Every section of pipe installed
b99d6c44-c36e-554a-8ccf-b76711765467 | note | Inspection Type (Visual, other) - On-Site Test
06f90db4-87bb-5f12-9ef7-24beb195e20a | note | Inspection: Key - H
64588d90-d5f9-577b-9b20-016697b2b094 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
69a8a319-ae3b-572d-a463-f1ca5eca6e7e | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
639fa143-b341-59d6-94b0-687287780f51 | note | Acceptance Criteria - Signed ITP
cff52efc-8af4-5481-8212-26bfd0d3f929 | note | Verifying Document - Red pen markup drawings
6cb9ccd1-f63f-5ec4-bcc3-3aca386ad59c | note | Frequency - After completion of pipe section
4bee6db4-55b7-56d2-b030-c996c4bcd76e | note | Inspection Type (Visual, other) - Document
aa477c00-6014-5d85-905e-108d1d1849a8 | note | Inspection: Key - H
088e458d-d157-5a69-b0f9-e55824f63e68 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1004 - Installation of Manhole - WCMH-2B | itp | ITP-1004 - Installation of Manhole - WCMH-2B | 1 | fc1c765b-747c-4c1f-8012-6573a033d81f
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
8fa440c1-35c5-5acd-a51d-7b63cb6819ad | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
b0775011-5c47-5478-a743-050b5e4e124f | note | Acceptance Criteria - Items are approved as per contract specification
1916c62f-0d2c-5946-a3c3-4f4e0ecce308 | note | ○ DCC approved
e22c4cf7-ba3b-530d-8827-d51d3fc91e53 | note | Verifying Document - Photos, delivery docket
7f7d3831-7829-581b-84bd-bb78b0212d8c | note | Frequency - On Delivery
edf2c7d9-ab72-5b5b-9799-c53ef40817b4 | note | Inspection Type (Visual, other) - Visual
d27a6a00-b74f-51bf-a1c9-ad9e267ac8ba | note | Inspection: Key - C
9316ddb4-9b6e-5563-9ef8-d03b6230b399 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
f81aa168-e5a8-5538-a502-81dc091b0694 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
b0a97d3e-4763-5a4b-94a9-64472d2198bb | note | Acceptance Criteria - Allignment set out matches drawing C4200-2 or aggreed with the Engineer
640f6956-0a9b-58cc-b4d8-9c1a0b867556 | note | Verifying Document - Survey marks, photos
dd42f976-425b-5c35-b376-c8b63ce81413 | note | Frequency - Prior to commencement of works
acb47ab2-3426-5196-a9c1-47ed2769912e | note | Inspection Type (Visual, other) - Survey
06ca9a3d-c73f-54f2-96f6-b088047b106f | note | Inspection: Key - H
f4651f5a-5a50-564f-be63-4ed2f6f66d38 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
0a7d577b-71ef-53c0-ab91-cc85d898547d | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
c93739d4-5f81-5b46-a260-ecf26f4749b7 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
0bbcab58-544d-50fb-a6c9-f534c56b42a3 | note | Verifying Document - Delivery dockets, photos
f1737fed-8057-5afa-ac20-e3a058349865 | note | Frequency - On Delivery
4d83e778-7f4f-5ea2-a72b-1fa535b38664 | note | Inspection Type (Visual, other) - Visual
f57f05df-bf6d-5793-a67e-d73780c58490 | note | Inspection: Key - C
ec227945-d25b-5ee2-93b8-9a3af819e859 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
0d3ee789-6114-5abe-96aa-1888cdb5ec60 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
7df35265-64d1-52bd-bf58-0c9c79c1ed70 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4057deb7-13bb-5ee4-90b6-5c658f603d88 | note | ○ Floor of Trench to be even across width and length
c95c216c-dfdf-55a2-baba-7748a0a7068f | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
abf5e034-9e42-5edb-8f4d-e40c9f91913f | note | Verifying Document - Photos, measurement checks
4cc64e1d-a805-5f2c-8520-c3129fee6143 | note | Frequency - During Installation
361e2426-2cca-5b2a-b138-7cfbdfc5ee6d | note | Inspection Type (Visual, other) - Visual
82c31f58-1382-5655-b00b-9e244d20d00f | note | Inspection: Key - V
8ce679d4-7b2e-56cc-bbe5-6aba815c4380 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
db1349e0-c37c-562a-984b-8dd83a107885 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
ebb09bc1-86a4-5db0-9b72-80fa8d68a632 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
49e613a2-9fe9-5bfd-bf85-7de44bde68a6 | note | Verifying Document - Test results
4cc02fab-c9d2-51a2-a782-ad30e38613c1 | note | Frequency - During installation, per 20m
43eed011-7105-52b0-bf4e-8d04815e680c | note | Inspection Type (Visual, other) - Visual, On site test
c08e0479-5b0e-59f6-9983-09693d4ffc63 | note | Inspection: Key - H
be471dab-2f27-5298-89cb-ff668bd7f56f | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
10dcd092-9a4e-52f1-bcca-7afc901a024b | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
b67b94dc-fc4f-5956-ba16-122048ad9dbb | note | Acceptance Criteria - Bedding to comply with requirements
bf01b1e9-1d9e-5f5f-8a13-71af8770afde | note | Verifying Document - Photo
31afb6b1-51c8-55dd-a565-5447ebf59d88 | note | Frequency - During installation
6f291ce0-4ff6-5068-8754-4c877f260982 | note | Inspection Type (Visual, other) - Visual, Measurement Check
c3d2eb8e-0b93-534c-9877-1e74125bb723 | note | Inspection: Key - C
bf6a94f4-628b-5d30-a36c-39a8f6342935 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
9b0db491-a9cb-564c-8c2d-2bad3e0c19d3 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
5bd7b6ef-bd55-53ec-b535-acade7c8379f | note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
00337b51-e286-5684-a097-2c725edf0514 | note | Verifying Document - Photos, As-built
1eadbb7f-3c41-5b2a-ac18-c20fb712da9d | note | Frequency - During installation
ade83643-63f3-5c98-b684-cb78a024ca39 | note | Inspection Type (Visual, other) - Survey
e3812b53-945b-5e99-92b3-d17ac162bb87 | note | Inspection: Key - H
96885560-ae96-5855-b777-211d31919e2c | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
1c6445ad-3259-545e-a1c5-1c527ea49e75 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
a418cdcc-d4c9-5bca-8796-8560a5aef0c5 | note | ○ Benching shape to have smooth transitions at bends and junctions
1b2e754b-1695-52e9-98e8-b0b7d9f85a51 | note | Acceptance Criteria - Benching built up to the specifications
46f57886-66cc-5359-9f92-ac62bb8d0a75 | note | Verifying Document - Photos
81571416-ec56-5f97-a5ba-fef7a53ed24a | note | Frequency - During benching contruction
c0ce49fb-7d55-5d85-ad19-55d04d72dffe | note | Inspection Type (Visual, other) - Visual, Test Results
2899b8cb-27b9-595a-a5ee-a452d8c3f2c3 | note | Inspection: Key - H
247e67d6-4254-580b-b23f-7fb864f0559d | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
50cbb4d8-92ca-54cb-922d-2eefa1d3c222 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
208d99fe-2c94-5475-bca4-f36e9144381f | note | ○ Compaction testing one test every two layers as required
ff634880-7be7-52a4-93b1-c4ddb5e0996f | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
db3078c3-787d-5ec5-bb09-64bb4f014f96 | note | Verifying Document - Photos, Compaction test results
83c16760-a499-53e7-97a7-d468e6ce33b6 | note | Frequency - During Installation
f1f5d583-8224-50b5-88c7-d2972cdfade0 | note | Inspection Type (Visual, other) - Visual, On Site test
7af48950-7658-5d3a-8156-fdbbdda1d11f | note | Inspection: Key - H
70fcba41-5093-5bc7-9eae-4661563cfa7a | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
ba52f972-ce5c-58bd-a3ad-7493fe092f6a | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
ab949f49-d09c-5c0b-813b-b1fbe163c4d3 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
4a5d664a-39c3-5eea-b1ea-f359b1166659 | note | Verifying Document - Photos, test records
481f87fe-004f-5b5f-b1c6-c3bdc2d3636a | note | Frequency - For every manhole
ab33242a-d9cc-5ca6-9095-2739d5fe87ee | note | Inspection Type (Visual, other) - Test, visual
ddf8de6d-7895-5fed-9920-6da42b03d295 | note | Inspection: Key - H
e122a6e1-b2a1-5138-b5e0-2abdd50995bb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
11e93153-0a59-56e2-8bf2-b48e861a1cce | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
8f489c22-9c6e-5a4a-96df-e96cb8ad05b4 | note | Acceptance Criteria - Signed ITP
4f80bbb7-24c7-5cab-a479-a612224c6f59 | note | Verifying Document - Red pen markup drawings
9e7dcbc8-9a00-589f-a41e-ce5a854e2d34 | note | Frequency - After installation of FSMH
dbef015b-f651-5642-8e52-97cc808e1371 | note | Inspection Type (Visual, other) - Document
9ab3b63a-07ed-51f1-93f5-1476d8da1168 | note | Inspection: Key - H
e1186783-7db3-58a0-b527-b39f5242c16b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | itp | ITP-1005 - Installation of pipe from WCMH-2B to WCMH-2A | 1 | 2721abef-a680-4a18-b9d4-643ff54d3bef
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
505aa3bc-ce48-585b-9675-ac77b0c86c18 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
878ba974-a1df-5555-83a3-08b59c313566 | note | Acceptance Criteria - Pipes shall be DN475 SN16 PVC-U rubber ring jointed
7ae8d70b-ec0d-5250-a8e9-29a12dfc425d | note | ○ Items are approved as per contract specification
30efd9fc-8910-5b59-a9e1-0eb09eebfcea | note | ○ DCC approved
7d03c096-7fb3-5172-afda-f587f93e8ff4 | note | Verifying Document - Photos, delivery docket,
12ca5ad7-41f9-52c3-b2d5-87ad75e6cad1 | note | Frequency - On Delivery
6e3b0029-edf4-503b-9c1c-e98d150aed14 | note | Inspection Type (Visual, other) - Visual
8df5884e-0043-5933-8740-218dfba3882f | note | Inspection: Key - C
6c4825d6-02eb-5a54-9114-13a9a60f0235 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
96fb792c-a0ed-564f-9031-39f163035cf7 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
57ed2993-2280-52c1-a68b-057e5086e963 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
de085eaf-71b0-5885-8525-eb7db1eb9de5 | note | Verifying Document - Survey marks, photos
effa6e55-dc1e-584c-9d18-32a972c4943e | note | Frequency - Prior to commencement of works
1ad182a9-26b7-58d0-9dd4-b4af46802d16 | note | Inspection Type (Visual, other) - Survey
d7b519fc-0422-535f-8c5e-9f115fa3f649 | note | Inspection: Key - H
c80b0be5-6e16-50ce-a6ad-ec319a06f93d | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
a5bd7563-0282-55e1-9359-bb279477c0d5 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
3028e414-bb7e-5d53-a0cf-60cf9afbdcdc | note | Acceptance Criteria - As per DCC code of subdiviison 10324
4f360565-505f-5111-9d5d-7da384d668cf | note | Verifying Document - Delivery dockets, photos
e919186b-f2a7-5235-ae94-a86c4346ad40 | note | Frequency - On Delivery
7f37cc99-17f5-5edb-bcd3-3c899943acbb | note | Inspection Type (Visual, other) - Visual
48a8bd03-2fbb-5029-a693-9bedd6f128b5 | note | Inspection: Key - C
9af3dd14-7021-5236-a495-bf5b6e9c2753 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
5f37e095-688f-545e-b03d-707c1b1739fd | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4200
c1eb6dbc-7fdc-59d1-9057-1f3b979b2143 | note | ○ Floor of trench to be even across width and length
792ae8c8-544a-54f4-a842-98b42c3ef7d3 | note | Acceptance Criteria - Allow 100mm for bedding
636ab15f-bd8c-5bbf-ac14-dd36de882474 | note | Verifying Document - Photos, measurement checks
8158c1e7-488b-5ffb-9255-83342b47bde1 | note | Frequency - During Installation
74c751f6-7448-554e-92a5-a8f7527309f6 | note | Inspection Type (Visual, other) - Visual
363c25b0-c787-55a3-a126-048128fb65a0 | note | Inspection: Key - C
815f83b4-feb3-57f9-93b8-e1218746474c | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
e0fde3f7-50fc-5454-830b-20f364e6469f | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
e4a94f48-19e5-5767-95b5-418a9af42ca4 | note | Acceptance Criteria - minimum of 2 blows per 100mm
a0d0ef8d-2979-5b85-a674-7f7952e97c7f | note | Verifying Document - Test results
26f3737b-9afc-58f8-8524-48b54e80ba3a | note | Frequency - During installation, per 20m
43891cfc-f9d6-5c87-afda-04fb7eb28533 | note | Inspection Type (Visual, other) - On site test
a9f632be-f684-589c-b3ce-4e5776954bf3 | note | Inspection: Key - H
56ad10bf-5806-5d48-883a-51fc638c6f9e | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
e260b6d3-1b42-5090-98b3-8a2fa3be4ec4 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
a016e2d1-9c31-5300-9594-996f22267b14 | note | Acceptance Criteria - Pipe not damaged during installation
ebcb428c-6fdd-5aa1-af16-febf1891fc7a | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
e429735d-ae66-5cec-a19f-ac2816de4148 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
ad760cb3-e85a-543c-bf39-4d9d64f3c494 | note | Frequency - During installation
b6546dd8-7acd-5944-89cf-d790be9a4f36 | note | Inspection Type (Visual, other) - Visual, Survey
c8007ceb-3df6-57a1-8df1-3eb65038684f | note | Inspection: Key - C
fd593a62-c22d-58af-bc8a-7ef2f1f0c879 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
7b947aaa-f092-59d6-9505-133003a8f5fa | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
09f24c2f-0564-5393-9b40-37e92863d51d | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
091424d3-a635-568b-9a8e-63aeabfd5849 | note | Verifying Document - Photos, measurement checks
2775a87b-5f02-56bf-bcf5-59ec5c64b3ea | note | Frequency - Every Lateral
9517d75f-2b6c-5b20-a9be-6f0c0a19d91f | note | Inspection Type (Visual, other) - Visual, Survey
db7fabf3-036b-52c1-9bc5-1ff2a1b3601b | note | Inspection: Key - C
791134d9-6384-541d-8d70-b5ee5bcdb957 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
22eb5ba3-1a0c-5810-9d45-e1015ce91df2 | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
386dafe8-bc21-553e-ba1d-f668302213cd | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
feaa418b-e62c-5559-ad82-f6447f23943e | note | Acceptance Criteria - min 100mm bedding
b26635bc-29ef-5cec-852c-5a71f45e0a5e | note | ○ 100mm overlay
30ab40b3-3963-59c2-a393-056a3405ee83 | note | Verifying Document - Photos
35c82a22-f7da-58cc-bd1f-56fb4816e52a | note | Frequency - During Installation
9be94209-fc25-54a1-ba21-27fbf2dad4db | note | Inspection Type (Visual, other) - Visual, measurement check
00c56886-bd87-5acc-b6ec-f3d0f2c05423 | note | Inspection: Key - C
ad7c3c87-15a6-5c6b-9443-98e5ae3b3e33 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
95a10363-9cf2-5a2d-8a71-e2c06639f4b6 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
7af12d1f-9dcd-54a6-a9ca-d0318ae485a2 | note | ○ Compaction testing one test every two layers as required
e904b3d6-3a7e-5c7e-be74-9bda6bfa8956 | note | ○ Conductive signal strip to be laid at 300mm above pipe
968af23a-f796-5736-be80-7950079c4be5 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
a98128f2-17cc-528d-b098-fa7369452567 | note | Verifying Document - Photos, Compaction test results
e84b06ce-392a-5b5a-ad49-28b646adaabf | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
13191704-d16a-504c-8883-9dc1ab874187 | note | Inspection Type (Visual, other) - Visual, On Site test
102c0a06-36c6-5d25-83b2-0936a14b0cf3 | note | Inspection: Key - H
ea82983f-7c01-5317-8e13-84796fd40be1 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
9c79a75b-d654-5ddf-af02-f939d455d89b | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
e084a2fc-fe1e-5f77-a544-a3048a314f0b | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
203f7a49-e446-50a7-bfc0-d0871589a778 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
5043ae62-60e8-5287-9b4a-bb4203f57df4 | note | ○ Dips or ponding of water inside the pipe
995a99a7-895e-5e19-bdb3-0433d0176e09 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
04a48434-6104-5ce7-b1f3-8abee42bd456 | note | Verifying Document - Test Records, CCTV footage
29483643-34e4-5d25-8f12-2471bd12cc75 | note | Frequency - Every section of pipe completed
c9c96860-c4fc-5931-a62f-580491234ed8 | note | Inspection Type (Visual, other) - On-Site Test
2ab0cc9e-4297-56bd-a6b8-8e8091f708bc | note | Inspection: Key - H
b87066bd-3786-5891-a23b-33f5775b32f0 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
c1267698-fc7c-5513-906e-fb5afafe68d2 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
e705f135-8ed9-57e1-b41b-a8daff76e8b1 | note | Acceptance Criteria - Engineer Approval
e3c9638a-ee85-5393-8355-5bb8499f4389 | note | Verifying Document - Test Records
fdaa6aa1-d6f2-5446-9cb8-ed3fa573292f | note | Frequency - Every section of pipe installed
00d10bdb-00c0-5163-a0b7-4d68a4967276 | note | Inspection Type (Visual, other) - On-Site Test
4e8ba3a1-e4cb-5a9c-9e07-71a46bcc0d2f | note | Inspection: Key - H
78fb41f0-47cd-5fc8-8d1c-5d3e2c166f41 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
7588d958-f2c7-5edc-9bd4-7e39bf28063d | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
ca0f782b-b6dc-5405-8cb6-65ace6b254af | note | Acceptance Criteria - Signed ITP
dcb9e0f3-84d3-578e-a617-f7d4b1e56bf9 | note | Verifying Document - Red pen markup drawings
a6422215-5d3c-512c-8999-22a446c0729c | note | Frequency - After completion of pipe section
e3173fa3-a24f-5908-9e43-5bf969e11427 | note | Inspection Type (Visual, other) - Document
f09bb50f-bf44-5078-ae99-9001f1a44758 | note | Inspection: Key - H
f9e20aad-09e7-5bd0-a722-23207a6e1ae6 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1006 - Installation of Manhole - WCMH-2A | itp | ITP-1006 - Installation of Manhole - WCMH-2A | 1 | 353fd70e-96d9-4805-b69e-43a9f6b81e92
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
2129be25-4552-50bf-bf84-67903ce8518f | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
c69bf63f-e8ae-5377-900c-e0cab33759d3 | note | Acceptance Criteria - Items are approved as per contract specification
616155bd-b974-584d-8f39-6ff02ec2af4a | note | ○ DCC approved
ee46d58e-4bee-5255-a55c-e6bf3a3846c0 | note | Verifying Document - Photos, delivery docket
ca16054e-2d0a-589d-adc2-2c7ccd97a27b | note | Frequency - On Delivery
f037fd79-3d3c-5205-baae-055bb6bd93c4 | note | Inspection Type (Visual, other) - Visual
d6b29b04-e9f7-558b-8ffb-392dd7acd207 | note | Inspection: Key - C
2630dc7e-7500-5338-bbdb-6519ad3e2d49 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
47fd9c63-6dbf-5f05-86ac-53d84be70473 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
60bbb8b6-f4b9-5529-8702-b1a0ac50d2c0 | note | Acceptance Criteria - Allignment set out matches drawing C4200-2 or aggreed with the Engineer
89398a54-d73d-5fd8-aa56-518b9012f526 | note | Verifying Document - Survey marks, photos
c90998c3-eed4-58eb-aab1-d8cfd05e854a | note | Frequency - Prior to commencement of works
bcde56a5-0f06-55ba-a453-9421dc3b2eba | note | Inspection Type (Visual, other) - Survey
53be4673-323c-55ed-a331-abad99c4ce23 | note | Inspection: Key - H
b32dada6-5d30-5647-b0d0-72df20139663 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
1c120b7b-82e8-58ac-8c42-d2966432c1f3 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
1e5e4fae-1a33-5481-a1dd-ee4cb906808b | note | Acceptance Criteria - As per DCC code of subdiviison 10329
fa4741c4-f48d-556e-93ee-cdc486a6ccea | note | Verifying Document - Delivery dockets, photos
afad5a3b-5975-5bf8-84a5-1632c1b4b30e | note | Frequency - On Delivery
ad435216-b5e1-5bb0-984f-a27f2f72dbb3 | note | Inspection Type (Visual, other) - Visual
4e227693-62da-5ab2-bd22-be08bab21229 | note | Inspection: Key - C
525d03ee-8a09-5eae-8c52-7e0c09cfc422 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
4f113d00-5196-559a-9ef9-5cc5dae96d33 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
fdb825c1-2343-5415-a8e0-4cb20f62e1fb | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
9a1dca0f-5d16-5e81-b25e-34bf470ee7f6 | note | ○ Floor of Trench to be even across width and length
3d32c05c-4376-58b7-bd23-0ec0f275812f | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
f2fde9ba-e16f-53a7-8079-c6063b74b2bc | note | Verifying Document - Photos, measurement checks
bd32687e-0444-5f6c-9205-6dff35a52800 | note | Frequency - During Installation
fd4ba671-13cf-5023-be13-c8e6bfc1d5e0 | note | Inspection Type (Visual, other) - Visual
65a4eeae-5d90-5ae1-ba0f-7e76fba2fd4d | note | Inspection: Key - V
fd427284-92c4-5b4f-b414-f0a9fd929a96 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
3640a966-b0cf-5803-a410-6d9379711ad4 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
3ab7c92a-3c86-523d-a20e-9b2369430c00 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
cd7412c4-369c-5714-9e1b-af03c2e39f3c | note | Verifying Document - Test results
8e06f3b4-26b0-56f7-aa0c-6076e7c95082 | note | Frequency - During installation, per 20m
1f75e2bb-e452-5772-9582-206ddd4dd3cd | note | Inspection Type (Visual, other) - Visual, On site test
d2d497ed-d5d8-57e2-93cf-680d77300851 | note | Inspection: Key - H
e5090e8c-30ad-5211-a742-1c906bd8fcaa | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
92cb3224-3812-5f50-9e16-39933d5c59f5 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
79c6b6d4-3d60-5c6f-b346-a4290f646112 | note | Acceptance Criteria - Bedding to comply with requirements
6f1cd2d6-82a2-5cf6-be7f-aa7d8bc3497d | note | Verifying Document - Photo
d12dbf11-927a-5bdd-9c2d-74e1d2325e80 | note | Frequency - During installation
25879f01-96b8-5238-a290-358c44a88044 | note | Inspection Type (Visual, other) - Visual, Measurement Check
6bafc9aa-b9ea-5003-8e85-7803896fa8ef | note | Inspection: Key - C
2b1788bd-4cbb-5d89-8276-84879530448b | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
894a0a03-2ee3-5401-a453-de584f9d0c37 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
ecd4aea4-b1fa-5944-ae9c-42c9e6f85917 | note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
51b3c559-a273-5376-bc3a-b8919df9796b | note | Verifying Document - Photos, As-built
45844737-9223-5e25-bdb1-3062ebb67b84 | note | Frequency - During installation
19013682-480b-5280-b917-8eb98b65e16f | note | Inspection Type (Visual, other) - Survey
cc97f992-d495-5f16-aa15-6ef8897de957 | note | Inspection: Key - H
53e4c8c9-6efd-5972-a4fa-74395ebc5ac4 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
2e7a56d3-6f2e-56aa-a563-38e2d5e57785 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
13efd17e-a901-5a46-a036-546af4e33734 | note | ○ Benching shape to have smooth transitions at bends and junctions
c63ab44d-2829-52c0-8adc-ef671f75dc8d | note | Acceptance Criteria - Benching built up to the specifications
e2baa901-d655-5495-b741-bc9dab50cc5d | note | Verifying Document - Photos
4f582598-267d-5ea6-b77c-f68771805ffd | note | Frequency - During benching contruction
65c7fa76-6c6a-521d-b657-0093f48b0e47 | note | Inspection Type (Visual, other) - Visual, Test Results
677a5413-5663-5f4c-910d-2218ea14546f | note | Inspection: Key - H
78793769-c239-5d72-9ce9-ec94d82814a8 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
cb53435c-3bd7-58d5-b086-1731c0ebc628 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
eafc30db-0b3e-56db-b0cd-923f99b26976 | note | ○ Compaction testing one test every two layers as required
d57c009b-a9b3-5806-b381-c0e3682a57bc | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1024d49f-3cef-5a43-ab42-8a61dc98c7ff | note | Verifying Document - Photos, Compaction test results
47791464-f279-56c3-88ab-08e03dbc6303 | note | Frequency - During Installation
5bb5eb5f-9adc-53f6-82da-0f93625ccd1e | note | Inspection Type (Visual, other) - Visual, On Site test
9cacae21-08a7-5ed1-bed3-2d838fec2af9 | note | Inspection: Key - H
b853e219-829d-5237-a6dd-e57a9a4a4df5 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
77ded28f-8a89-513f-a1ee-73dd14fb01c4 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
78c1bcea-f008-5967-b3da-41b9233cf8d8 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
cad6fe85-7a03-55b5-a9ea-52efe86e21d4 | note | Verifying Document - Photos, test records
90551d42-8ce1-54bb-a583-7e5f0af076fc | note | Frequency - For every manhole
15621810-4f8e-5b6c-8b36-3c47c78ddbc1 | note | Inspection Type (Visual, other) - Test, visual
d50d28d4-3ecd-5c39-953d-f6d25fe0b328 | note | Inspection: Key - H
a9f99947-4464-56c9-936c-cc3115e52936 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
e8a97ddd-77a4-5c4c-979c-4b062488616e | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
13e4645f-df8d-5910-baf2-c0b82ebfd420 | note | Acceptance Criteria - Signed ITP
ef451ab7-c771-5ef8-9c6c-e68622b53e13 | note | Verifying Document - Red pen markup drawings
02ee9c30-1ef9-537e-a7e0-f941a7a74a7f | note | Frequency - After installation of FSMH
ec02aa85-a5ca-599c-8032-35fae5ed0a51 | note | Inspection Type (Visual, other) - Document
144d11e1-c35d-501c-8054-4edfbef2e178 | note | Inspection: Key - H
0d93a497-5140-52ef-92af-e464fb7aea49 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1007 - Installation of Manhole - FSMH-A1 | itp | ITP-1007 - Installation of Manhole - FSMH-A1 | 1 | 0b0fb212-2821-4219-b1d8-d25634b484be
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
9c944456-aaa8-570c-afbd-83041f113b0d | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
c6ebbd4c-0297-5055-a3eb-7924a73ce439 | note | Acceptance Criteria - Items are approved as per contract specification
3e9335c5-4ded-55ce-96a7-96f1167b96e8 | note | ○ DCC approved
e402b958-12d5-5840-a813-702b4fb20a53 | note | Verifying Document - Photos, delivery docket
156f23b8-e638-5d98-ae0e-922d43de3e28 | note | Frequency - On Delivery
9f009fe1-0381-57c1-849f-e3f635b08faf | note | Inspection Type (Visual, other) - Visual
988644a3-b067-563f-9ad8-4e55699d86a9 | note | Inspection: Key - C
53120ce5-6838-573a-9adb-fe5a6c210451 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
cc3edff8-d4c8-5017-8777-dd6eafc55626 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
eca05494-0818-5482-bd75-dd93bc902e9e | note | Acceptance Criteria - Allignment set out matches drawing C4400-2 or aggreed with the Engineer
a37fe102-149a-50e2-bef9-61b67bce901f | note | Verifying Document - Survey marks, photos
86213202-f372-51a9-bcc8-25927764da5f | note | Frequency - Prior to commencement of works
f8e2225c-b5e3-5a96-86d8-386192c87b20 | note | Inspection Type (Visual, other) - Survey
9666c49e-409e-5e80-a063-836d58eaa914 | note | Inspection: Key - H
d66e82fe-b168-5cdf-8a64-56abdb5e21cd | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
ca74c357-4db9-5d64-ac08-07271c460100 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
21d395e6-7db6-58ef-8121-960d33196ae2 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
8e0b4de2-5a38-5c20-87e9-386d3f3e87d0 | note | Verifying Document - Delivery dockets, photos
ea6fb9c5-e728-5b7e-b13f-f79bd66e3d93 | note | Frequency - On Delivery
ebc0da6a-803e-5da8-8d7d-7abbbdc1d1ad | note | Inspection Type (Visual, other) - Visual
142ef0a9-305b-55d8-8f2b-19f50bb1c487 | note | Inspection: Key - C
5f8c380d-99e2-5ed4-948f-dd2cc9bf2be9 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
00942766-1d14-5d66-93b5-31ddfcb351c5 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4400
f988e3ca-b55d-52d0-a2ed-e748ba961db2 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
3c8146fc-1c3c-5f7e-9962-fa659f5c9db6 | note | ○ Floor of Trench to be even across width and length
ef19da8b-b82c-5699-870d-8d4246063218 | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
766ced10-59b6-500a-bd59-2ab91717eae6 | note | Verifying Document - Photos, measurement checks
76add296-34f1-54fd-8007-c3d99b0042b9 | note | Frequency - During Installation
efa07efd-49ae-5760-9872-b95d8eacb97e | note | Inspection Type (Visual, other) - Visual
69635b0c-5daa-5a4d-a111-56085607e195 | note | Inspection: Key - V
f76eb922-e8f8-57a7-ad03-5ad53ce4d7f6 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
8c839496-38a2-55ee-a946-94b4df250110 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
be32d594-a994-58f6-94c9-a5290345d245 | note | Acceptance Criteria - Minimum of 2 blows per 100mm
ff316229-4259-5cdd-a585-52ac1d68fb8f | note | Verifying Document - Test results
93e97bc4-a41a-599c-9402-7b0b47a6c4b5 | note | Frequency - During installation, per 20m
2a309cf1-690b-58f7-b044-92d6bb173195 | note | Inspection Type (Visual, other) - Visual, On site test
a7a84084-fbe6-50e6-92bf-b8c185229b48 | note | Inspection: Key - H
ea651c0a-c31f-5a28-8a7c-872696fc6e6b | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
8401336f-d25f-5dd6-bbbc-4d681ee3697c | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
960e79f6-3215-56bc-8844-371e489f411f | note | Acceptance Criteria - Bedding to comply with requirements
32da611d-8ead-5126-bb89-5c2ae2538ba1 | note | Verifying Document - Photo
28d58762-ba10-5818-b9ba-206dd13868a5 | note | Frequency - During installation
52f34e24-f0fb-5ed5-a70c-c2f9cfaeeac2 | note | Inspection Type (Visual, other) - Visual, Measurement Check
375dc0d5-7d5b-51a8-802b-6649a5f59a53 | note | Inspection: Key - C
c919c74c-aed8-5c81-b9e4-52b28149e082 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
0d5c0eab-c3b1-5d92-9a13-984815af7f67 | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
a3de11cc-2d22-51d9-b336-6999c04d787f | note | Acceptance Criteria - Final levels are in accordance with the C4400 or within tolerance and agreed with the Engineer
f3211e54-16ba-58fd-b958-5abbcf5cf902 | note | Verifying Document - Photos, As-built
1e165e38-8284-59da-ae21-d1b90fa66e08 | note | Frequency - During installation
eab72def-6d2a-53b0-8eb4-85e82082d0a5 | note | Inspection Type (Visual, other) - Survey
0c2534d9-3a76-5562-8607-f67a9acfc900 | note | Inspection: Key - H
f21f59e6-d4ad-5e34-b898-1ba7ebd79e26 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
051c3272-cfad-59ad-ae90-790b61514e59 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
11484d81-5f63-5420-93e4-b5c39927ae5a | note | ○ Benching shape to have smooth transitions at bends and junctions
4201a6d0-6557-5047-a172-56939822d0bb | note | Acceptance Criteria - Benching built up to the specifications
229a9782-619c-5b14-87a3-48709f78db89 | note | Verifying Document - Photos
81a392af-5b9d-52cd-85f3-546d80c60c5c | note | Frequency - During benching contruction
0746f08d-4f6d-59ec-bf65-e9269b837e86 | note | Inspection Type (Visual, other) - Visual, Test Results
0895683c-59ce-5dfb-b142-6b83c6af50ff | note | Inspection: Key - H
5f070747-8a2d-5bd9-b48d-3a7ca34bd449 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
962f9774-4d33-5bfd-833d-f5e3c6d4a54c | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
cf8ef5ce-fd60-5653-9703-0876db6fd5ce | note | ○ Compaction testing one test every two layers as required
0f708920-4193-5d34-9824-eceec8ceefea | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
b54d469e-fe1f-586a-b4d7-314e7025b3e4 | note | Verifying Document - Photos, Compaction test results
b8e8611f-a82d-572a-99e3-fbfddf404edd | note | Frequency - During Installation
52751212-2ed9-5ccf-996a-a4bc80ae5309 | note | Inspection Type (Visual, other) - Visual, On Site test
7e3e4e85-d427-5e06-a73a-cb5f8faa6bc2 | note | Inspection: Key - H
fc4d8c1f-0bfc-5116-a9fb-bb6473e2d005 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
08ec59ee-56cb-5cb1-be69-04ef62ba7815 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
ae27363a-f1aa-51ca-9dcd-fa70794a5483 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
22ed5cbe-24e2-5661-9c55-6786a6a863d2 | note | Verifying Document - Photos, test records
8317cb1f-703a-5b62-ae92-37aeb60756cf | note | Frequency - For every manhole
8342123b-407f-5e38-9ba1-b62043b545ab | note | Inspection Type (Visual, other) - Test, visual
486b9504-0920-5725-8792-5da29d4d05cc | note | Inspection: Key - H
ac60132c-0a6c-59aa-93ce-71a2ec59d09e | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
2ab6b4e8-8df5-54b5-88d0-b8aa1fd0ee03 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
ed5dc7b3-8416-572a-8c03-20d3c0da2821 | note | Acceptance Criteria - Signed ITP
bbfedd29-485c-5f0a-979d-accdb925ff52 | note | Verifying Document - Red pen markup drawings
54f648cd-498e-5dd1-be98-714bfafdc594 | note | Frequency - After installation of FSMH
b9a6ffc2-deae-5e1b-af83-08bfd62ce41e | note | Inspection Type (Visual, other) - Document
e40004ef-bc3f-50e7-967f-f8f7866c85ea | note | Inspection: Key - H
bd7731ce-94e7-5dfe-aef1-ad2fd78298b5 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | itp | ITP-1008 - Installation of pipe from WCMH-2A to WCMH-1 | 1 | 30c97d16-6742-4f7e-bfe0-90ff6786ca50
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
9fbfa753-62b5-5840-8f5c-bf538ffa02a6 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
d202728e-5c6c-5e27-b5a9-1adbf97cbaca | note | Acceptance Criteria - Pipes shall be DN475 SN16 PVC-U rubber ring jointed
921c29f3-03f4-5355-8ff4-9685ea218669 | note | ○ Items are approved as per contract specification
8166fe20-8a6e-50bf-9fa8-98a749c457c1 | note | ○ DCC approved
149c2570-044e-51aa-848c-dbdca55e0b20 | note | Verifying Document - Photos, delivery docket,
bdf7a695-3925-57ae-a828-3ea6e33c705d | note | Frequency - On Delivery
ecaa81e0-e9b5-5e62-be39-33c51ae0df33 | note | Inspection Type (Visual, other) - Visual
cdce3789-b321-5cc8-a3ec-87c7f5434171 | note | Inspection: Key - C
56936986-31ad-52e4-916e-845e8897321f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
833b47f4-3e8f-58ea-9bb5-6d39dcece58c | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
4062f108-cdc0-5059-84a2-f949be6a4ecc | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
bea0c50d-88b6-5ae8-ae7f-02867ebcc527 | note | Verifying Document - Survey marks, photos
bdb0944e-5f28-525b-81be-0a6c88f9b4e2 | note | Frequency - Prior to commencement of works
ca79c446-beff-5da3-a1a3-b63ae6eaee6f | note | Inspection Type (Visual, other) - Survey
6b854e07-cb90-5bb1-bc22-c3d280f85e3d | note | Inspection: Key - H
a2051a3c-95f6-5c74-b779-976959e1d745 | note | Inspection: By (Role Key) - SV/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill Material
305d5052-2e6a-5a1a-a824-499506b184a3 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10324.
670e5aa2-c584-5f7b-aa44-10a9b0122d78 | note | Acceptance Criteria - As per DCC code of subdiviison 10324
3611541f-e70e-56b7-8b86-74b4c34967d2 | note | Verifying Document - Delivery dockets, photos
24519e0a-9baa-5e64-afa0-c9d7aed9b25d | note | Frequency - On Delivery
8c01f679-1b29-5327-83e8-effe6627f3b1 | note | Inspection Type (Visual, other) - Visual
858cb321-5f1b-5f88-83f8-c2acc98f4583 | note | Inspection: Key - C
0d47a9b9-e6ac-5a71-9de0-4eab2bbc3073 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
638d5a55-32d2-5eba-b56a-a6ecb9b5e8c9 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per drawing C4200
9f455471-db22-5533-b40e-9bd1cc91d1cc | note | ○ Floor of trench to be even across width and length
c58381e4-0c54-5009-b6cd-b396954a4681 | note | Acceptance Criteria - Allow 100mm for bedding
d43fb638-05ea-537e-9b69-700273dbd2d2 | note | Verifying Document - Photos, measurement checks
7dca67ae-76a1-55ab-9ee1-5a1ef4bd2247 | note | Frequency - During Installation
69f3bebc-5c27-5274-a215-874159513e31 | note | Inspection Type (Visual, other) - Visual
3b03accd-5760-5f4e-85f1-6b6c71f3c4ae | note | Inspection: Key - C
390e4892-35ac-52bc-bd79-a128d0028fda | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
cd3a0620-7367-58d2-b9b9-969c31c9badd | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
70f37a66-d6a5-5270-ae43-a34169f91045 | note | Acceptance Criteria - minimum of 2 blows per 100mm
e7342646-5e9e-54b2-a75e-9653ad0c8523 | note | Verifying Document - Test results
0a3524f6-4a11-5ead-bca6-29cf6722eff2 | note | Frequency - During installation, per 20m
611fd3ec-48e8-5e3a-9815-1d831919fb6c | note | Inspection Type (Visual, other) - On site test
a80775e2-1d0c-5f78-8be1-05fa72adc80d | note | Inspection: Key - H
6cf2f752-a707-5633-8546-5512a63c93e3 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install Pipe
4c363166-460d-5a96-a72d-b7924fcf8622 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
4dcadefe-a899-582d-97ff-f6c225d60ca4 | note | Acceptance Criteria - Pipe not damaged during installation
91de3483-8cef-5608-abe5-29c88fb876d8 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
e2d3991c-b663-5dc1-9b57-e0694b5f62e6 | note | Verifying Document - Photos, Grade check sheet, Survey of position for as-built
2f443c9b-fb4e-5d7f-9709-9f1b064d93d4 | note | Frequency - During installation
5f3dfc3a-b73e-5d36-80c8-a5e57522cbc7 | note | Inspection Type (Visual, other) - Visual, Survey
c023637e-6e25-554f-93ff-ce7d36447ec5 | note | Inspection: Key - C
2aa1315e-0765-5075-ac64-958c43f14078 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.4 - Laterals connections and installation
ef40722a-f507-5b02-b348-5929c57b8332 | note | Inspection Point: Quality Control Activity - Lateral connection as per drawing C4310
35983ed5-0633-5886-b218-b3c7adbb6826 | note | Acceptance Criteria - Lateral connection as per drawing C4310 and DCC standard details and project specs.
56de8f20-f6fe-5aaa-a403-21b2b634c558 | note | Verifying Document - Photos, measurement checks
c5981c3b-5f98-5d31-b5f0-38d5b883970f | note | Frequency - Every Lateral
a435fb29-e5cf-5264-9843-00d93aa1a1cc | note | Inspection Type (Visual, other) - Visual, Survey
d4a714d3-343e-5a48-b7ce-3c39e2f846ae | note | Inspection: Key - C
7b4a5121-8a89-575c-8ed2-2140bf6decc5 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
bc37c08f-e34a-5961-b532-19c111293ac1 | note | Inspection Point: Quality Control Activity - Embedment material AP20 or approved by the Engineer in writing
fc5c891e-672c-5409-a7fc-ce4f3cdde181 | note | ○ Where required (trenches with >5% slope) AP20 stabilised with cement hall be used (40kg cement to 1000kg aggregate)
712c9d21-c05a-5868-9a9c-e7b3006d7c05 | note | Acceptance Criteria - min 100mm bedding
9bf26cd3-add6-56ad-99d4-35f093d2a0df | note | ○ 100mm overlay
c56e373d-52d3-51ac-8546-fa31e94b8221 | note | Verifying Document - Photos
a592180a-6d0c-5c14-8ed1-52a16b7ab331 | note | Frequency - During Installation
6e7acb20-07a0-5269-a949-519e5d2fbe92 | note | Inspection Type (Visual, other) - Visual, measurement check
829aca7a-2b9c-5108-9472-3af7e73b9979 | note | Inspection: Key - C
0e77e215-f078-5418-be53-e86ca9bf1c86 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
62c39fd9-b8ca-5fa1-85ba-4f86094f2274 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
6bff3366-a164-5f57-ae7e-68de2a3f7b76 | note | ○ Compaction testing one test every two layers as required
c2c8f2d4-7842-5d50-8eb1-3f053f8de0e2 | note | ○ Conductive signal strip to be laid at 300mm above pipe
ebbd758b-d762-50dc-99f9-14fcd38dc5d5 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1db21480-8fa9-5cb4-a648-7d28152d9f61 | note | Verifying Document - Photos, Compaction test results
2618520b-c8fe-5d32-8293-f33137afb955 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
762b5234-6d5b-5af1-8ac3-3a9aac7ec87f | note | Inspection Type (Visual, other) - Visual, On Site test
2a05f051-ae67-58b6-8284-2147bc3f2d7c | note | Inspection: Key - H
098b78f8-c8c8-5ec5-a195-5bdf489bbb03 | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
8bd24b35-9681-5a30-bb2c-bcadbd02bd8a | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
21d76fbd-f8d9-51c6-9cc1-c7a23751313a | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
03fe4385-7475-5c80-8755-701fafe7e1f0 | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
2023fe8d-11d0-5477-8161-95e381fd8872 | note | ○ Dips or ponding of water inside the pipe
709b2f0d-7662-5965-9b0e-0793207c4176 | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
859ec798-1207-5129-b161-5ce6976eaefb | note | Verifying Document - Test Records, CCTV footage
81527384-d626-5314-852c-e256bcb21409 | note | Frequency - Every section of pipe completed
9273ff0a-86be-542c-8b31-611ac8c9c376 | note | Inspection Type (Visual, other) - On-Site Test
d3f94ff6-34d3-5f0b-9d49-604d0f486d43 | note | Inspection: Key - H
4f406e5e-91df-567e-b751-00a5eec2679c | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak testing
a8647a26-85f5-52aa-8bce-64caa32f700d | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
b783d040-8543-50ce-a6fe-6edc8b2b69f1 | note | Acceptance Criteria - Engineer Approval
d1d50049-9c7b-5639-8692-acce007720ea | note | Verifying Document - Test Records
26457815-1c0d-5590-a349-5aa515236dfb | note | Frequency - Every section of pipe installed
91644c01-e863-5c94-b8ae-df41f1d71be9 | note | Inspection Type (Visual, other) - On-Site Test
7f7aee61-7b4b-521f-8085-e3bf1d0ebe13 | note | Inspection: Key - H
5805cebc-c181-512a-a54b-edeca012ebb6 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
a200137e-460b-5c7c-a761-38a5356aa73d | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
a449b680-e434-5719-8493-59f1538cf4ad | note | Acceptance Criteria - Signed ITP
f884d3cf-fed5-58b2-bf78-334783f100c7 | note | Verifying Document - Red pen markup drawings
1a7ea784-2121-5a95-ae50-dea9285b4647 | note | Frequency - After completion of pipe section
f1e76802-f9e5-5ac0-8a22-7cb2087370cd | note | Inspection Type (Visual, other) - Document
c7a852e8-6447-5ba4-906d-2ea7c5d90966 | note | Inspection: Key - H
d4ba4208-96f5-55bd-b558-edd56ace4e4b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-1009 - Installation of Manhole - WCMH-1 | itp | ITP-1009 - Installation of Manhole - WCMH-1 | 1 | 44d20cfb-a373-4bd2-82ec-3c15da2e7499
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
4bba8f0c-bedb-5fb0-8969-0c980dc0215b | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
ee0dd9d0-6654-59b7-b028-36af54ee93b5 | note | Acceptance Criteria - Items are approved as per contract specification
f9de903e-253b-58b2-9df4-f35504fe6cd8 | note | ○ DCC approved
c8083818-2d19-5401-817c-0e41c8a0f59e | note | Verifying Document - Photos, delivery docket
b5dc0145-6899-5802-8337-27f1860c5544 | note | Frequency - On Delivery
30219fde-0c78-54ea-a456-4a9334dca039 | note | Inspection Type (Visual, other) - Visual
11435c04-3962-5adb-97cb-9d6223beaadd | note | Inspection: Key - C
d1423c98-6dc6-5e86-9efa-71de3953a734 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
e7156165-aee1-56d0-baef-820d7de568ac | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
35089c78-f9e4-5412-8d1e-1947d0ff0f39 | note | Acceptance Criteria - Allignment set out matches drawing C4200-2 or aggreed with the Engineer
dd5fccc5-a1d3-58bf-8c6d-fafc6d627548 | note | Verifying Document - Survey marks, photos
582da6db-b956-5bcd-98f9-d97a74d28827 | note | Frequency - Prior to commencement of works
40dd9e6f-881d-54f1-900d-f407820d604c | note | Inspection Type (Visual, other) - Survey
65604cd3-4381-587f-8dc8-f8e655c4eaa6 | note | Inspection: Key - H
d2220e04-ea6e-5c89-bd1e-0fb73c14b440 | note | Inspection: By (Role Key) - SV/SP/QE
| signoff | HOLD POINT
| checkpoint | 3.3 - Backfill / Bedding Material
c3553c7b-e239-52b5-8f8f-6dab93cf91d0 | note | Inspection Point: Quality Control Activity - Approved Material, AP20 as per DCC code of subdivision 10329.
c1cbe52a-7ba7-5e0e-8864-2bf8a6298f74 | note | Acceptance Criteria - As per DCC code of subdiviison 10329
c4843dee-9ffb-53cb-b2c3-1156f96b6434 | note | Verifying Document - Delivery dockets, photos
d6c5a021-73e2-5da8-a5ae-6e433ee02942 | note | Frequency - On Delivery
34f5a313-cb40-562f-bdbe-7edecde82e3d | note | Inspection Type (Visual, other) - Visual
930626e8-eaa0-566b-a064-b867591ec4ba | note | Inspection: Key - C
dfaacdfe-de84-5e22-8892-c1a560eedbb4 | note | Inspection: By (Role Key) - SP/QE
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
b2ccea4c-a642-533c-9959-b69b08169a73 | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
45e6a967-ac20-527f-83d4-ad2decdd29ea | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
41c70a73-3c1d-59bb-955b-94be1d0648a0 | note | ○ Floor of Trench to be even across width and length
5675a2b2-064e-543e-a8fb-f18c49476165 | note | Acceptance Criteria - As per 561467-TW-04-DRW-001
6460381c-725e-5df9-8d3a-d622be4b69b5 | note | Verifying Document - Photos, measurement checks
5f9241db-4e59-582d-961f-2554d5c2645b | note | Frequency - During Installation
dc7e6ecf-3b09-59c1-9c0b-6cb4e257b20e | note | Inspection Type (Visual, other) - Visual
9bba54ba-de83-5239-8e35-85a873c59ab8 | note | Inspection: Key - V
d39c4d9d-872a-5f24-95e9-2d6cd80572f4 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.2 - Foundation
66cc17a0-1741-54ec-9037-12708146e48c | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
6f48e733-4c7d-5504-ab50-96604e26a06d | note | Acceptance Criteria - Minimum of 2 blows per 100mm
048742b5-e420-505f-a0b4-b79e6b0e5c81 | note | Verifying Document - Test results
c5c1b880-1138-5801-9ae3-397cccf1d3d4 | note | Frequency - During installation, per 20m
10caefc7-24f2-5020-8a6f-022f90ccc2f4 | note | Inspection Type (Visual, other) - Visual, On site test
990e78e0-ca6a-5bd9-a5e8-a2cda578ca3c | note | Inspection: Key - H
b7c253da-4966-514d-9a99-b6bbea3a0c80 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Bedding
cdf17202-8724-5cd5-a3fa-e53ae564f944 | note | Inspection Point: Quality Control Activity - Bedding minimum 150mm compacted material
57ca8dd9-eb73-5f7e-a201-f4cb8819058d | note | Acceptance Criteria - Bedding to comply with requirements
1e3ac7ec-b384-54e1-909a-d02f3fbcbff3 | note | Verifying Document - Photo
2113429f-4cf7-547d-8614-e1f0af0e4b74 | note | Frequency - During installation
19832ed9-691e-55ea-a268-e8d62d4e7f70 | note | Inspection Type (Visual, other) - Visual, Measurement Check
82388996-cd26-58d9-b7e2-294fce67c929 | note | Inspection: Key - C
b9e70f09-12ba-554b-852f-f124f3791a10 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - MH Installation
d942c43c-b7ca-5eb7-9db5-99379fbe2c2d | note | Inspection Point: Quality Control Activity - MHs to be installed true to the design level
44238abf-a60a-54ff-ad49-6dde4bb8a678 | note | Acceptance Criteria - Final levels are in accordance with the C4200 or within tolerance and agreed with the Engineer
3566d868-c896-55eb-b2d6-2a2938b54a80 | note | Verifying Document - Photos, As-built
3e25e488-b705-5971-a5a1-abf024b0fb26 | note | Frequency - During installation
449fc9df-2809-5163-bdef-354d88e3a99f | note | Inspection Type (Visual, other) - Survey
d6c97684-c881-59f0-a9f3-ec5bb97e5e00 | note | Inspection: Key - H
42f0a032-2f6b-575d-a3b8-5d9d64ec5b57 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.5 - Benching
167c5266-3770-508a-ae0b-89b6c82f6443 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days.
1abdff5a-1b61-57b0-b5bc-06449d170f13 | note | ○ Benching shape to have smooth transitions at bends and junctions
822edcdc-e161-57f1-b85a-6bf53c4b92b0 | note | Acceptance Criteria - Benching built up to the specifications
e58acd2d-fa29-509e-ba17-804e6f463446 | note | Verifying Document - Photos
a8c3f034-2c26-5e91-804a-d84a2d4552fa | note | Frequency - During benching contruction
f048d018-1558-56ae-a0ae-d7614f451ddb | note | Inspection Type (Visual, other) - Visual, Test Results
a8f609ef-45da-57ef-956f-53760fc18c23 | note | Inspection: Key - H
4380f189-3dfb-541e-8eff-1e37c5edcd07 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
2d959c0f-236b-5fcb-a06c-b15ed1c6282e | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
4dc6ed87-34f7-5dab-887b-96492ba55425 | note | ○ Compaction testing one test every two layers as required
23befd66-83b5-57f0-9389-63a3b4c79118 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
3876fd68-f718-57df-bb19-3f2f48734dc6 | note | Verifying Document - Photos, Compaction test results
0ba0c3a8-0ed5-58ca-9648-e6db15e37f01 | note | Frequency - During Installation
e34f44ce-9b1b-5007-90bc-180195489e62 | note | Inspection Type (Visual, other) - Visual, On Site test
367ed3c8-06b6-5a6b-8865-9b7decf42b81 | note | Inspection: Key - H
8c4229f9-c268-5b3b-80f0-a3a01cc705c2 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.7 - Reinstatement - Carrigeway
| note | Inspection Point: Quality Control Activity - Match existing pavement thickness or minimum of 35mm. - Place a tack coat.
| note | Acceptance Criteria - As per CI-094 / AC20-80mm followed by AC14-55mm
| note | Verifying Document - Photos
| note | Frequency - During Installation
| note | Inspection Type (Visual, other) - Visual
| note | Inspection: Key - H
| note | Inspection: By (Role Key) - PE/SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
e81040af-9acd-53da-bcc3-5b2bb36ccf60 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
f7b3631f-d592-5cc9-8c42-edc47bf4dce4 | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
e1153e1a-af64-5704-85e2-f4e9cb30fde1 | note | Verifying Document - Photos, test records
44b7803e-1682-52a1-a201-5ae8c9dcc41d | note | Frequency - For every manhole
8d308915-c59c-5264-a658-e2cb9af205df | note | Inspection Type (Visual, other) - Test, visual
288ed0d9-b6fc-5c0e-a96f-2d8ecfe9c1ca | note | Inspection: Key - H
751f5cf4-630a-5f15-bcc0-b724d99c02be | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Red pen markups
222a2907-4622-55d9-87a8-bf6dd5c5f67f | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from project drawings
0fcc88b2-3ab8-5015-b305-b1b55e43b262 | note | Acceptance Criteria - Signed ITP
ee0759fc-cbcf-5ecf-a72e-a47c3648acfb | note | Verifying Document - Red pen markup drawings
a8b08e99-a452-5b7f-b374-28485b3dffc2 | note | Frequency - After installation of FSMH
5dd8d99f-f3d4-584e-9758-37824a076a72 | note | Inspection Type (Visual, other) - Document
4a1b0c21-d0e5-596c-91f1-738d3e84e129 | note | Inspection: Key - H
503e0ce5-25c4-5f75-93a2-9e60397cc53b | note | Inspection: By (Role Key) - SP/QE/CM
| signoff | HOLD POINT
/1 | checklist | ITP-4001 - Brick Barrel Corbel Connection | itp | ITP-4001 - Brick Barrel Corbel Connection | 1 | e2e83650-14ec-4676-8a85-5d05c37c2771
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
df6a6cb8-4f95-51c2-be51-1aceeb681998 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
586907b7-5ab2-589c-8f35-0b9c5853c9b0 | note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
6a6315a6-276b-568a-84bd-092d52ae19c7 | note | ○ Items are approved as per contract specification
088fb763-f7e4-56a7-b925-82904c7ba48b | note | ○ DCC approved
3180f4f7-5c5f-5f42-9488-c8ecf3166c7a | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
aff52395-af05-54b6-8492-db24467d282f | note | Frequency - On Delivery
2e2e8ddb-6ee6-5fc8-ad4f-c0e2eb927738 | note | Inspection Type (Visual, other) - Visual
4f4e092f-2a67-5643-be02-876c17b8058c | note | Inspection: Key - C
b35713ac-9921-564d-94c5-590a47271b61 | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
225acd77-0423-50c7-9fe0-2a79ffc2fa29 | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
58562ff4-07d7-5a9e-8b3a-98b486d37d32 | note | Acceptance Criteria - Allignment set out matches drawings, 2D data and linework provided or aggreed with the Engineer
44c9ff24-e2f7-5a09-8494-30cfe6936470 | note | Verifying Document - Survey marks, photos
71beee53-1c7c-5185-9fac-4e8cd82317d2 | note | Frequency - Prior to commencement of works
14fca69e-c4e1-5626-a156-3fcc914cf4df | note | Inspection Type (Visual, other) - Visual, Instrumental
d44b69f3-c640-5fcd-8286-6388d6ad17e4 | note | Inspection: Key - H
b18a2c94-16da-5305-ba2a-6345a5a6dc83 | note | Inspection: By (Role Key) - SV/SP/QE/CM
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
b7e4ff50-ff5e-51b9-bf9a-033f2cb7d274 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200, C4300, C4301
df4c971a-caff-50f1-b84d-1d6f7ba02975 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
b6149933-2d60-5b43-906c-3e91bdbc1913 | note | ○ Floor of Trench to be even across width and length
2b94477e-f9c6-5b5d-a509-7f1d1a3fec41 | note | Acceptance Criteria - Allow 100mm for bedding
681feb7b-91a1-570b-a656-e919ce52372b | note | ○ Allow for minimum cover of 750mm.
713bd5a6-e50a-57ce-a93c-03af39277527 | note | Verifying Document - Photos, measurement checks
2271ab2c-1eb8-588c-ac46-439046d9bb34 | note | Frequency - During Installation
ed10fbc7-f530-5520-adf0-632dabd1a2c8 | note | Inspection Type (Visual, other) - Visual
26f93781-3cc6-55fd-a5e9-33d2d084424e | note | Inspection: Key - C
5e8a2d28-3e55-5549-accc-27c9401cac79 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Foundation
019d366e-d262-5769-9e01-6c02ffcef3a9 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
77277469-fdb4-52cb-8a31-f7beb95702d4 | note | Acceptance Criteria - minimum of 2 blows per 100mm
3636cfd1-b513-5eae-8b2f-2d247baa54a2 | note | Verifying Document - test results
27f1245c-e4b7-510c-b3fe-8835df6f7734 | note | Frequency - During installation, per 20m
20f44909-0a5b-500b-825b-44ef19c7d5ca | note | Inspection Type (Visual, other) - Visual, On site test
a7737c7f-e457-5683-921c-ac2b7584507b | note | Inspection: Key - H
b2cee8ec-bd49-5a23-a473-4c66f7c0b5fd | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.3 - Install corbell
572abdee-4a99-5882-b0a5-48525bcf1eed | note | Inspection Point: Quality Control Activity - pre pour inspection
241ad6b3-0569-5d1b-96e8-0890d56db9d9 | note | Acceptance Criteria - Engineers approval to proceed
560bbe87-6fbb-5480-854d-2868bdd8d75f | note | Verifying Document - Pre pour inspection form
c506e4d2-6527-5655-b277-02cc6cade40d | note | Frequency - Prior to pour
9930c6d3-a850-5a83-8d22-2ebed0880616 | note | Inspection Type (Visual, other) - Visual
74ddb0fe-1ae3-5887-b969-3676cc54038d | note | Inspection: Key - I
f358af24-db3b-566e-a5e1-412f10ade309 | note | Inspection: By (Role Key) - CR
| checkpoint | 4.4 - Install Pipe
bd419529-1ae9-5538-b903-c2c30d8d60c4 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200, C4300, C4301
19d88ea5-5e3c-5502-bb84-d786f304eda1 | note | Acceptance Criteria - Pipe not damaged during installation
d0ae15ac-ad5c-5c38-98c6-1257cf696152 | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
9ef0c3b8-4bb8-572c-9bf4-202eab54d55b | note | ○ Pipe installed at approved angle
e7460f0a-2048-5e09-980b-4caecb6d770d | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
a9643693-70b9-527a-b6ce-e32117949c9f | note | Frequency - During installation
94f92a24-7547-5f02-9b4d-c2f6fa7ea38d | note | Inspection Type (Visual, other) - Visual, instrumental
e8df5b1c-0441-5279-ab90-2238db549453 | note | Inspection: Key - C
6f475b95-b9ee-510e-b8ca-6ac7a107d924 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
bd716f95-4b33-5c53-8b08-15cef9ecc057 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
64533a30-3800-5889-b164-c0bc8e781443 | note | Acceptance Criteria - min 100mm bedding
a5c4c4cf-f373-53c4-b164-e06f23981bb3 | note | ○ 150mm overlay
3e23554d-c91b-55c9-819b-45f3185f16a6 | note | Verifying Document - Photos
85d4ff2a-5ad9-50d9-95e1-e0f20919e92f | note | Frequency - During Installation
5c56996c-74db-5ae8-af52-bcee11199049 | note | Inspection Type (Visual, other) - Visual, measurement check
b79421e2-e43c-5ed2-a862-dde20c27f2dc | note | Inspection: Key - C
f1f3f54b-b7de-5009-87f8-77ff40042b71 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Backfill and Compact
7d48c4fe-feb9-51cf-be3f-b91585d6826f | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
396778eb-09bc-58f8-86dc-83c81be956cc | note | ○ Compaction testing one test every two layers as required
f85be66b-af91-5cbf-95ac-cf81b4f4df88 | note | ○ Conductive signal strip to be laid at …mm cover
2987fc39-3716-5ace-bdc8-966f37d1cf92 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
41405a61-90f6-5085-b988-63edff3a1c9c | note | Verifying Document - Photos, Compaction test results
ae468b6a-3865-557f-898e-fcb2e02da7bd | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
fd2d5433-4ac0-5808-aece-62607c897a32 | note | Inspection Type (Visual, other) - Visual, On Site test
6677f2f7-7ff1-5ca7-9bca-b6a9b2967cb4 | note | Inspection: Key - H
ec24dab7-9b5f-52ec-a312-b58ae892f41a | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - As built
eb3c23bd-396c-5a7c-817e-78cd93a84fda | note | Acceptance Criteria - Engineer Approval
72915a9a-98b4-5c94-a884-64dffc7aebfb | note | Verifying Document - QA records
9debece8-6676-5674-9aad-577bcb23380b | note | Frequency - at completion
2d4c15ad-2980-506d-be93-ceb95d50afcf | note | Inspection Type (Visual, other) - H
bbf6b9ee-735e-5025-88f8-adf4e2234a73 | note | Inspection: Key - CM/PM
| signoff | HOLD POINT
/1 | checklist | ITP-4002 - WCMH-5 | itp | ITP-4002 - WCMH-5 | 1 | 9288ffc6-0ed4-4be6-b70d-0bb793bcd661
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
38603c8f-a73c-5d3d-82f1-28b95910bac8 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
9c267aa9-0cf7-5ce5-84c5-061a05ab0636 | note | Acceptance Criteria - Items are approved as per contract specification
07635d10-95b8-5590-8a3b-78d90300b01c | note | ○ DCC approved
68703632-508d-5e5d-954d-ce925de00a15 | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials
e79ca831-2d9d-5c32-95f2-e0cc09660e08 | note | Frequency - On Delivery
f65e4f50-fbc7-5114-b934-12ba70cc876c | note | Inspection Type (Visual, other) - Visual
e03b5b46-05ea-57a1-abb6-130c5cbfcccb | note | Inspection: Key - C
65de8343-ad37-5854-9247-8f0f72e39085 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 3.2 - Set out
bfc82637-aaf4-5433-8c1a-408b5acaf4bd | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
89ac8ef3-7f5a-5e88-8bf9-a3f875988828 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed with the Engineer
e5a14dd7-3629-55b7-b396-dda6dac09c4b | note | Verifying Document - Survey marks, photos
8d03c984-cae6-545e-81f9-c5fd949e1c9b | note | Frequency - Prior to commencement of works
a97224c6-c592-5809-a764-70600471ae60 | note | Inspection Type (Visual, other) - Visual, Instrumental
da82f296-0062-59fd-b461-65eab2d4bc44 | note | Inspection: Key - H
3c3c0e11-54bf-5a9d-bd5b-18b3487a3c57 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
8261be8e-3b86-5fe8-9e6b-db454c71faaf | note | Inspection Point: Quality Control Activity - Excavate to required depth to invert as per C4200
994c45d7-2f1b-5ef6-8094-e9598e4e6bc2 | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
4b9898c5-242a-59f1-a4b2-c3afaa7455a3 | note | ○ Floor of Trench to be even across width and length
0e3b8cb1-8106-5f6e-b1e2-95bd2c6c778b | note | Verifying Document - Photos, measurement checks
6a299a39-c994-5c6b-bbda-5e01b757a357 | note | Frequency - During Installation
dbb2364c-9356-5d6a-ba4a-9de963d3bac6 | note | Inspection Type (Visual, other) - Visual
1f515b94-1bc0-50b4-800b-acd76aed6fbe | note | Inspection: Key - V
4639a0bc-8afe-5e70-b44d-2c89026711b8 | note | Inspection: By (Role Key) - SP/QE/PE
| checkpoint | 4.2 - Foundation
bedd57af-f748-5622-ab50-bc09b56e7f26 | note | Inspection Point: Quality Control Activity - Scala tests on base
a5a9c327-6b92-5386-9837-7d85367045ca | note | Acceptance Criteria - minimum of 2 blows per 100mm
5daf8c44-62c9-5d5d-af5e-597f07cb2f48 | note | Verifying Document - test results
1bdac60f-976c-5d3a-8f8e-b85af7a0a9da | note | Frequency - One off
031b4f8e-d70b-558c-9fe3-0e2beaebe73d | note | Inspection Type (Visual, other) - Visual, On site test
85d9d35b-aa6a-516e-97ae-79ff198602d6 | note | Inspection: Key - C
ce6a87c3-bea1-51eb-aa81-a8e80422a68f | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Bedding
9b7be36a-4d29-5381-b326-3ae29434cf20 | note | Inspection Point: Quality Control Activity - Bedding minimum 75mm compacted material
9b117924-f2fc-5dec-8892-8369b9c6f17b | note | Acceptance Criteria - Bedding to comply with requirements
d1fa6168-e255-52d7-bf49-6cea3eb08aa3 | note | Verifying Document - Photo
5778ed11-0cce-56c3-9d8a-7204219c1b49 | note | Frequency - During installation
ad94ef2e-1f9f-5aa2-9c15-ac75da3dbd35 | note | Inspection Type (Visual, other) - Visual, Measurement Check
1c643703-4893-5e4b-8924-1438ac282e91 | note | Inspection: Key - C
29b35aa2-e61d-5d02-b15d-535273317b10 | note | Inspection: By (Role Key) - QE/SP
| checkpoint | 4.4 - Chamber Installation
8fa3e48e-fcea-5e18-886f-6da1c9b22b6f | note | Inspection Point: Quality Control Activity - Chambers installed true to the design level
8e7e29a8-d04e-5c66-bdde-cdcfa0202099 | note | Acceptance Criteria - Final levels are in accordance with the drawings or within tolerance and agreed with the Engineer
49e59276-ffec-5798-a96f-f90e3827b361 | note | Verifying Document - Photos
005763f4-aba0-56b3-a823-bf70212a06bf | note | Frequency - During installation
30da20b8-85ab-5e07-a4b2-9bf402e9e1d3 | note | Inspection Type (Visual, other) - Visual, instrumental
d9651a06-241a-5264-ab38-76add105648f | note | Inspection: Key - C
2a0a209f-be3f-55f6-af65-c6dc81a5bf16 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Benching
5004ff03-0b46-5519-90ec-18dfd4bc3858 | note | Inspection Point: Quality Control Activity - Benching concrete shall have a crushing strength of 20MPa at 28 days. All benching and sloping surfaces on manhole floor shall be rendered in 20mm thick 1:3 mortar
b76e848b-6fc8-53fe-bcec-d3782e58347c | note | ○ Benching shape to have smooth transitions at bends and junctions
4860b592-5293-5da4-89df-6e9e0441aa52 | note | Acceptance Criteria - Benching built up to the specifications
d9e719b5-8a10-5050-80be-c503d0085b3d | note | Verifying Document - Photos
98c10eea-6d73-520e-8b13-c92526597efc | note | Frequency - During benching contruction
7ffb771d-3810-5af2-9c03-8af3e7babc23 | note | Inspection Type (Visual, other) - Visual, measurement check
c1344bc6-bc2b-57b8-a74b-682bdc3b19c4 | note | Inspection: Key - H
5308cc01-12e1-5a76-ac3f-8b34b0dec9c0 | note | Inspection: By (Role Key) - SP/QE/CR
| signoff | HOLD POINT
| checkpoint | 4.6 - Backfill and Compact
ffb18f72-2e7e-5229-bca1-ccac49a0e930 | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
61b74aea-25a8-528e-8edb-dd8b128c052b | note | ○ Compaction testing one test every two layers as required
855cf8a1-5bac-59dd-a8b6-c89df0dab385 | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
d609b4d9-4a9b-5bcb-8c39-5497aa3d0669 | note | Verifying Document - Photos, Compaction test results
90518fb7-7b58-5a35-8957-c77127c90408 | note | Frequency - During Installation
7317b953-c5df-509e-a83c-abb29536cd4c | note | Inspection Type (Visual, other) - Visual, On Site test
1561bf6a-ce61-5c95-82cc-e72f9bf8526b | note | Inspection: Key - H
f69cb71b-3f9e-5b17-81f0-ec5d5b8ebfa3 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - Leak Testing
85871b29-7e2b-53af-9055-c7a5939fe7d0 | note | Inspection Point: Quality Control Activity - Manholes to be water tested up to within 150mm of the concrete lid level.
02dfb382-218b-5265-bec7-14042d01f6ed | note | Acceptance Criteria - The amount of water leakage from chamber under test shall not exceed 1/300 of the volume of the chamber during a 30 minute period
836e8631-b378-5042-960e-d5888427bf20 | note | Verifying Document - Photos, test records
c1ff320f-a793-52da-bd22-55f1a9c9a5e9 | note | Frequency - For every manhole
91dc5f95-d488-5bab-b5fd-a08345a6ea50 | note | Inspection Type (Visual, other) - Test, visual
57774758-f600-59c4-9e2d-3088a547c5b5 | note | Inspection: Key - H
8000a74d-ae72-5c21-b7de-fcf1d76b22e7 | note | Inspection: By (Role Key) - SP/QE/PE/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - As built
0d089f0a-1f73-554b-8f41-6abc17237ee8 | note | Acceptance Criteria - Engineer Approval
924fa07a-a0d7-5c8c-8d10-a3ab51d55132 | note | Verifying Document - QA records
b1045636-68e5-5afa-8560-f907829ad853 | note | Frequency - at completion
282d2a98-a19f-52ba-b676-62f80d90217b | note | Inspection Type (Visual, other) - Asbuilt drawings
5e8866e2-f29d-5476-ac1e-55fdbc99ce68 | note | Inspection: Key - H
c63bbce1-2a68-52e1-b8dd-26f7d75f1068 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT
/2 | checklist | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | itp | ITP-4003 - DN750 WC main WCMH-5 to WCMH-4 | 1 | 59b9401e-e477-4206-8eed-a125cb4292ae
| section | SECTION 3 - RECEIVING INSPECTIONS
| checkpoint | 3.1 - Material Delivery
fd6945ee-161e-528f-a7ba-18671463b1f4 | note | Inspection Point: Quality Control Activity - Inspect for damage and wear, Confirm items are correct as per drawings and Specifications
30500143-ffbe-5e6f-b61b-3f02c8de8a97 | note | Acceptance Criteria - Pipes shall be DN750 Class 4 RCRRJ
25a84a91-46b6-5297-bd5a-7c2e359cc295 | note | ○ Items are approved as per contract specification
872e47c9-deec-5ace-9b6e-bf29fab0b698 | note | ○ DCC approved
4cbd8926-a97c-5e69-9c28-12c208e9b94e | note | Verifying Document - Photos, delivery docket, MDD results for backfill materials (if required)
c638e561-52bc-5cc6-940d-97426bc3270f | note | Frequency - On Delivery
32412e66-96ea-5503-a4bd-fd012de17507 | note | Inspection Type (Visual, other) - Visual
0e3de0f6-fbf7-5689-9c59-a9a488b72514 | note | Inspection: Key - C
37a5d4d0-ae36-5598-b6ae-d0c128a6a6e6 | note | Inspection: By (Role Key) - SV/QE
| checkpoint | 3.2 - Set out
1d025ba7-84f8-5a68-80aa-f546c3e476fe | note | Inspection Point: Quality Control Activity - Set out completed by an approved surveyor marked allignment
a18a71b7-f5b3-55da-9a42-315f8a3fb085 | note | Acceptance Criteria - Allignment set out matches drawings or aggreed by the Engineer
c438f1ca-ca49-573a-a728-98d9b23df8fc | note | Verifying Document - Survey marks, photos
145385a7-3c62-5568-8c18-f5d74aebe421 | note | Frequency - Prior to commencement of works
b53b2af4-9ec3-5597-820f-1b1844e48c44 | note | Inspection Type (Visual, other) - Visual, Instrumental
907002a6-abe7-5234-a401-c5411967045c | note | Inspection: Key - H
5170a963-0ce3-5629-898f-7773978a3e51 | note | Inspection: By (Role Key) - SV/SP/QE/PE
| signoff | HOLD POINT
| section | SECTION 4 - IN-PROCESS INSPECTIONS
| checkpoint | 4.1 - Trench Excavation
876c492a-569c-5cad-af49-b1f4a14d0982 | note | Inspection Point: Quality Control Activity - Excavate to achieve required depth to invert as per C4200
f726ae62-5fc4-55d1-b510-9bdece611fba | note | ○ Trench width to allow for 300mm seperation between springline of the pipe and trench wall or an adjacent pipe
2e968e45-52fd-5eca-91d4-f9f0f9cdbd9b | note | ○ Floor of Trench to be even across width and length
3b577317-9241-5e89-8610-01d9fe1b0b35 | note | Acceptance Criteria - Allow 100mm for bedding
06794c26-132e-5aee-8dc1-d514aead8a3c | note | ○ Allow for minimum cover of 750mm.
57e0e33f-08ae-5ce0-84ca-228614e7049f | note | Verifying Document - Photos, measurement checks
1cb1a6e3-29a6-59ac-8117-1e241067659e | note | Frequency - During Installation
13749fcb-6ec8-5dcb-8f20-5c27a7ca0a79 | note | Inspection Type (Visual, other) - Visual
58cbc2ee-2495-5961-9a85-2385c3b78aff | note | Inspection: Key - C
1bf9adb5-fc40-5a40-af5c-8530adc1e7da | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 4.2 - Geotextile
a01e27da-3e23-5b0d-8e39-cde180bf65b8 | note | Inspection Point: Quality Control Activity - Install Bidim A29 or approved equivalient around bedding, haunch, overlay zone and trench fill up to the subbase.
a4e4ff19-b865-52d0-a713-267a182ce132 | note | Acceptance Criteria - Geotextile not damged during pipe installation and backfilling
0864ed3d-5d0b-55f7-9d86-da2dedd9d448 | note | Verifying Document - photos
f865fed2-061a-549e-b998-657a685eb152 | note | Frequency - During Installation
9d442d0d-e9cf-5a89-a5f9-0bccfa4ca9f2 | note | Inspection Type (Visual, other) - Visual
3c852204-1ad1-5825-8b23-c8338d5c19b8 | note | Inspection: Key - C
fb694baf-9510-5682-9be8-cd6c79bb6041 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.3 - Foundation
6c32f554-45a8-5982-b71d-dca3d103fcb3 | note | Inspection Point: Quality Control Activity - Scala tests on base of trench
5ec6f3c9-66ec-5521-8443-fe515516bc0d | note | Acceptance Criteria - minimum of 2 blows per 100mm
3fe36b72-c1c3-538d-959b-e45ea6bc8401 | note | Verifying Document - test results
ed36a9ca-a1bc-528e-aa48-9e7e4a9ae34d | note | Frequency - During installation, per 20m
44ef94b6-f5d4-554e-bbf4-5b0310580a0f | note | Inspection Type (Visual, other) - Visual, On site test
d4f55b18-cbcd-5461-aa31-b605fd390874 | note | Inspection: Key - H
bedcb70b-88f8-579c-8759-7988b37c23f7 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.4 - Install Pipe
01774be6-7dc1-5c81-b86a-e4bf082451e0 | note | Inspection Point: Quality Control Activity - Pipe installed to grade as per drawing C4200
e3885ae4-8036-572c-abc6-f8802c2bd193 | note | Acceptance Criteria - Pipe not damaged during installation
794e737a-2ee8-5ac6-b649-813a5ceab51b | note | ○ Pipe installed to grade within tolerances specification GP 3.1.8
005e0fb5-bc55-5c1d-9353-eb2af465a1d4 | note | Verifying Document - Photos, Grade check sheet, Survey of position for asbuilt
5f6b8ad9-7595-5489-b523-045227f15a4a | note | Frequency - During installation
0fb163fd-01ae-5e8c-838f-52ef56dbdb84 | note | Inspection Type (Visual, other) - Visual, instrumental
be2be8c5-4579-5558-b01e-23e65b49783d | note | Inspection: Key - C
218d0fd8-0a90-5908-b041-ef93fb4df668 | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.5 - Embedment zone
635df6bc-2169-5075-9217-3ee8d00a7d28 | note | Inspection Point: Quality Control Activity - Embedment material shall be AP20 or approved by the Engineer in writing
bbd42304-d1c1-5a05-bd03-efb6f7749b8a | note | Acceptance Criteria - min 100mm bedding
9e8031c2-4766-5977-a396-fead57d2b48a | note | ○ 150mm overlay
d8b9e474-727f-5ee5-8691-0bb3131de80c | note | Verifying Document - Photos
2696b515-34d1-5d3e-be54-4061b38c961f | note | Frequency - During Installation
3259ebe2-d38a-531c-824a-f1f258940d2d | note | Inspection Type (Visual, other) - Visual, measurement check
18dbfcc2-4a89-541f-9ea3-9e611a4e10c3 | note | Inspection: Key - C
de3b6d4a-fa11-5e69-9ce7-aae5376e159d | note | Inspection: By (Role Key) - SP/QE
| checkpoint | 4.6 - Bacfill and Compact
5acfd24f-c4b3-5a56-8afa-017a6cd382ce | note | Inspection Point: Quality Control Activity - Backfill in 200mm layers of compacted material
96405d46-6e1a-5c33-86d3-d93a5fbd2dde | note | ○ Compaction testing one test every two layers as required
58f08d5f-b76a-5af5-947b-54470eef25ce | note | ○ Conductive signal strip to be laid at 300mm above pipe
3f878185-066f-5194-88ab-ea20381b2f1d | note | Acceptance Criteria - 95% MDD in roads, paths, and pavements
1825faef-0a26-55b7-83b1-c69af9b159fa | note | Verifying Document - Photos, Compaction test results
7dc98ecd-1581-5e8f-b7a3-4a0ab66d8a18 | note | Frequency - During Installation, compaction testing per 50m of pipeline or per straight section of pipeline
65acd8ea-4631-5acb-814d-cd26fd5fc915 | note | Inspection Type (Visual, other) - Visual, On Site test
75a8bf67-1ef5-5ac7-87d7-505aacc93b2c | note | Inspection: Key - H
6de8bec6-504c-512a-a402-c398fbe2f3d5 | note | Inspection: By (Role Key) - SP/QE
| signoff | HOLD POINT
| checkpoint | 4.7 - Reinstatement - 326 Floor
a295dbdf-f5c5-57b8-abad-47ad06c1750e | note | Inspection Point: Quality Control Activity - DPM inplace
2862edf5-2db4-5161-af16-02037e63d3db | note | ○ HD12 @ 250 ctrs, 600mm lond embedded 150mm.
c2eae84e-cf7f-5573-8188-e05f9036bd2d | note | ○ Place SE72 mesh
f4e8f871-6d7d-53b6-a386-2d5612c2f3c7 | note | ○ Follow detail 33 at change in floor level.
22232a40-5b53-5031-ac17-40d2adb1b3b9 | note | ○ Pour 25mPa concrete
9f996c43-d9ed-5476-aec3-28a5f18fc222 | note | Acceptance Criteria - steel installed and poured in accordance with drawings.
8d82f5f5-502e-5569-8d79-4215f13f4ff7 | note | Verifying Document - Site Report
33f9463a-4f3b-5e6e-80a4-b963d1b77ebe | note | Frequency - During installation, prior to pours.
0068c42a-cd0b-5797-9f6f-913d15857ba0 | note | Inspection Type (Visual, other) - Engineers Inspection
c4c14247-943a-507e-93e2-f142ac5ebfb6 | note | Inspection: Key - H, I
822b3fbc-b64b-5a0a-a620-cdccfad0ecd9 | note | Inspection: By (Role Key) - CR/PE
| signoff | HOLD POINT
| checkpoint | 4.8 - Reinstatement - Carrigeway
0454e4f3-a6bb-5eb3-9cb1-6e32d01bc76f | note | Inspection Point: Quality Control Activity - Match existing pavement thickness or minimum of 35mm.
c0997346-9187-573d-98ed-e1c17c1580c9 | note | ○ Minimum depth of 250mm 28 day strength 20MPa concrete, R20 steel installed at 500mm ctrs, 250mm embedment and 250mm into excavation, placement of 665 steel mesh, coarse broom finish.
7c216b16-68dd-5c02-a321-088a00852a2d | note | ○ Place a tack coat.
3332c608-fba8-53cb-a423-037a4ca8317c | note | ○ Mix to be NZTA M/10: AC10
744b5eba-aa8f-510b-b0fd-80b16b6768a1 | note | ○ Bandage seal
4cdf20e6-b003-59ac-8683-ba9e7b3d1bf7 | note | Acceptance Criteria - Asphalt installed as per the design
0c1f3c53-d3b5-5ff5-978a-d5065bb3b9fc | note | Verifying Document - Photos
53de95be-dab4-537e-a393-20ce3940355b | note | Frequency - During Installation
af25c8b2-f749-5ffe-b391-8ffab5b24bc7 | note | Inspection Type (Visual, other) - Visual, Prepour inspection
3c14fdf9-2906-5c67-afe6-32783e8036b9 | note | Inspection: Key - C
e8b6dcb4-5bf8-5288-920b-6062fdbb08d8 | note | Inspection: By (Role Key) - PE/SP/QE
| checkpoint | 4.9 - Reinstatement - Footpath
e46bfda0-573f-59d7-9f54-3f76e1407163 | note | Inspection Point: Quality Control Activity - Match existing pavement thickness or minimum of 35mm.
aed541f3-beb1-514b-ac45-2eba1cc022b6 | note | ○ Minimum 75mm of basecourse.
89ebab7e-6bf4-5912-bfb3-99dec716524d | note | ○ Place a tack coat of 0.2-0.5 L/m².
42bdc910-cb80-5177-91c9-19e8efeb9c4d | note | ○ Mix to be DG7 Asphaltic Concrete.
233f666c-b13f-59a5-a883-0605d8cc8c35 | note | ○ Bandage Seal
b5f27022-def1-5231-95d0-b1b3a0745b0e | note | Acceptance Criteria - Asphalt installed as per the design
7fd12387-8500-582e-a978-7d3a98730a27 | note | Verifying Document - Photos
fa269829-0213-5669-8d90-62127574b592 | note | Frequency - During Installation
263b5951-6e65-50e3-9ee0-d7e84ddb5191 | note | Inspection Type (Visual, other) - Visual
10b1e1a7-e5f2-59cb-976e-370d244b5a26 | note | Inspection: Key - C
78fdc4df-2e7e-5266-9410-1dbef20daf8c | note | Inspection: By (Role Key) - PE/SP/QE
| checkpoint | 4.10 - Reinstatement - Kerb and Channel
d3db036a-414d-56f3-8190-bb94063c88d3 | note | Inspection Point: Quality Control Activity - Length a minimum of 1m.
7e58fa5a-faf9-5efb-808a-8e6266749f04 | note | ○ Match existing grade.
79702115-329c-5bf1-9ba0-facd94d56812 | note | ○ Concrete strength 20MPa
1cb2de81-0dec-5ae3-8eb4-769672088b54 | note | ○ Vertical joints at 3m intervals.
12625a68-117b-504a-8fc1-261376625ee4 | note | Acceptance Criteria - Tolerances for kerb and channel and paving edge beam shall be +5mm vertically and E16+3mm horizontally. The deviation from a 4m straight edge shall not exceed 3mm
49efb441-9535-5cf3-b040-30f18d30c0e1 | note | Verifying Document - Photos
0344cfad-cbc9-5e0d-96b3-ab1db9c4a5c0 | note | Inspection Type (Visual, other) - Visual, Pre Pour inspection
31e27d77-405e-575e-82cf-76c58adad59c | note | Inspection: Key - C
b8196527-75df-56e0-a1a1-b055de6ac206 | note | Inspection: By (Role Key) - PE/SP/QE
| section | SECTION 5 - FINAL INSPECTION AND HANDOVER
| checkpoint | 5.1 - CCTV
626aa881-27ba-59a2-82b1-9365e8b3f93c | note | Inspection Point: Quality Control Activity - CCTV inspection to confirm pipeline conforms with specification
56d851cd-d52e-5b44-9782-c820003a2728 | note | Acceptance Criteria - Pipeline will fail is any of the following is visible:
d62af583-43b3-5825-88a9-9e19923c3f2f | note | ○ Pipe misalignment or deformation more than 5% of the pipe diameter
9c38fdfb-3666-52f4-87a9-9724124be89f | note | ○ Dips or ponding of water inside the pipe
1575af2c-bf99-564a-b95a-643631d0d42d | note | ○ Defects such as open joints, potruding laterals, cracked barrels, or similar
b2ac9c90-0f8d-544c-9b2a-1cf6e61120b8 | note | Verifying Document - Test Records, CCTV footage
1fc07a43-648f-5765-bb1a-fbb32620c000 | note | Frequency - Every section of pipe completed
d4ffe9d1-9cc4-5358-bb32-940fc63a731f | note | Inspection Type (Visual, other) - On-Site Test
670e48e7-7035-584d-a4b7-539ce0478048 | note | Inspection: Key - H
a74729c6-6813-560c-a502-dda72f882b23 | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.2 - Leak Testing
d6681634-7294-527f-8e31-05ec4baf8649 | note | Inspection Point: Quality Control Activity - Tested in the presence of the Engineer or their representative testing in accordance with AS/NZS 2566.2 Section 6.4
3b8806c2-3ac1-5058-a26c-02271ab79ba5 | note | Acceptance Criteria - Engineer Approval
fc9740a0-2050-5c5f-9784-b07cd6cd5e42 | note | Verifying Document - Test Records
5db85558-8b9d-57d0-a926-b7bc5887cb60 | note | Frequency - Every section of pipe installed
147407a2-a6a2-5132-8b77-2855588ff1ac | note | Inspection Type (Visual, other) - On-Site Test
bc0bfb46-5276-528d-89cb-6ee202faf965 | note | Inspection: Key - H
f8fad0e0-8e0e-5707-b7a5-654fe9bc88cb | note | Inspection: By (Role Key) - SP/QE/CM/CR
| signoff | HOLD POINT
| checkpoint | 5.3 - Red pen markups
b7859528-d948-54ce-aeb9-29d8eb672c80 | note | Inspection Point: Quality Control Activity - Complete mark up of any changes from supplied drawings
bc228714-ca29-537f-9188-731a14e8f7ca | note | Frequency - After completion of pipe section
293a5856-2300-56e3-afef-d9469d25f14f | note | Inspection Type (Visual, other) -
f5f0fc6a-51b8-581e-a72d-7f77e4e2bd84 | note | Inspection: By (Role Key) - SP/QE/CM
| checkpoint | 5.4 - As built
a080f463-13fb-547e-ab99-95e877eb407a | note | Acceptance Criteria - Engineer Approval
7629ddab-d5e6-5881-8c26-f38602705d7b | note | Verifying Document - QA records
7a7d1b44-0f34-5b2c-85bb-636589345f36 | note | Frequency - at completion
179452ed-7c4b-5bca-bf88-28a26a8892d8 | note | Inspection Type (Visual, other) - Asbuilt drawings
3ff4bf4d-396e-5457-af8d-359b6a03b7fc | note | Inspection: Key - H
a7da4251-21b4-57ce-b991-01fb006cb615 | note | Inspection: By (Role Key) - PE/PM/SV
| signoff | HOLD POINT