## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | DN1210-SP2-016-002 ITP SH29 Wastewater (MH 05-MH 12) | itp |  |  |  |  | DN1210-SP2-016-002 ITP SH29 Wastewater (MH 05-MH 12) Rev 3
section | SECTION 3 - PRE-CONSTRUCTION HOLD POINTS - MATERIALS, PERSONELL & THIRD PARTY APPROVALS
checkpoint | 3.1 - Extent of Line Setout
label | Detail / Activity - Ensure line and level of Wastewater has been marked out and agreed with Engineer in accordance with Waste water drawings.
label | ○ Identify any clashes before construction.
label | ○ LOT- markup
label | Acceptance / Conformance Criteria - As Per Drawings & Markup drawing
label | Standard / Specification - Design Drawings
label | Verifying Document - ITP Sign Off / Mark-up
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction & Every Revision of IFC Drawings/Data.
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.2 - Pipe Laying
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Wastewater Construction Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.3 - Pipeline Pressure Testing
label | Detail / Activity - Method statement
label | Acceptance / Conformance Criteria - As Per Specification and IFC Drawings
label | Standard / Specification - PS- 22.3 Appendix V
label | Verifying Document - Wastewater Pipeline Pressure Testing Work Pack Sign off
label | Testing Quantity Required (based from schedule qtys) - Prior to Construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.4 - Material grading: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.8.1 - Particle Size Distribution
label | Acceptance / Conformance Criteria - No Particles >200mm
label | ○ Maximum fines 10% passing 75micron sieve
label | Standard / Specification - PS 22.13.1 Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - Lab Test Report NZS 4407.3.8.1
label | Testing Quantity Required (based from schedule qtys) - Stockpile Size (m3):
label | 0-400 - 2 tests
label | 400-1,500 - 3 tests
label | 1,500-4,000 - 4 tests
label | >4,000 - 1 test for each additional 1,000m3
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.5 - Weathering index: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.11 - The Weathering Quality Index of Coarse Aggregate
label | Acceptance / Conformance Criteria - AA, AB, AC, BA, BB, or CA
label | Standard / Specification - Appendix XVIII, PS 16.5.5 Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.6 - Crushing Resistance: Materials (GAP65/AP65)
label | Detail / Activity - NZS4407:2015, Test 3.10 - The Crushing Resistance of Coarse Aggregate Under a Specified Load
label | Acceptance / Conformance Criteria - >100KN
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 2 Tests Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.7 - Maximum Dry Density and Optimum Water Content (AP65/GAP65)
label | Detail / Activity - NZS4402:1986, Test 4.1.2 - Heavy Compaction Test
label | Acceptance / Conformance Criteria - Report Value Only
label | Standard / Specification - Appendix XVIII, Appendix V
label | Verifying Document - IANZ Accredited Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test Per Material, Per Source
label | ○ Results to Engineer 2 wks before importing
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.8 - Material grading: Materials (Sand)
label | Detail / Activity - Bedding/Side Zone/ Overlay Zone/Embedment Zone
label | Acceptance / Conformance Criteria - Sand: Sieve Size ¦¦ % Passing
label | 4.75mm ¦¦ 100% passing
label | 2.36mm ¦¦ 90-100% passing
label | 1.18mm ¦¦ 85-100% passing
label | 0.600mm ¦¦ 70-100% passing
label | 0.300mm ¦¦ 50-100% passing
label | 0.150mm ¦¦ 0-40% passing
label | 0.075mm ¦¦ 0-5% passing
label | Standard / Specification - AS/NZS 2566.2 Table G3 PS 22.4.5
label | Verifying Document - Lab Test Report NZS 4407.2015 Test3.8.1
label | Testing Quantity Required (based from schedule qtys) - 0-400m3 ¦¦ 2 Test
label | 400-1500m3 ¦¦ 3 Test
label | 1500-4000m3 ¦¦ 4 Test
label | >4000 ¦¦ 1 Test Additional 1000m3
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.9 - Pipes (PVC/PE)
label | Detail / Activity - Manufacturer's record and location of extrusion plants.
label | ○ PVC pipes must be Series 1, plain wall construction, rubber ring jointed pipe, unless shown otherwise on the Drawings.
label | ○ All PVC-U (Unplasticised) pipe must conform to the requirements of AS/NZS 1477.
label | ○ Name of the proposed PE resin, the manufacturer, production information on the properties of resin.
label | ○ Full Traceability information and certification of analysis for the resin batch.
label | Acceptance / Conformance Criteria - Full Traceability information and certification of Material
label | Standard / Specification - PS-22.4.1 (d) AS/NZS 1477
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.10 - Flanges, Fittings, Bends
label | Detail / Activity - Have a pressure rating no less than the designed pressure.
label | ○ Mechanically, chemically and electrically compatible with the class and material of the pipe.
label | ○ Current Water Services Association of Australia (WSAA) appraisal certificate or approved independent proof of fitness-for-purpose.
label | Acceptance / Conformance Criteria - Engineer approval AS/NZS 4129
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.11 - Pipe and fittings/bends
label | Detail / Activity - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm diameter, class & jointing type as shown on the drawings, and that the pipes are correct and in good condition.
label | Standard / Specification - Design Drawings
label | Verifying Document - Delivery Dockets / Inspection Checksheet (DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.12 - Fittings
label | Detail / Activity - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Acceptance / Conformance Criteria - Confirm class and type as shown on the drawings, and that the fittings are correct and in good condition.
label | Standard / Specification - PS-22.4.2
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.13 - Granular Material (Imported Sand, GAP20/AP20, GAP65/AP65)
label | Detail / Activity - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Confirm Specification and material in good condition.
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.14 - Bidim/Geogrid
label | Detail / Activity - BIDIM A29 Durogrid 30/30 or similar.
label | Acceptance / Conformance Criteria - Site Engineer Approval
label | Standard / Specification - PS-22.4.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.15 - Waste Water Manholes
label | Detail / Activity - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Acceptance / Conformance Criteria - Confirm the class and type as shown in the drawings, and fittings required for MH is same
label | Standard / Specification - Design Drawings TCC IDC DS 6.5.12.1
label | Verifying Document - Delivery Dockets / Inspection Checksheet(DG-QA-TP019)
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - PE/SE
checkpoint | 3.16 - Reinforcing steel (manhole ballast)
label | Detail / Activity - Manhole ballast reinforcing steel.
label | Acceptance / Conformance Criteria - Grade 500E, Confirm the class and type as shown in the drawings.
label | Standard / Specification - AS/NZS 4671, PS 22.6.2
label | Verifying Document - Material Certifications. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 3.17 - Horizonal Directional Drilling
label | Detail / Activity - Detailed methodology of directional drilling
label | Acceptance / Conformance Criteria - Engineer Approval
label | Standard / Specification - PS 21.6.6a
label | Verifying Document - Engineer APPROVAL
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.18 - Grouting Methodology
label | Detail / Activity - Cement grouting the sleeve annulus
label | Acceptance / Conformance Criteria - Enginner Approval
label | Standard / Specification - PS 21.6.6g
label | Verifying Document - Engineer approval
label | Testing Quantity Required (based from schedule qtys) - Prior to construction
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - ENG
checkpoint | 3.19 - Pipe and fittings. Ducts
label | Detail / Activity - Duct Pipes shall be of the 50mm
label | ○ Ducts shall be high impact uPVC
label | ○ Duct colours shall be Salmon3
label | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
label | Acceptance / Conformance Criteria - Duct Pipes shall be of the 50mm
label | ○ Ducts shall be high impact uPVC
label | ○ Duct colours shall be Salmon
label | ○ Duct colours for the different Utility Structures must be in accordance with the guidelines.
label | Standard / Specification - PS 25.13.6 b)
label | Verifying Document - Delivery Dockets/Material Certification
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - SE
checkpoint | 3.20 - Pits Covers
label | Detail / Activity - Jointing and pulling pits shall have slip resistant surfaces complying with AS/NSZ 3661-1-1993. the cover set load rating shall be in compliance with AS3996.
label | Acceptance / Conformance Criteria - Class A-10kN loading - footways and areas only accessible to pedestrian and cyslists.
label | ○ Class B - 80kN loading - footways that may be mounted by vehicle or livestock and light tractor paths. (Light duty)
label | ○ Class C - 150kN loading - grass verges or other areas open to slow moving commercial vehicles such as tractor mowers etc (medium duty)
label | ○ Class D - 120kN loading - Carriageway of roads and areas open to commercial vehicles (heavy duty)
label | Standard / Specification - PS 25.13.6 c) AS/NZS 3661-1-1993.
label | Verifying Document - Material Certifications. Delivery Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Delivery to site
label | Verification Activity: Activity - H
label | Hold Point (Internal)
label | (Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point)
label | Verification Activity: By - SE
checkpoint | 3.21 - Butt-Fusion pre construction weld test
label | Detail / Activity - One weld on the most common size of pipes used for the project.
label | ○ One weld on the thickest wall (highest PN) pipe
label | Acceptance / Conformance Criteria - ISO 13953 for tensile strength and failure mode.
label | ○ WMS Report
label | Standard / Specification - PS 22.9.6 (a) ISO 13953 Standard
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - Two test welds per operative(Welder)
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 3.22 - KWIK Spacers
label | Detail / Activity - Confirm Specification and material in good condition.
label | Acceptance / Conformance Criteria - Installation: Centred and restrained
label | Standard / Specification - Manufacturer’s Installation Guide. IFC Drawing 0312
label | Verifying Document - Photographic Evidence
label | Testing Quantity Required (based from schedule qtys) - Every spacer
label | Verification Activity: Activity - W
label | Review of text reports/records or other evidence of compliance
label | Verification Activity: By - SE
section | SECTION 4 - CONSTRUCTION - WASTEWATER PIPELINE - Excavation and Laying
checkpoint | 4.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | (Or)
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Scala/Shear test result
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals along pipelines with a minimum of 1 test between each pit/manhole.
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 4.2 - Undercut approval
label | Detail / Activity - Trench Foundation
label | Acceptance / Conformance Criteria - 300mm Max cut
label | ○ IFC Drawing Sheet 320
label | (Or)
label | ○ Engineers approval
label | Standard / Specification - IFC Drawing WST 0320. AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
checkpoint | 4.3 - Undercut Backfill Compliance (PAP5)
label | Detail / Activity - On Granular Material / On each layer as per specification / on the trench foundation.
label | Acceptance / Conformance Criteria - Visiual Inspection
label | Standard / Specification - IFC Drawing WST 0320
label | Verifying Document - Lab Test Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Undercut
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
checkpoint | 4.4 - Bedding Zone Compaction Testing
label | Detail / Activity - On Granular Material / On each layer as per specification (Imported Sand/GAP20/19mm chip)
label | Acceptance / Conformance Criteria - Bedding Zone: 100mm minimum thickness (compacted) over the bottom of the trench.
label | ○ Minimum Compaction - 85%MDD
label | ○ Paeangaroa Sand: clegg of ave 9 CIV and min of 7 CIV.
label | ○ Wilson Sand No.2: clegg 4 CIV
label | Standard / Specification - IFC Drawing 0320-1 AS/NZS 2566.2/2002
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - As per SW Specification.
label | ○ One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.5 - Laying of Pipes
label | Detail / Activity - Lay in straight lines, beginning at the lower end of the line.
label | ○ Lay all pipe with manufacturing codes and class markings facing upwards.
label | Acceptance / Conformance Criteria - As Per Drawings.
label | ○ Facing upwards
label | Standard / Specification - PS22.7.1 C
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 4.6 - Pipe Installation on Curved Alignments
label | Detail / Activity - All Industry Guideline PVC, PP AND PE PIPE INSTALLATION ON CURVED ALIGNMENTS (POP202)
label | Acceptance / Conformance Criteria - AS Per POP 202
label | Standard / Specification - PS 22.7.1 D
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - M
label | Monitor on Random Basis
label | Verification Activity: By - SE
section | SECTION 5 - CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE (Joint and Connection)
checkpoint | 5.1 - Flanges
label | Detail / Activity - Manufacturer specifies their own bolt tightening torque and sequence, it should override the project specification.
label | Acceptance / Conformance Criteria - Flanges to AS/NZS 4087
label | Standard / Specification - PS 22.7.5
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - First flanged joint
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 5.2 - Bends
label | Detail / Activity - PE 100 butt fusion welded segmented bends only where specifically indicated on the Drawings.
label | ○ Fitting must meets the same PN rating as the adjacent PE 100.
label | ○ Fittings must be suitable for producing the joints shown on the Drawings.
label | Acceptance / Conformance Criteria - PIPA POP 006 and AS/NZS 4129
label | Standard / Specification - PS 22.4.2
label | Verifying Document - Visual Inspection
label | Testing Quantity Required (based from schedule qtys) - As per the IFC drawing
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 6 - CONSTRUCTION ACTIVITY - WASTEWATER PIPELINE INSTALLATION - Directional Drilling
checkpoint | 6.1 - Check levels while drilling
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | ○ Horizontal design Setout: +/-30mm variance
label | Standard / Specification - PS- 21.7.6 Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.2 - Drilling Fluid Mix
label | Detail / Activity - Viscosity record
label | Acceptance / Conformance Criteria - Viscosity record
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Viscosity record
label | Testing Quantity Required (based from schedule qtys) - Every shot
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.3 - Correct Reamer used
label | Detail / Activity - Reamer size to confirm on site
label | Acceptance / Conformance Criteria - Reamer size to confirm on site
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Visual Inspection/Photo
label | Testing Quantity Required (based from schedule qtys) - 1 per drill shot
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.4 - Pipe Damage
label | Detail / Activity - Damage <10% of wall thickness
label | Acceptance / Conformance Criteria - Damage <10% of wall thickness
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Each pipe
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.5 - Tracer Wire
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 6.6 - Drill Report
label | Detail / Activity - Drill report to be submitted
label | Acceptance / Conformance Criteria - Drill report to be submitted
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Report
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.7 - Settlement monitoring and ground deformation (Baseline measurements)
label | Detail / Activity - Topo survey completed before and after drill shot
label | Acceptance / Conformance Criteria - Topo survey completed before and after drill shot
label | Standard / Specification - PS 21.6.6
label | Verifying Document - Survey data
label | Testing Quantity Required (based from schedule qtys) - Every 6m
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 6.8 - Cement Grout - Annulus
label | Detail / Activity - The sleeve annulus are to be cement grouted after installation to prevent settlement.
label | Acceptance / Conformance Criteria - The grouting mix is to be:
label | 1. 1:1 Sand/cement ratio 1 : 1
label | 2. Water/Cement ratio 1 : 0.67 by weight
label | Standard / Specification - PS 22.5.8b
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Every Grout
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 7 - CONSTRUCTION - WASTEWATER PIPELINE - Inspection
checkpoint | 7.1 - Pipe Inspection
label | Detail / Activity - Inspection of Drainage line
label | Acceptance / Conformance Criteria - Inspect pipes prior to backfilling to ensure they have been installed correctly and the joints are in place. Check for gaps and/or defects and check pipe alignment for straightness
label | Standard / Specification - Internal
label | Verifying Document - Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Continious 1 per Line
label | Verification Activity: Activity - I
label | Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
section | SECTION 8 - CONSTRUCTION - WASTEWATER PIPELINE - Backfill
checkpoint | 8.1 - Emebment Zone - (Side Haunch Overlay)
label | Detail / Activity - Granular sand backfill compacted in 200mm Layers.
label | ○ NDM/Clegg Testing to be completed on maximum 200mm lifts of overlays .
label | ○ NDM BS to be Carried Out
label | Acceptance / Conformance Criteria - in 200mm layers.
label | ○ More than 85% of MDD.
label | Standard / Specification - IFC Drawing 0320-1
label | Verifying Document - Lab Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - One test per 20m evenly spaced intervals.
label | ○ 200mm lift
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 8.2 - Pipe Markers
label | Detail / Activity - Lay a conductive signal strip or tracer wire along the full length of all non-metallic pressure pipelines as shown on the Drawings.
label | ○ Mark fire hydrant positions in accordance with SNZ PAS 4509
label | Acceptance / Conformance Criteria - AS Per Drawings.
label | Standard / Specification - PS 22.7.3 a
label | Verifying Document - Visual Inspection / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - Every Line
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 8.3 - Backfill Compaction Testing
label | Detail / Activity - Backfill Compacted in 200mm Layers.
label | ○ NDM Testing to be completed on maximum 200mm lifts of backfill.
label | Acceptance / Conformance Criteria - GAP65/AP65 or site won material Backfill Compacted in 200mm layers.
label | ○ Testing to be completed on maximum 200mm lifts of backfill.
label | ○ 95% NDM on Shared and Carriageway.
label | OR
label | ○ 25% CIV
label | ○ For site won: Shear Vane min 125kPa
label | Standard / Specification - PS- 22.13.5 NDM Standard 25832 NZS 4402 Test 4.1.3, IFC Drawing 0320-1, PS - 16.5.5
label | Verifying Document - Lab Report / Wastewater line record
label | Testing Quantity Required (based from schedule qtys) - As per WW Specification.
label | ○ One test per 20m evenly spaced intervals.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 9 - CONSTRUCTION - WASTEWATER PIPELINE TESTING
checkpoint | 9.1 - Pressure Acceptance Testing (air)
label | Detail / Activity - Backfill/cover with embedment before testing
label | ○ End caps in place, provision for filling the pipeline and bleeding air.
label | Acceptance / Conformance Criteria - Wastewater Rising Main Pipelines – 800kPa
label | ○ Ensure the STP is not more than 25% above the rated pressure of any pipeline component.
label | Standard / Specification - PS 22.7.12(d), PS 22.7.13(b), PS 22.7.15
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline, All valves
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.2 - Constant Pressure Testing (water)
label | Detail / Activity - Backfill/cover with embedment before testing, plan for where water will be diverted or sent to
label | Acceptance / Conformance Criteria - There is no failure of any pipe, fitting or other pipeline component.
label | ○ There is no visible leakage at pipe joints or other fittings.
label | ○ The make-up water volume does not exceed the maximum allowable quantity as calculated. Q ≤ (0.14 x L x D x H).
label | Standard / Specification - PS 22.7.15
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 9.3 - Pressure Rebound Test
label | Detail / Activity - Backfill/cover with embedment before testing, plan for where water will be diverted or sent to
label | Acceptance / Conformance Criteria - There is no failure of any pipe, fitting, or other pipeline component, and
label | ○ There is no visible leakage at any joint or fitting.
label | ○ The volume of water bled off (ΔV) is less than the calculated ΔV(max allowable air), and
label | ○ The pressure has not dropped below the rebound peak within 30 minutes, or
label | ○ The test has been extended to 90 minutes and the pressure has not dropped more than 20 kPa below the rebound peak value after 60 minutes.
label | Standard / Specification - PS 22.7.16 TCC IDC IT-6
label | Verifying Document - Test Report, Pressure Log in.csv or .xlsx format
label | Testing Quantity Required (based from schedule qtys) - All Pipeline
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
section | SECTION 10 - CONSTRUCTION - WASTEWATER Manhole installation
checkpoint | 10.1 - Foundation Compliance
label | Detail / Activity - On Granular or Cohesive Material
label | Acceptance / Conformance Criteria - Granular Material: Scala 3 blows/100mm
label | ○ Cohesive Material: Vane Shear Strength min50kpa, ave>60kpa
label | Standard / Specification - Appendix V Table 21:11
label | Verifying Document - Shear vane or Scala test result
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.2 - Undercut approval
label | Detail / Activity - On Subgrade
label | Acceptance / Conformance Criteria - Subgrade CBR between 3.5% <5%: Undercut 150mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between 2% <3.5%: Undercut 300mm and Replace with Compacted AP65 or Approved Granular material.
label | ○ Subgrade CBR between <2%: Engineer to advise or Undercut 450mm and Replace with Compacted AP65 or Approved Granular material.
label | Standard / Specification - PS 21.6.5 Table 21.5
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - If Undercut required
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.3 - Undercut Backfill Compliance AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - Appendix XVIII
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test per Undercut
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.4 - Bedding Compaction Testing AP65
label | Detail / Activity - On Granular Material
label | Acceptance / Conformance Criteria - Average 95% MDD, min >92%
label | OR
label | ○ Clegg 25% CIV
label | Standard / Specification - Appendix XVIII PS- 21.6.11
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.5 - Survey
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Horizontal Alignment: The permissible deviation of the horizontal alignment between manholes or structures shall be ± 30mm.
label | Standard / Specification - PS- 21.7.6
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 10.6 - Sidefill Compaction Testing
label | Detail / Activity - From the bedding layer to the overlay layer of pipe.
label | Acceptance / Conformance Criteria - AP20/GAP20
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 85% MDD
label | ○ AP20/19mm chip
label | Standard / Specification - PS- Table 21.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.7 - Backfill Compaction Testing
label | Detail / Activity - From Overlay layer to the subgrade layer
label | Acceptance / Conformance Criteria - AP65
label | ○ Testing to be completed on maximum 200mm lifts of backfill - 92% (Average 95%) of MDD on metal.
label | ○ AP65-Clegg 28%CIV
label | Standard / Specification - PS- 16.5.12
label | Verifying Document - Lab Test Report
label | Testing Quantity Required (based from schedule qtys) - 4 Density test per layer at Quarter Points around the Structure.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE/ENG
checkpoint | 10.8 - Man Hole joints inspection
label | Detail / Activity - Inspection of joints
label | Acceptance / Conformance Criteria - Right joint type used, no visual leak or breakage
label | Standard / Specification - PS 22.7.10
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.9 - Inspection
label | Detail / Activity - Inspection of Structure
label | Acceptance / Conformance Criteria - Inspection of Structure prior to backfilling to ensure correct installation and that the joints are sealed. No damages caused to the Structure.
label | Standard / Specification - PS- 21.6.11
label | Verifying Document - Manhole/Catchpit Record
label | Testing Quantity Required (based from schedule qtys) - 1 Checksheet per manhole/catchpit
label | Verification Activity: Activity - I
label | Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SE
checkpoint | 10.10 - Plumb
label | Detail / Activity - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Acceptance / Conformance Criteria - The maximum permitted installed out of plumb is 25 mm of horizontal deviation in 1 m of vertical rise.
label | Standard / Specification - PS-22.7.10
label | Verifying Document - Survey Data
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SV
checkpoint | 10.11 - Step Rungs
label | Detail / Activity - Step rungs evenly spaced at nominal 300mm vertical intervals
label | Acceptance / Conformance Criteria - Lowest rung more than 450mm above floor highest rung not more than 600mm below the top surface of MH cover
label | Standard / Specification - PS-22.7.11
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.12 - Manhole frame and covers
label | Detail / Activity - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
label | Acceptance / Conformance Criteria - Make up the height between the manhole roof slab or precast lid and the finished surface level using concrete riser rings. Set the manhole frame and cover in concrete so it finishes flush with the finished ground or roadway level. Finish the concrete in a way that allows the final surface to be brought close to the cover frame.
label | Standard / Specification - PS-22.7.12
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - 1 Test/Manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.13 - Manhole lateral connection
label | Detail / Activity - DN150 PVCu connection for future lateral.
label | ○ 800mm above manhole outlet invert
label | ○ DN150PVCu end cap.
label | Acceptance / Conformance Criteria - DN150 PVCu connection for future lateral.
label | ○ 800mm above manhole outlet invert
label | ○ DN150PVCu end cap.
label | Standard / Specification - IFC Drawing 0320-Rev 03 TCC IDC DS6.5.12.4b
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Per connection
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.14 - Concrete Formwork - surveyor to check
label | Detail / Activity - Equivalent to check the position of the formwork
label | Acceptance / Conformance Criteria - +\- 100mm of design
label | Standard / Specification - Project Specifications 27.4.5 (b) NZS 3109:1997
label | Verifying Document - Pre-pour Check Sheet
label | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
label | ○ 1 set = 5 tests
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.15 - Concrete Formwork - surveyor to check
label | Detail / Activity - Equivalent to check finished height of framework
label | Acceptance / Conformance Criteria - +\- 10mm of design
label | Standard / Specification - Project Specifications 27.4.5 (b) NZS 3109:1998
label | Verifying Document - Pre-pour Check Sheet
label | Testing Quantity Required (based from schedule qtys) - 1 Set Every 20m Centres
label | ○ 1 set = 5 tests
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 10.16 - Pre-pour inspection
label | Detail / Activity - Pre-pour inspection of manhole before ballast
label | Acceptance / Conformance Criteria - Stable form work, ready for pour
label | Standard / Specification - Design drawing
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Pre each manhole ballasts installation
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SUP/ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 10.17 - Manhole Ballast WWMH06 to WWMH10 (concrete & reinforcing steel)
label | Detail / Activity - Additional manhole ballast.
label | Acceptance / Conformance Criteria - All Concrete to be 25MPa at 28 days.
label | ○ Minimum cover to steel = 50mm.
label | ○ Reinforcing steel to be grade 500E and to comply with AS/NZS 4671.
label | Standard / Specification - IFC Drawing Sheet WST 0321 NZS 3109 5.6.3(B). AS/NZS 4671 PS 22.6.2 PS Table 22.4 specific manhole requirements
label | Verifying Document - Visual inspection
label | Testing Quantity Required (based from schedule qtys) - Per manhole
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
section | SECTION 11 - CONSTRUCTION ACTIVITY - COMMUNICATION DUCT INSTALLATION
checkpoint | 11.1 - Bedding
label | Detail / Activity - In wastewater trench ensuring 50mm of beeding over wastewater pipe
label | Acceptance / Conformance Criteria - Clean Imported Sand or SAP 7 to be placed 50mm minimum thickness (compacted) over the bottom of the trench.
label | Standard / Specification - PS 25.13.2 g)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
checkpoint | 11.2 - Installation of Ducts
label | Detail / Activity - Layed in same trench as wastewater with sand cover.
label | Acceptance / Conformance Criteria - Must have 50 mm bedding material
label | Standard / Specification - PS 25.13.7 b) iii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
checkpoint | 11.3 - Draw Wires
label | Detail / Activity - A draw wire shall be intalled in all ducts and within all sub-ducts to facilitate the hauling-in of cable after the completion of the ducting.
label | Acceptance / Conformance Criteria - Pigmented, stranded polypropylene or equivalent rot-proof material draw wire of 5kN breaking load.
label | ○ ≥20 years design life.
label | ○ The ends of draw wires shall be made fast within the pits and be secured to the duct plugs.
label | ○ Blue colour wire
label | Standard / Specification - PS 25.13.7 e) ii to iv
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
checkpoint | 11.4 - Caps
label | Detail / Activity - All duct ends shall be capped
label | Acceptance / Conformance Criteria - Capped ducts
label | Standard / Specification - PS 25.13.7 e) v
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
checkpoint | 11.5 - Warning Tape
label | Detail / Activity - Warning tape to be placed above services.
label | Acceptance / Conformance Criteria - Warning Tape to be placed no more than 300mm above the topmost duct
label | Standard / Specification - PS 25.13.7 b) iii & f)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
checkpoint | 11.6 - Overlay
label | Detail / Activity - 150 mm minimum sand placed on top of duct.
label | ○ No mechanical compaction will caarry out till 300mm drom top of duct.
label | Acceptance / Conformance Criteria - 100 mm minimum sand placed on top of duct.
label | Standard / Specification - PS 25.13.7 b) ii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Cable
label | Verification Activity: Activity - M
section | SECTION 12 - CONSTRUCTION ACTIVITY - COMMUNICATION PIT INSTALLATION
checkpoint | 12.1 - Pit Installation Location
label | Detail / Activity - Locations shall be avoided where running water can flow over the lid or where mud and debris can fall or be washed onto the lid . Confirm on site with engineer,
label | Acceptance / Conformance Criteria - Pit lid and concrete apron shall be flush with ground level in grass, concrete or asphalt areas.
label | ○ When pit is located on a slope of 10 to 30 degrees, the lid shall be flush with ground on the upper side.
label | ○ When slope is greater than 30 degrees, the lid shall be up to 100mm above the ground level on the upper side.
label | Standard / Specification - PS 25.13.8 a) i and ii
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 12.2 - Pit Installation Bedding
label | Detail / Activity - Bedding with 150mm compacted GAP20 hard-fill coverd with 20mm compacted sand. Pits shall be carefully lifted into place and lined up with the ducts to penetrate the chamber.
label | Acceptance / Conformance Criteria - 150mm compacted GAP20 hard-fill covered with 20mm of compacted sand
label | Standard / Specification - PS 25.13.8 d)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.3 - Pit Installation Sidefill concrete
label | Detail / Activity - Plactic pits shall be cast into the ground with 150mm concrete surround
label | Acceptance / Conformance Criteria - Plactic pits shall be cast into the ground with 150mm concrete surround
label | Standard / Specification - PS 25.13.8 d)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.4 - Pit Installation Backfilling
label | Detail / Activity - Backfill and compact the ground around concrete pits. Extra care to be taken to avoid damaging the ducts in 200mm layers of GAP 65.
label | Acceptance / Conformance Criteria - Min 92% compaction rate and Average of 95%.
label | Standard / Specification - PS 25.13.10 a) modified
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.5 - Pit Installation Concrete
label | Detail / Activity - Top 300mm of pit shall be concreted around with a width of 150mm with a 20MpA concrete.
label | Acceptance / Conformance Criteria - 20 mPa
label | Standard / Specification - PS 25.13.8 d) iv.
label | Verifying Document - Concrete Dockets
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 12.6 - Pit Installation Clean up
label | Detail / Activity - Clean out all pit after completion of the work
label | Acceptance / Conformance Criteria - Pit are free of dirty, mud,water and foreign materials
label | Standard / Specification - PS 25.13.8 e)
label | Verifying Document - Checklist
label | Testing Quantity Required (based from schedule qtys) - Each Pit Location
label | Verification Activity: Activity - M
label | Verification Activity: By - SE
checkpoint | 12.7 - Survey As Built
label | Detail / Activity - As Built every ducts joint before backfill
label | Acceptance / Conformance Criteria - Completed as per drawings
label | Standard / Specification - Standard Practise
label | Verifying Document - Survey
label | Testing Quantity Required (based from schedule qtys) - On going
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - PE
section | SECTION 13 - CONSTRUCTION ACTIVITY - WATERMAIN PIPELINE - Butt-Fusion Welding
checkpoint | 13.1 - Butt-Fusion Construction weld test
label | Detail / Activity - Test at least two welds from the first 50 welds.
label | ○ One of the welds to be selected by the Engineer for satisfactory result.
label | Acceptance / Conformance Criteria - Tensile testing and ductility of welds.
label | ○ 95% tensile strength; welds aligned
label | Standard / Specification - PS- 22.9.6 (a) (iv)
label | Verifying Document - Test report
label | Testing Quantity Required (based from schedule qtys) - Two welds for the first 50 welds
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 13.2 - Butt-Fusion Welding
label | Detail / Activity - Use only semi-automatic or automatic welding machines.
label | ○ Maintain a site record for all butt-fusion welds.
label | ○ The lead welder or supervisor must verify on the site record form that all welds have been made in accordance with the WMS and that the information on the record form is correct.
label | Acceptance / Conformance Criteria - Site Butt Fusion Welding record to be filled out. (Refer to CWP)
label | ○ WMS Report
label | Standard / Specification - Appendix XXII PS 22.9.4 C
label | Verifying Document - Visual Inspection / Butt Fusion welding records checklist.
label | ○ WMS Report
label | Testing Quantity Required (based from schedule qtys) - Every Welding Point
label | Verification Activity: Activity - HP
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - ENG
holdpoint | AUTHORITY HOLDPOINT
checkpoint | 13.3 - Survey
label | Detail / Activity - Inspection of Pipeline Inverts
label | Acceptance / Conformance Criteria - Vertical design Setout:
label | ○ Pipes ≤ 1% grade: +/- 10mm variance
label | ○ Pipes > 1% grade: +/- 20mm variance
label | ○ Horizontal design Setout: +/-30mm variance
label | Standard / Specification - PS- 21.7.6 Table 21.15
label | Verifying Document - Survey Data / As-built record
label | Testing Quantity Required (based from schedule qtys) - Pipeline invert to be surveyed at chainages as indicated in the drawings.
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | 13.4 - Photograph of Each Weld
label | Detail / Activity - Take sharply focused photo while clamped
label | Acceptance / Conformance Criteria - Unique weld identifier visible
label | Standard / Specification - N/A
label | Verifying Document - Weld Records; Photos
label | Testing Quantity Required (based from schedule qtys) - Each weld
label | Verification Activity: Activity - I
label | Formal inspection activity to be undertaken and recorded.
label | Verification Activity: By - SUB
section | SECTION 14 - POST CONSTRUCTION (FINAL INSPECTION AND HANDOVER)
checkpoint | 14.1 - Survey As-Builts
label | Detail / Activity - Quality check on the pipeline and structure based on the tolerances in RITS.
label | Acceptance / Conformance Criteria - Meets spec as per drawings and capture any NCR or change to design.
label | Standard / Specification - Project Specifications
label | Verifying Document - Red pen markup only
label | Testing Quantity Required (based from schedule qtys) - Post works completion of a lot
label | Verification Activity: Activity - H
label | Work Shall not proceed past the Hold Point until released by the organisation imposing the Hold Point.
label | Verification Activity: By - SE
checkpoint | Client Final Inspection - the signature below verifies that this ITP has been completed in accordance with the Specifications and verifies lot compliance.
textbox | Contractor's Rep Name:
textbox | Engineer's Rep. Name:
date | Date:
signoff | Add Signature