## zres_siteapp_NEW
Id | Type | Name | Values | Prompting Name | Postfix | Resource Id
cf939dde-910e-4a0b-ac53-327fe503dc0f | checklist | FH-ZU2-QU-ITP032 - ALER 3 Structure - Rev 2 | itp | ITP032 - ALER 3 Structure
da604e6a-18b4-4d23-94f9-4b8dcf8224cd | section | 1.0 - Preliminary Activities – Permits, Documentation, Approvals, Survey Documentation
32d8866e-7749-4e1d-89d0-66e34655ad9e | checkpoint | 1.1 - Check for correct documentation
7c355e4a-89dc-520e-a43f-08001b6b2173 | note | Frequency - Prior to commencing activity
226226d9-c476-5a9f-a54d-036cf3879dbd | note | Acceptance Criteria - Ensure that all employees and subcontractors are:
f1194ebb-9b3a-5e1f-9aa1-a2ce831b5d9c | note | — using the correct and complete set of drawings.
241c0746-9044-515e-b217-ad4284f39b98 | note | — all drawings are the latest revision.
cc5283df-8c06-5f0c-be3d-173327422ad1 | note | Reference Documents - Drawings / Aconex Register
a0b6ac93-dc6a-5e5c-97fd-14ab51ae7991 | note | Inspection/Test Method - Verify
a523b193-600f-5605-94e0-8f504a60351e | note | Record of conformity - Drawings and drawing registers
9f41f4e8-e111-537f-82f9-a7b99383577f | note | HP*
a6d9c328-332e-5ef2-b13c-0c05d922058a | note | Responsibility - Project Engineer
1c26cc8e-222b-53b6-bb78-e4aa7e606ff7 | date | Date Completed:
30b0b7bc-eaef-49b4-ba30-673093e0b43d | checkpoint | 1.2 - Implementation of all measures and controls
cd7cdcb8-b153-5351-a751-afcc6a34c032 | note | Frequency - Prior to commencing activity
04bbc392-7146-5c4b-a166-0700d45458ef | note | Acceptance Criteria - All necessary measures and controls being implemented, that is PSP, EMP, TMP, SWMS & WP.
5475cb4a-8a99-548b-b38e-301bb2b889a6 | note | Reference Documents - PSP, EMP, TMP, JSEA, SWMS, WP
72d5622e-5e21-55e8-bcc0-c9c5ad8e1187 | note | Inspection/Test Method - Visual inspection
2b72bec2-e6f1-54c1-b667-2cad7515e9f1 | note | Record of conformity - This ITP signed
852c6373-e797-5656-817d-794beaa8a3b6 | note | HP*
d42fddbf-02ee-5442-8d04-509edeac8a9b | note | Responsibility - Project Engineer
10963abb-96e7-5793-8c8d-32bc8b6fe11b | date | Date Completed:
ce64c3be-05f6-4a78-b60d-e71ece2dea75 | checkpoint | 1.3 - Survey Checks
79b8941a-8ecb-5a56-bb43-cdb8663f8579 | note | Frequency - Prior to commencing activity
063912c3-420d-511d-be48-fa3ac6b92399 | note | Acceptance Criteria - Check survey to be completed of all footing positions prior to placing any of the panels.
43b8397e-2021-529c-b8d8-d2757244feb6 | note | Reference Documents - Drawings
6739b750-4d6b-524c-8132-217bdbc275e4 | note | Inspection/Test Method - Verify
60e4a22f-1036-5e9f-aa9f-27b197708b7b | note | Record of conformity - This ITP signed Survey Report
e14dd37c-08f9-5791-8f8c-1697028ba024 | note | HP*
29483447-99ee-5a46-9333-19c6a18c9ca7 | note | Responsibility - Project Engineer / Surveyor
1d51861c-9982-592c-8933-f7cb12c49447 | date | Date Completed:
24800a53-e827-4828-be45-97bb77ca46d9 | checkpoint | 1.4 - Submission & approval of precast shop drawings
1099d67e-75cc-56a4-897c-474142b1cfa5 | note | Frequency - Prior to commencing activity
51b16bf3-3dcf-5346-9999-a3523156c5d5 | note | Acceptance Criteria - HOLD POINT
e4b657ec-d212-5f90-8703-2bdba2ce5cca | note | ○ Submit precast wall panel shop drawings to the principal’s representative for approval prior to fabrication commencement.
488e07f0-832f-564d-b12b-c9d567a8aac3 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 cl 1.16, Drawing 20003 note PC7
598a21b7-987d-53d4-a0cd-b4224855bbdd | note | Inspection/Test Method - Verify
435496ad-a461-5f41-b73c-7de163e1fcc2 | note | Record of conformity - Aconex Reference
c4966e54-a425-5ff7-b042-9bbcae45b2c8 | note | HP
3831aeb3-5339-5897-be20-7731ea9d7418 | note | Responsibility - Project Engineer / Principals Representative
86f84417-e754-5004-b360-78ff8e22e794 | date | Date Completed:
dc48684c-ccab-4b6f-ab85-f1280fc321a7 | signoff | AUTHORITY HOLDPOINT
f96dbc9e-cd2f-4e0e-a2a6-02fceb22e6db | checkpoint | 1.5 - Submission & approval of structural steel shop drawings
f6fb871f-a953-51d0-8a87-1186f539afbb | note | Frequency - Prior to commencing activity
257adc40-a845-598b-adf6-e9daf6d75f7e | note | Acceptance Criteria - HOLD POINT
e41b78b6-7e38-5fac-860b-6a3b6e964a94 | note | ○ Submit structural steel shop drawings to the principal’s representative for approval prior to fabrication commencement.
bd93fe76-2ed9-5f72-bba8-e646850bcf38 | note | Reference Documents - Drawings 20002, 20020, 20113, 20221
a705612b-c7b4-57ff-882b-b2c170c71fb1 | note | Inspection/Test Method - Verify
9b3dac7c-f305-5265-8a82-6c258c32216d | note | Record of conformity - Aconex Reference
b5f1f732-1266-5ae6-9817-18760aedb93c | note | HP
52f45dab-dd4f-550a-9e83-23f0d4934087 | note | Responsibility - Project Engineer / Principals Representative
e2099029-3497-57ef-b6b1-adbadebf5095 | date | Date Completed:
530d7935-2978-4a39-a96e-4217c508b8d0 | signoff | AUTHORITY HOLDPOINT
788ff20b-1e3b-46cf-98a3-e14152c66de0 | checkpoint | 1.6 - Material Submissions
35b585c9-bf8d-53c0-81e8-fda2d5c98725 | note | Frequency - Prior to commencing activity
086ecbb1-0fab-5714-92e5-acc13e2bbc80 | note | Acceptance Criteria - HOLD POINT
867ec0eb-ab90-5604-8fe2-ea16ae548ed2 | note | ○ Items to include but not limited to:
906cda9a-94f5-553b-8aff-b109eed0af37 | note | — Concrete Mix Design
aa6c69b4-5499-5392-ba82-22fa0d491e75 | note | — Element Casting Checklist
e0e4d6dc-549b-5330-82e7-f87fc7cb8df3 | note | — Steel Reinforcement
259b6b05-cebd-5cb8-a097-4187b0ec5a9c | note | — Precast Sample
a2bcde34-d23d-532d-8430-18690f2ca7fa | note | — Bolts
a776a9a4-6830-5301-9650-2d07513a0bc2 | note | — Ferrules
8d19cdcb-b09f-5cda-b251-c50d846576ed | note | — Grout
322bd507-9486-56c4-bccf-7337d24e2405 | note | — Incompressible filler
e22fb135-6e1d-5117-a2a3-c619b6905108 | note | Reference Documents - ZULU-BECA-001-SPC-00005 cl 1.16, Structural Drawing Set 030-20 AS/NZS 1252.2
e34f2487-830b-5aae-b26d-e67cb38ba137 | note | Inspection/Test Method - Verify
d5528ca4-e2bd-564f-a0e1-f28f6cc3568f | note | Record of conformity - Aconex Reference
e30195f5-3035-5c66-9350-c313162bb8b7 | note | HP
1ec700a3-d59c-5616-986b-e799e878334e | note | Responsibility - Project Engineer / Principals Representative
9ca5c81f-954b-58b8-bf66-922d521a7f14 | date | Date Completed:
f9ad00e1-14c8-4b08-b595-39fd98488f6e | signoff | AUTHORITY HOLDPOINT
ef056269-1a2c-43eb-bf4d-beb5fe31389d | checkpoint | 1.7 - Welding Certification
2e2bfb11-1c82-54b3-9114-2b71ac73b4bd | note | Frequency - Prior to commencing activity
2cdf28bc-2cb9-56b1-8b7a-c04e40d5abfd | note | Acceptance Criteria - Submission & approval of the following:
e5b947af-076a-50e1-81b6-9f5da6456a71 | note | — Welding Procedure Qualification
fc699360-6cd7-5853-9149-84589601c35a | note | — Welding Procedure Specification
1c5fee45-db6b-5702-96fa-b0218bcc062e | note | — Welder Qualification
02c01339-39f9-53b1-9dce-748817967364 | note | — Approved Consumables
54ce3c0a-acd6-5794-8d1b-d140da58d0d9 | note | Reference Documents - AS1554.1
917d3271-b973-5cb8-835e-1b407aa9beec | note | Inspection/Test Method - Verify
00362234-2867-5172-93be-8f5ed3506f19 | note | Record of conformity - This ITP Signed, Qualification Documents
450d96f9-b7e1-5550-9bb7-31b000134679 | note | HP*
afa44590-6ab1-53ee-a5dd-ebe80303308b | note | Responsibility - Project Engineer
21ace4fa-bff4-5bca-8c5a-f9bdcf4bcc55 | date | Date Completed:
9fcfdce8-5abb-44c8-a7a5-106e03abc599 | checkpoint | 1.8 - Temporary Works – Pre- Cast Concrete Panels
99a0a409-7857-5eea-9fb4-a28942a99261 | note | Frequency - Prior to commencing activity
9ab425d5-6c45-5f5c-8292-a382c3a6fa2f | note | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
d265c5b2-eefb-52c9-8006-1555eb83a9db | note | — Certification of Lifting Points
444a2aed-b1b8-588e-98ab-8bb0bd04e74e | note | — Propping plan
c0802cb0-adcc-53e0-8c8c-54b1cf54710f | note | — Erection sequence
db023486-1536-5299-bc07-e50d5691ae70 | note | — Lift Plan
d19ccbca-21f3-53bb-bd71-49209d9a2f0f | note | — Certification of Ground Platform for lift
c38b7ede-26b0-587e-91e6-5a40d193ec40 | note | — Lifting inserts
d32e6ce6-08c3-5126-8de1-8e4ec70adee0 | note | Reference Documents - Structural Drawing Set 030-20
a9f2fad5-a9ce-58e3-b671-dbcf43b09a6f | note | Inspection/Test Method - Verify
85f9d944-cab0-5169-b7d5-00fdafd9083e | note | Record of conformity - Certification of lifting points, propping plan, erection sequence, lift study, Geo Report
bba6696c-55a3-50a5-aceb-3151fab3690f | note | HP*
f30cabe5-fc09-5f56-aa9a-4009031e28f7 | note | Responsibility - Project Engineer
1fc22e52-598a-5f2c-98b5-f7ebd965243c | date | Date Completed:
e4ea0eaa-1f71-4d80-80b5-1b8ef4d262aa | checkpoint | 1.9 - Temporary Works – Structural Steel Roof
718bd0c7-893d-5600-9d3c-72a9188d65a7 | note | Frequency - Prior to commencing activity
64ef3b56-9af8-5ebe-a7c3-5ca6a3812501 | note | Acceptance Criteria - Submission and approval of the following documentation by the FH Temp Works Coordinator (not limited to):
18b2b294-68da-5ee4-b100-e47dfdbe097b | note | — Certification of Lifting Points
422f7a32-25fa-5df1-8693-b6d259f0f6f0 | note | — Installation sequence
dc90a506-3d95-5871-b9b2-3a9a9e67ba01 | note | — Lift Plan
f9dd3169-3ae7-510a-9f8a-0af699b02d4b | note | — Lifting Point calculation
126cc9bb-c43c-5a11-8ebe-b51327abb87e | note | — Certification of Ground Platform for lift
7fc570ad-e1d1-5a26-ab63-d8eafa17b957 | note | Reference Documents - Structural Drawing Set 030-20
96295fe3-231f-5eb6-948b-6b3e1759860d | note | Inspection/Test Method - Verify
4fb41381-69f2-507b-a3bf-e1e2b4cef5ef | note | Record of conformity - Certification of lifting points, erection sequence, lift study, Geo Report
c9f9f112-4186-5900-a305-f8247d1e0298 | note | HP*
a59a740e-7e80-5331-8eee-4bd2aadc3a5c | note | Responsibility - Project Engineer
6d9fb1d1-d7b9-54ab-be28-9017f7ad025d | date | Date Completed:
fbaa66f9-418c-4d89-9a7a-4ab31f0ec917 | section | 2.0 - Construction - Precast Concrete Panel
249afd3a-0ed4-492d-a2ea-4655a16c9c32 | checkpoint | 2.1 - Fabrication Inspections
da94efe2-caf6-5001-8ea4-db8bf40b5c79 | note | Frequency - Each Lot
81f3cee7-4515-5e20-a227-a58f7082f54e | note | Acceptance Criteria - Inspection of the following prior to casting:
8f915a59-384f-5b28-a856-a2e59c0779ed | note | — Formwork dimensions & stability
6933cbb6-2fc8-57dc-9d67-2d011fc6e1a5 | note | — Edge details and penetrations
6805f212-a9f4-5635-9338-f75289752c98 | note | — Connection materials and inserts in place
8d00b931-840e-5f16-8ba0-aef00d113c18 | note | — Reinforcement
751c0798-489d-55dd-b4ac-403bfacabf0b | note | — Concreting
a947bb90-3c8a-5067-8fe5-19888ac899a2 | note | ○ Inspection of the following after casting
0d04d6f1-1536-575d-a011-ca79c0434c5a | note | — First precast element of each type at the earliest possible time before and immediately after stripping
56720e04-1612-577c-8c9a-55e3c001dd60 | note | — Stripping & storage
acdee0ff-18a0-5625-a39b-4cd553ca56ae | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Shop Drawings
9c1a850d-57fe-5d5c-9a34-dcc57458c2c5 | note | Inspection/Test Method - Verify
4b2b8dfe-a9ad-5cd1-9f2c-8c30fbf9dde4 | note | Record of conformity - This ITP Signed, Element Casting Checklist
ceec0016-6926-5745-984c-f94b4c138a46 | note | WP
94425407-3e8a-54cb-a627-c9a2d42385a1 | note | Responsibility - Project Engineer / Principals Representative
92c1eedd-7df6-5c1a-b86f-be4700df31b6 | date | Date Completed:
ec5d9c02-aea8-4a69-b93e-358e2067841d | checkpoint | 2.2 - Delivery of Precast Panels
0963e8eb-e2c1-5e79-8f3d-3481c91d8e0d | note | Frequency - Each Lot
f5164d33-0ec2-5244-aca1-f982ff121138 | note | Acceptance Criteria - Complete inspection of precast panels whilst still loaded on the truck prior to accepting the delivery on site.
336248ef-2bb5-58e7-97a9-88158a6f0030 | note | ○ Identify any damage/defects prior to unloading of the material and correct panel being delivered as per the sequence.
02ff43c5-1ee0-5872-8522-6a5dac8c8256 | note | ○ Precast element identification is available on each panel
c8a51499-cdfa-5b4e-8b8f-00a264b591c8 | note | Reference Documents - FH Quality Process
331294d9-bbff-52fa-a8ae-4f2a28d70d40 | note | Inspection/Test Method - Visual Inspection
b61c9d22-91e3-59f3-b926-cdc9afb6d4aa | note | Record of conformity - This ITP Signed, Materials Inspection Checklist on Conqa
f855f9cb-0ec5-55d1-9f25-66a01264d425 | note | IP
b083594d-fabb-530e-8b3a-207298575b4d | note | Responsibility - Project Engineer / Site Engineer
19cff88e-1d31-5577-b63b-9dde13da0bbb | date | Date Completed:
de2d270e-8f81-4f8c-aab7-a80ed353a49f | checkpoint | 2.3 - Erection Preparation
82fbf92f-d28a-56e7-b777-18181634b76c | note | Frequency - Each Lot
831bc499-a28e-509e-9dc5-e91cf2423352 | note | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
3739b2b5-fd34-5748-a996-da06ae404188 | note | ○ Ensure erection drawings & propping plans available to the crew
b2c8074c-7d75-5bfd-8de5-bd1aa17289ec | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850 cl 4.4.2
ad1e87a1-979d-5312-881d-4ccf2d363781 | note | Inspection/Test Method - Visual Inspection
f734f5c5-ae37-59d1-9a41-ceef1dce2bd7 | note | Record of conformity - Pre-Lift/s Commencement Checklist, This ITP Signed
0ac93dda-e517-5dc9-b82d-d9219411a9d0 | note | IP, SCP
f1a6eca3-36b2-5596-8da7-a74dd3b47245 | note | Responsibility - Site Engineer / Foreman / Surveyor
223db3c4-d584-5d7a-867e-889675e0b135 | date | Date Completed:
3a2cd550-1987-4a32-9bb7-b3f095930b65 | checkpoint | 2.4 - Panel Placement
4d163078-0a60-5486-8913-d34a0282d5d4 | note | Frequency - Each Lot
7a02a727-4c12-5ddf-9862-3a397d4cab0f | note | Acceptance Criteria - Levelling shims have been set correctly and gap between the footing & precast panel is not greater than 40mm
00aa9f62-53ff-5654-ab5f-23cfe3e2528f | note | ○ Survey to confirm panel placement as per the design
afd97b72-8f24-5d70-a846-f5d06289b8e0 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321 Drawings
715ce228-7f52-588e-9e08-772ae14c0b7b | note | Inspection/Test Method - Verify
711855bd-3553-5444-a40e-928e82d5ccba | note | Record of conformity - This ITP Signed
5a5d9fe2-b835-5e85-b6ab-75f9d38a5b61 | note | IP / SCP
22dc27e6-5110-5310-8d59-d1b868abed93 | note | Responsibility - Site Engineer / Surveyor
470d748f-eaef-56ad-9256-f8a9aede842c | date | Date Completed:
c9e16d65-56b7-42f2-9414-f3c587295f3f | checkpoint | 2.5 - Propping & supports
7fca6c3e-3f3b-50aa-9f50-70d2bbacee39 | note | Frequency - Each Lot
3644fb02-0326-5d24-af50-8a4dc6a5e173 | note | Acceptance Criteria - Witness Point
2b5cdef7-3619-577a-9453-257a0bb4e207 | note | ○ Propping plan is available for each precast panel
5a0d4d23-ac6a-56be-b260-ad113110b869 | note | ○ Ensure propping is installed as per engineer’s design and/or conforms to AS 3850.2 Sections 5
38858e64-5faa-56f3-a9e6-0cba7297e649 | note | ○ Inspection Notice provided for installed temporary bracing
845df5da-6844-512a-9cea-a81637df390f | note | Reference Documents - ZULU-BECA-001-SPC-00005 0321, AS 3850.2 Section 5
d7469f77-fe27-5507-befc-0ccf94b7d4e2 | note | Inspection/Test Method - Visual Inspection
4cdacf3d-9027-57ec-8960-6a11f1b9d047 | note | Record of conformity - This ITP Signed, Building Engineering ITP
c9a86c84-3220-5f5b-aedc-ac2b6aacb40e | note | WP
68279ee0-8bcf-578c-942a-af0f871f186f | note | Responsibility - Site Engineer / Foreman / Principals Representative
dac54f02-5278-5669-a6ca-0c1ddcc5aea0 | date | Date Completed:
5c762cc4-94da-48b4-9a32-8193170294c4 | checkpoint | 2.6 - Fixing & Welding on Precast Elements
617ce996-8a57-5015-9878-881a6e1e3ab0 | note | Frequency - Each Lot
d00dc752-4028-5bc2-893b-fa1c9db8625b | note | Acceptance Criteria - Install all fixings as per the drawings & engineers plan
5fd8a5e8-7c3e-5f3e-bfce-cf0c27ed7ae4 | note | ○ All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
d231c235-e322-5d7b-8541-6b7dc30990ed | note | Reference Documents - AS 1554.1 Drawing 20002
36df6213-aa81-5377-ab20-6a721248047e | note | Inspection/Test Method - Verify
eda2b672-17c2-5290-98f1-91267019e081 | note | Record of conformity - This ITP Signed Welding Certificate
14ade121-5f9d-59e1-be36-f1173d0c4747 | note | HP*
d7c0eb35-d283-5f75-9268-976539b68b09 | note | Responsibility - Site Engineer / Foreman
6cbf68e0-2fe0-576e-82a1-80429c8fdd79 | date | Date Completed:
3d5eb739-1361-4ed8-9266-be84de515f7e | checkpoint | 2.7 - Testing of Welding on Precast Elements (if required)
7b565fe0-a4fd-53d5-ad65-637358c17464 | note | Frequency - Each Lot
e8706ddf-9cd5-5e93-86a4-109280cd9127 | note | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table or as otherwise stated by the engineer:
4d066bb9-1a3d-5bd5-b9a1-219d2b94ebfd | note | – – – – – – – – –
f2b22a3f-2a65-52f2-8480-73fc930e7806 | note | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
4cef1085-e35c-5cbe-bc56-5f3571dba6ee | note | – – – – – – – – –
f0dc9dc5-ba9d-5e9f-a6b5-a4033ae8035d | note | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
776900ec-27d1-52dd-9c6d-bd8c29e1895f | note | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
125e71d2-bd25-5714-921c-c61cdcf3d623 | note | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
c46a84c3-261d-5b9d-9cbe-1eab98348210 | note | – – – – – – – – –
c5f28dcf-03f4-55d0-81eb-ccb486fb97c0 | note | Reference Documents - Drawing 20002 Note S8
2fe091ea-906e-5fcd-a15a-97a81684862c | note | Inspection/Test Method - Verify
31ca6b5c-1a86-5cdb-94f5-d15d96f8a0b2 | note | Record of conformity - This Signed ITP, Welding Test Certificate
faf4ed83-23f3-532d-a1e2-bfdcfa2ceb07 | note | HP*
c4f1c274-2571-5d6d-9bfc-906f89ee3a73 | note | Responsibility - Project Engineer / Site Engineer
a428003c-87fa-5e03-b4c8-264dd20657eb | date | Date Completed:
2fb0f814-0b96-472d-8e24-e141d34446a2 | checkpoint | 2.8 - Grouting
8ca66cdb-2e00-5e67-90f6-585a9788086b | note | Frequency - Each Lot
c174b55c-f8d7-5490-b767-094c8c73d072 | note | Acceptance Criteria - Grout to be used shall be non-shrink and have a 28 day characteristic strength of 40 MPA. Details of the proposed grout used to be submitted to the engineer for approval.
1d997adb-e02e-5853-b8f8-441aafd76acc | note | ○ Note: sealing of the panel vertical joints will be by the precast contractor.
c9ff5cc5-5deb-5741-b1a1-f1493b5b66a0 | note | Reference Documents - Drawing 20003 Note PC35
b53bca2e-4058-520e-8910-898e37b7570f | note | Inspection/Test Method - Verify
fc19ee69-a3ed-5f95-9c1e-7ca7a2474492 | note | Record of conformity - This ITP Signed, Building Engineering ITP
c80aadec-40fc-5f7b-972b-f71b23730298 | note | IP
57ee8a4b-c02b-523a-9b41-30cdca97b6d0 | note | Responsibility - Site Engineer / Foreman
34bf48ab-5362-5524-b280-9db76bafda68 | date | Date Completed:
917ba98a-82d8-4c72-9a14-5e193dfc1aea | checkpoint | 2.9 - Removal of Props and Inspection of Completed Precast Walls
9ea7723e-30e8-5a7c-9226-e056043a43e1 | note | Frequency - Each Lot
16ada410-8285-555d-8f7d-9d36b7900573 | note | Acceptance Criteria - All propping must remain in position until all structural elements (roof beams, bracing, struts and purlins) affecting stability are fully erected and braced, securely fixed to the panels and the panels have become an integral part of the structure. During construction the builder must ensure no panel props are disconnected by contractors other than the panel contractor.
fe123380-9114-57fa-91ad-081ad2761fd3 | note | ○ No propping is to be removed without the written consent of the temporary works engineer
43ef42a0-e56a-55b4-ad85-d2dff024cbb8 | note | Reference Documents - Approved Shop Drawings Drawing 20003
bc6cafa0-866a-5d0a-86a4-1ce42cdd65ac | note | Inspection/Test Method - Visual Inspection
96cd1e12-058f-573d-a156-a36b2ddc7fbd | note | Record of conformity - This ITP Signed, Engineers Written Approval, Building Engineering ITP
3123aadf-503f-592d-963d-26666cc79d1b | note | HP*
5ec14204-ddf6-52ae-9f8b-40e544a9b4c4 | note | Responsibility - Project Engineer / Site Engineer
4b1eea38-75c6-59c9-8d59-8a5b4f2d7cb2 | date | Date Completed:
26a10640-de4b-4347-8182-151ec05e63a2 | section | 3.0 - Construction - Structural Steel Roof
9b003894-db6d-47be-8317-d01ef52733fa | checkpoint | 3.1 - Delivery of Steel Sections
bdc9830c-4283-54e4-8e79-7342d9e2395d | note | Frequency - Each Lot
740a1965-87d6-58e2-a5fb-ba575a6a4bfc | note | Acceptance Criteria - Complete a materials inspection upon arrival of steel sections.
2b26ffbc-867f-5ebf-9788-83d4f66e3a56 | note | ○ Ensure correct components and sections have been sent
f11dc666-8ffc-5894-9c13-b5dd127c3d15 | note | Reference Documents - FH Quality Process
668e3c2b-b578-58ff-a88a-db88ce8c8fe2 | note | Inspection/Test Method - Visual Inspection
4f1c5e87-2219-5192-a10b-389e8e545bb0 | note | Record of conformity - This ITP Signed, Building Engineering ITP, Materials Inspection Checklist on Conqa
f9f07b99-d592-5098-9618-8e68182c684f | note | HP*
b47291b7-5d82-54f4-8b39-89a62d31ee57 | note | Responsibility - Project Engineer / Site Engineer
89d1af5e-047c-500c-93de-85eb70595dc6 | date | Date Completed:
0e1b0f0f-7041-46eb-8fca-cc0c55bc7bc1 | checkpoint | 3.2 - Erection Preparation
36830239-cf60-54e1-93a5-e2cc1ae03187 | note | Frequency - Each Lot
32942208-6064-5766-9834-2d4369179b71 | note | Acceptance Criteria - Complete Pre-Lift/s Commencement Checklist
556e573e-1781-5d20-aa7d-a876f0abb570 | note | ○ Lift sequence/arrangement of steel members available
ca40cbe3-7045-50e4-b7ed-0ad21d418417 | note | ○ Adequate fall protection in place eg guard rails, safety mesh
fca6e940-8b09-574f-a724-7aebe42d6224 | note | Reference Documents - Drawing 20002
6f4916d4-060c-51ab-80db-dc0edaf41194 | note | Inspection/Test Method - Verify
977aa463-e702-5e40-beed-99a82e0039c9 | note | Record of conformity - This ITP Signed, Building Engineering ITP
ba6a247d-1729-5709-a8e9-ca9cad8e5636 | note | HP*
3946c6c4-7942-518a-84ef-fecaa18a3ad3 | note | Responsibility - Project Engineer / Site Engineer
efcd1830-ac6d-555d-825d-b2f7bd4e6948 | date | Date Completed:
e69240e5-6f30-4d35-94be-06e33fd355d4 | checkpoint | 3.3 - Erection of Steel Members
bb49ddc4-0318-5409-83c6-7ce7ae92696a | note | Frequency - Each Lot
868d2b71-ad3c-55ff-9296-308b330d14d4 | note | Acceptance Criteria - Steel Members erected as per design layout and Steel Framing Schedule
25b244d4-7861-50ec-9710-2c92f8dfe4ea | note | Reference Documents - Erection Sequence Approved Shop Drawings, Structural Drawing Set 030-20
685a4595-d339-5816-b8a6-f00395372f76 | note | Inspection/Test Method - Visual Inspection
b3340cb2-1af0-53ab-bfee-56e9702e8dc5 | note | Record of conformity - This ITP Signed, Building Engineering ITP
df044819-4489-5c24-bee9-9a628c026571 | note | IP
070d2b7d-771c-5956-b10e-ef4cc591850e | note | Responsibility - Site Engineer / Foreman
4c806dd4-79a5-554d-9759-122ab8060046 | date | Date Completed:
12822e1b-cbaf-4834-b92a-9ddcddb5d006 | checkpoint | 3.4 - Bolt installation
dbd7b1c2-ed9a-5633-a43e-f0de6ef62393 | note | Frequency - Each Lot
85c6e8eb-9d23-56b2-9dc3-717fe3883fa5 | note | Acceptance Criteria - Unless otherwise noted, all bolts shall be M20 Grade 8.8/S, all H/D bolts shall be grade 4.6/S.
f0c8714e-6a13-563f-8927-0e8c5a4ff031 | note | ○ No connection shall have less than 2 bolts
31f18543-3f7e-5756-8af5-1239fd5ba16f | note | ○ Bolts to be installed as per manufacturer/engineer specification
990024d3-7289-5c74-a1f1-4e7c26f3810e | note | Reference Documents - Drawing 20002 Note S6
f39b661a-e6bf-55e9-960b-ea6504b9692b | note | Inspection/Test Method - Visual inspection
6147f49c-891e-58f1-827f-71a79d4b4571 | note | Record of conformity - This ITP Signed
4bd1e4c5-65c7-5b4c-a46a-eb28d31fe2b4 | note | IP
d09a5e1f-bb81-5b8c-b45b-4c6c62b025d6 | note | Responsibility - Site Engineer / Foreman
3f536564-2ea1-5dea-aa78-4f0c36e218ab | date | Date Completed:
8b49cf40-4a05-465c-997e-96f4d33a4e5f | checkpoint | 3.5 - Welding on Steel Framing
43bc7846-b4f3-5b1e-a331-cb847fb8870e | note | Frequency - Each Lot
b203ca90-ac26-5306-9dbc-cb1c61eaf609 | note | Acceptance Criteria - All welding shall be carried out in accordance with AS 1554.1 unless noted otherwise, all welds shall be 6 continuous fillet category SP using E49XX electrodes - butt welds shall be complete penetration butt welds, category SP.
95e12cac-3c85-52a0-b645-79a1dc634545 | note | Reference Documents - AS 1554.1 Drawing 20002
a370217d-6a8a-5b73-8814-789af9286473 | note | Inspection/Test Method - Verify
8435eea3-1542-5866-ad7c-7df0cd144447 | note | Record of conformity - This ITP Signed Welding Certificate
fa484a78-b5f1-5d38-90f8-807bf216dad0 | note | HP* IP
ccfb08f1-3600-51f1-8ec5-5d148b7d7c29 | note | Responsibility - Project Engineer / Site Engineer
28dd321f-4b79-5869-982b-f65126b26c96 | date | Date Completed:
15fe4e6f-aea7-4543-8bc8-18720b1277e4 | checkpoint | 3.6 - Testing of Welding on Steel Framing
ecd39c90-6d35-5236-a0a9-20ffa9a0df2d | note | Frequency - Each Lot
59856f88-70d3-5fb2-8e9f-a127fd1fa564 | note | Acceptance Criteria - A competent inspector shall inspect welding works as per the below table:
6c0432e0-bc14-5729-9863-1b0ff8855861 | note | – – – – – – – – –
7a93941f-9817-56ed-a23b-e35dd2892320 | note | WELD TYPE ¦¦ % OF WELDS TESTED ¦¦ TESTING PROCEDURE
aaa8063b-3070-5cdb-ab60-f6f17b3ab947 | note | – – – – – – – – –
f53ca713-bc33-5a25-874b-0d06da7e2b66 | note | ALL GP/SP ¦¦ 100% ¦¦ VISUALLY SCANNED
b4c5c6ae-bb98-5173-b6ed-83e8adf0d776 | note | SP ¦¦ 20% ¦¦ VISUALLY EXAMINED
73fde17f-dd2d-5af6-9eec-c8493dade9b7 | note | SP BUTT ¦¦ 5% ¦¦ ULTRASONICALLY OR RADIOGRAPHICALLY
aeae3d0b-5e6e-5a33-8a0d-df37acf728a7 | note | – – – – – – – – –
34bb1725-edf2-5e43-ac22-476c479c0551 | note | Reference Documents - Drawing 20002 Note
473b139d-ac9d-592f-9ab0-d0812677fde0 | note | Inspection/Test Method - Verify
39c96f4f-82a6-5be1-a727-ae2d66882eda | note | Record of conformity - This Signed ITP, Welding Test Certificate
b88c568d-ee09-5dcc-82f8-d383a498a038 | note | HP*
1f95ab89-9dd3-577a-9a30-9f0d7c7c889d | note | Responsibility - Project Engineer / Site Engineer
7f8a620e-a390-5f57-ab53-8a5d8e4762c5 | date | Date Completed:
3353926a-1127-4ad4-9d3d-5e6bfbeade14 | checkpoint | 3.7 - Inspection of Completed Steel Framing
bee679c4-4931-57ab-a321-d688d0a780f0 | note | Frequency - Each Lot
f8b872ca-3510-5701-9053-114e5df59618 | note | Acceptance Criteria - WITNESS POINT
7de1abac-a010-533b-9b34-5f91153a0ead | note | ○ Provide notice for an inspection of the Steel Framing erected on site before installation of roofing sheets/lining.
1834f0aa-4195-548e-ab67-06d6b5218fa1 | note | Reference Documents - ZULU-BECA-001-SPC-00005 0342 cl 1.17
db1feb12-e56a-54aa-b71f-a9b5f25d5c96 | note | Inspection/Test Method - Visual Inspection
8e1bbb72-fbf1-5b57-9a99-2bf4e32e93cc | note | Record of conformity - This ITP Signed, Building Engineering Structural Steel ITP
79466241-f6bd-51f3-b34d-8cb16a96ab5c | note | WP
f544fbf8-dda3-579b-a1c5-136ebbdfd0ca | note | Responsibility - Project Engineer / Principal’s Representative
af280d3a-95e2-5e15-820c-8e6ab6cfc940 | date | Date Completed:
8f13865f-84aa-4c98-8806-d1bb24edac05 | section | 4.0
c199956c-9bcc-4b17-9c30-32fba3616e3f | checkpoint | 4.1 - Airport Building Controller Sign Off
96208133-ae7f-5c3c-8a45-7c68159aa230 | note | Frequency - At the completion of works
d14af70f-c62e-567e-ba3f-b17df4095efa | note | Acceptance Criteria - HOLD POINT
5cb38d3d-6dbd-5c72-9e1d-d87b0755b81f | note | ○ Give 72 Hr Notification to the Airport Building Controller for Mandatory Inspection of completed precast & steel framework.
e8048d1e-d680-58c3-b5d3-12979b2c96c5 | note | Reference Documents - ALER 3 Building Permit
6852560b-3ad3-582c-8a07-77ec61809e1a | note | Inspection/Test Method - Verify
2701c5e3-17d1-5f59-a2b2-d5d0c33e93c9 | note | Record of conformity - This ITP Signed Inspection Certificate
b04d0aba-cb5d-5856-bb01-e0b577b16a71 | note | HP
570fb9f5-3520-5efc-a5ea-284b631b3d84 | note | Responsibility - Project Engineer / Principal’s Representative
afe66c70-78a4-56d9-9190-11a647ed39d7 | date | Date Completed:
45462c05-a40b-4d39-bda0-f02f19f94eaa | signoff | AUTHORITY HOLDPOINT
4ca4a586-ecf6-4d2b-8aee-6bcfe7066931 | checkpoint | Final Inspection
6dca4a6b-b170-58d3-98d3-f48b5bc891cf | note | The signature below verifies that this ITP has been completed in accordance with the Fulton Hogan’s Quality system Procedures and verifies lot compliance with specifications.
737cd6a5-c435-5a6b-b20c-861732d9b368 | textbox | Print Name:
d5d7dc71-fbf5-582e-b582-0eac79c1213a | textbox | Position:
262e9f4c-a796-5f7f-a8b5-055bc03c7420 | date | Work Completed On:
965c8fa8-5d77-5ba1-9543-99e1b29b1d4e | date | Date: