## Table 1
Client: AIAL | [8 empty] | Subcontractor: Omexom | [9 empty] | Work Area: Substructure Headhouse
Project Name: Domestic Jet Terminal | [8 empty] | Job No: HA0423 | [9 empty] | Subcontractor Representative: N Lovell
1. ITP Element : Underground Ducts below slab 2. Revision Records
Rev No. |  |  | Revision Description | [12 empty] | Name of Author |  |  |  |  | Authorised by: |  |  | Date
A |  |  | For Approval | [12 empty] | N Lovell | [7 empty] | 2025-05-15
B |  |  | For Approval following comments from Mott Mac-CAN-000783 | [12 empty] | N Lovell | [7 empty] | 2025-06-17
C |  |  | For Approval following comments from Mott Mac-CAN-000939 | [20 empty] | 2025-06-26
3. Relevant Documents
Doc No. |  |  |  | Specification/ Drwgs/ Standards |  |  |  | Additional Info |  |  |  | Document No. |  |  | Specification/ Drwgs/ Standards | [8 empty] | Additional Info
1 |  |  |  | Mott Macdonald Containment Layout Zone Drawings |  |  |  | Zones 33 to 46 |  |  |  | 6 |  |  | DP001-HAW-DRW-CIV-B-H0141_C
2 |  |  |  | DP001-MMD-SPC-EL-Z-Z-0001 |  |  |  | Domestic Processor – Buildings Electrical Specification |  |  |  | 7 |  |  | DP001-HAW-DRW-CIV-B-H0142_C
3 |  |  |  | DP001-MMD-SPC-CV-Z-Z-0001 |  |  |  | Section 12 |  |  |  | 8 |  |  | DP001-HAW-DRW-CIV-B-H0145_B
4 |  |  |  | DP001-HAW-DRW-CIV-B-H0134_B | [7 empty] | 9 |  |  | DP001-HAW-DRW-CIV-B-H0146_B
5 |  |  |  | DP001-HAW-DRW-CIV-B-H0140_B
4. Process
No. |  | Description Inspection / test |  |  |  | Frequency | Spec/standard |  |  | Acceptance Criteria |  |  | Measuring Devices |  |  |  | Reporting Format | Inspected by* |  |  |  |  | Hold Points Sign off |  | Remarks
[18 empty] | HCL |  | SC |  | Consult
1 |  | Delivery inspection of HDPE ducts and fittings |  |  |  | Each delivery | AS/NZS 4130 / Manufacturer CoC 7.3.3.3 12.3.3, 12,3.4 |  |  | Correct SDR, diameter and undamaged |  |  | Visual and CoC |  |  |  | Delivery slip / CoC | R. |  | Sub |  | R | N/A |  | Material CoC matches spec; no damage No damaged packing material.
2 |  | Welder qualification check |  |  |  | Before work start | NZ Certifications; standards and industry training |  |  | Accept / reject |  |  | Document review |  |  |  | Welder Qualification | R |  | I |  | R | Hold Point |  | Welder certification reviewed and approved prior works Hawkins- ITP-000061
3 |  | Trenches and routes inspections |  |  |  | Per section | Drawings Spec 4.23.2 /7.3.4.5/7.3.4.8 |  |  | Installed as per project drawings and specifications |  |  | Visual |  |  |  | Site coordination | I |  | I |  | S |  |  | Suitable route and bend allowances
4 |  | Duct alignment check |  |  |  | Per section | Project drawings / layout 4.23.2 |  |  | Installed as per drawing |  |  | Visual |  |  |  | NA | M |  | I |  | R |  |  | No excessive bends or misalignments
5 |  | Inspection of duct cleanliness and joint |  |  |  | Before welding | ISO 13954 5.10.3 |  |  | Ends scraped, dry, and clean |  |  | Visual |  |  |  | OMX Quality check sheet | M |  | I |  | R |  |  | Free of debris, scratches, moisture
6 |  | Fusion setup – pipe end scraping, machine check |  |  |  | Each weld | ISO 13954 / ISO 13955 |  |  | Scraping complete, scan barcode |  |  | Scraper / EF machine |  |  |  | OMX Quality check sheet | M |  | M |  | R |  |  | Pre-weld approved by supervisor before fusion
7 |  | Electrofusion weld execution |  |  |  | Each weld | ISO 13955 12.4.6. 12.5.2 |  |  | Parameters met; uniform bead |  |  | EF machine logger |  |  |  | Fusion log / OMX Quality check sheet | M |  | Sub |  | R |  |  | Fusion data logged and bead visually compliant Weld number time and date next to weld.
8 |  | Post Weld visual inspection and cooling |  |  |  | Each weld | ISO 13955 / 13956 |  |  | Bead uniform, cooled per spec |  |  | Visual |  |  |  | OMX Quality check sheet | s |  | R Sub |  | R |  |  | Cooling time respected; weld integrity confirmed.
9 |  | Weld traceability and documentation |  |  |  | Each weld | 7.3.4.9 |  |  | Barcode and weld ID logged |  |  | Log Sheet |  |  |  | OMX Quality Check sheet | S |  | Sub |  | R |  |  | Log completed and ID matched field location
10 |  | Post Weld inspection |  |  |  | Project Scope | DP001-MMD-SPC- EL-Z-Z-001 12.5.2 |  |  | CCTV footage of below ground ducting, duct contains no debris or penetrations that could damage cable sheath when pulled |  |  | CCTV |  |  |  | Video | S |  | Sub |  | R |  |  | Submission of CCTV footage before handover
11 |  | Electro fusion welder calibration |  |  |  | Project Scope | As per manufactures specification |  |  | Electro fusion welder calibration certificate |  |  | Calibration certificate |  |  |  | Certificate | S |  | Sub |  | R |  |  | Submission of calibration certificate before handover
12 |  | Draw Cord |  |  |  | Each conduit | 2012-03-08 |  |  | 5 kn |  |  | N/A |  |  |  | QC checklist/ photograph | M |  | Sub |  | R
13 |  | Hot Bending of HDPE Ducts |  |  |  | Direction change | DP001-MMD-SPC- EL-Z-Z-001 7.3.4.5 |  |  | Minimum bending radius of 2m |  |  | Measuring tape |  |  |  | QC checklist | I | [6 empty] | Heat apply using controlled hot air: duct support during bending. Cool down in place to retain shape
14 |  | Installation of tracer wire |  |  |  | Each installed duct | DP001-MMD-SPC- EL-Z-Z-0017.3.3.11 |  |  | Wire securely fixed on top of duct, continuous, accessible at both ends | [6 empty] | QC checklist Photograph | M |  | T |  | R |  |  | Tracer wire to be installed above duct, secured at 3m intervals. Ends terminated in accessible pits or boxes
15 |  | Installation of Warning Tape and Polymeric Cover (Mag slab) during Backfilling |  |  |  | Each installed duct | AS/NZ3000. 2018 |  |  | Install 300mm above top of duct. |  |  | Tape measure, visual check |  |  |  | . QA checklist / photograph | M |  | W |  | S | removed |  | Materials supplied by Omexom, installation by civil contractor. Hold point required prior to backfilling. Supplier to verify delivery and provide installation guidance. Coordination required to ensure correct placement and documentation.
16 |  | Pit to Duct Jointing Process |  |  |  | Each duct at each pit | DP001-MMD-SPC- EL-Z-Z-0017.3.3.12 |  |  | Manufacturer’s installation guidelines and project specifications |  |  | Secure, watertight connection between duct and pit; no gaps or misalignment |  |  |  | Visual check, QA checklist / photograph | S |  | R |  | S
17 |  | Coordination with Waterproofing and Concrete Encasing |  |  |  | At each interface with waterproofing or encasement | MMD DP Buildings Elec Spec July 2024 7.3.3.12 |  |  | IFC drawings and Sika Details (by others) |  |  | N/A |  |  |  | By others | S |  | R |  | R |  |  | By others
5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
Delivery Slip / Certificate of Conformance (CoC) For delivery inspection of HDPE ducts and fittings. | [13 empty] | Calibration Certificates For electrofusion welder calibration.
Welder qualification checks. | [13 empty] | Log Sheets For weld traceability and documentation.
Site Coordination Reports For trenches and routes inspections. | [13 empty] | CCTV Footage For post-weld inspection.
QA Reports For duct alignment checks.
6. Distribution Records
| Name |  |  |  | Position | [5 empty] | Company | [14 empty] | Date
| TBA | [9 empty] | Mott McDonalds
| TBA | [9 empty] | BECA
| TBA | [9 empty] | AIAL
 Inspect (I) – To visually examine or measure an item or contracted work operation to verify its conformance to predetermined quality requirements  Review (R) – To examine any form of documentation to establish its acceptability against specified requirements  Surveillance (S) – To observe in-process activities to the degree necessary to be assured that they comply with the established criteria  Test (T) – To subject a component, structure, or system to a controlled set of physical, chemical, environmental or operational conditions to determine or verify its capability to meet specified requirements  Witness (W) – To watch over, observe or visually examine a specific work operation or test performed by others under Contractor supervision  Monitor (M) – General oversight of work in progress with no need to document formally.  Submission (Sub) – Submission of a document