## Master List Templates
Id | Type | Name | Values | Prompting Name
1f037b5a-e32e-492a-858a-fa4721d88988 | checklist | Bonding Installation |  | Bonding Installation
90ad685f-59f8-44e5-91d1-d5c07edb1f28 | section | Pre-Installation
426b0e08-24af-497b-a564-2b74e6209a5a | checkpoint | 1.01 Review drawings and ensure all earthing conductors installed as per relevant drawing. Hold Point
4b82e205-8a2b-4221-b31c-60aa7d7872fc | signoff | Signoff
184b8943-2362-4506-a52d-42c60703c805 | section | Installation
193b2b43-c078-47eb-9c59-a41b41b9f507 | checkpoint | 2.01 Confirm conductor size as per drawing. Confirmation
bc804dac-a1e1-4b04-92d9-d81235fc9b5a | checkpoint | 2.02 Confirm all required links are in place. Confirmation
2e002e62-ca90-43bf-8b9b-31422561dd14 | checkpoint | 2.03 Confirm all bolted connections are torqued and correct fixings are used . Confirmation
c299a922-aec0-442e-9f0e-1edd8957b590 | checkpoint | 2.04 Confirm all cables are terminated correctly (i.e. correct lugs, ferrules etc.). Confirmation
5c1adf67-ecec-4429-ab2a-bb8f549324c8 | checkpoint | 2.05 Confirm labelling installed and correct. Confirmation
2f6430c5-b057-4ad4-9cbc-98029d8a8de4 | checkpoint | 2.06 Confirm one lug per bolted connection. Confirmation
6e0e3ccc-9a12-4482-9cbe-31b621bf1031 | checkpoint | 2.07 Complete testing. Ensure test sheet complete . Confirmation
65a7acfe-4189-4120-9d62-8076531be034 | signoff | Signoff
fd2d5b7a-3cb7-4981-afa8-4fb08916262a | section | Completion of works
93e0dd57-51e4-413a-8101-318b22ac82db | checkpoint | 3.01 Supervisor to update, collate, check documents, drawings and results then record . Confirmation
7b77c117-395f-41b9-86d8-ba42dd0b62f1 | signoff | Signoff
1bc0ecbc-239e-4f0f-bf86-4081c7b208de | section | Documentation
5e625758-3ad4-4184-8b32-e7199f76e010 | checkpoint | 4.01 Verify all drawings “As built” status . Confirmation
8a49a245-dbdf-42eb-b2b1-5a55997568e3 | checkpoint | 4.02 Verify that all necessary documentation has been signed by the appropriate persons . Confirmation
c5bcca10-5901-415c-9fbc-29e4bba4cb90 | checkpoint | 4.03 Collate and Deliver final reports. Confirmation
425676ba-576e-4572-a086-d1c9e79c6c6c | signoff | Signoff
94940b1f-38a9-4b83-9494-daf2a07570e3 | checklist | Cable ladder & Support installation |  | Cable ladder & Support installation
5e3cebee-67c0-4b86-b7c5-8f942e7734d1 | section | Pre-Installation
5cf31b0a-0b86-4987-b119-d69a2dfee1fe | checkpoint | 1.1 Review drawings and ensure all cable supports installed as per relevant drawing. Hold Point
35a6d7af-08b1-4cc4-b98c-0a0bf57e1342 | signoff | Signoff
b3afae21-0c1f-47d5-9019-c56723b521e7 | section | Installation
15c5e49c-8939-4173-b523-6654224472ce | checkpoint | 2.1 Confirm all brackets installed at suitable spacing with correct fixings. Confirmation
28b20ba6-38f0-45d8-9249-3ed01430f2df | checkpoint | 2.2 Confirm all cable tray are weatherproof. Monitor
6f60fbcd-75ae-4908-8f8e-a60eb1541953 | checkpoint | 2.4 Confirm all brackets are as per spec. Monitor
7980bef7-5eab-40ac-bfdd-a97d731d0f55 | checkpoint | 2.5 Confirm all fixings used are HDG. Monitor
a86e951d-3358-4f2c-8c08-6e660364e5a1 | checkpoint | 2.6 Confirm all fixings installed correctly and are suitably tight. Confirmation
e8b4ac76-21f1-4853-a8f1-1d0c384a6d89 | checkpoint | 2.7 Confirm fixings installed outward to reduce risk of cable damage. Confirmation
feb774df-531c-4934-9326-3841830de4c0 | checkpoint | 2.8 Ensure cut edges are filled and smooth. Confirmation
e48bd6b1-d567-49d5-b077-dbb3b3c1adaa | checkpoint | 2.9 Ensure all bonding links are in place. Confirmation
7100a56d-7b74-46b6-bf36-204fd33b2f1b | checkpoint | 2.1 Ensure loading does not exceed maximum as determined by manufacturer. Confirmation
8cad1e5d-67bd-4c4a-8d51-341d03db1baa | checkpoint | 2.11 Ensure all tray has lid installed where required. Confirmation
886c5001-d2c3-419f-ba52-db5a0804158d | checkpoint | 2.12 Confirm one lug per bolted connection. Confirmation
ff260095-8858-4365-be90-17558c5f18fc | signoff | Signoff
4b900dff-812e-46d5-9da0-b0a35a1542c0 | section | Completion of works
a70dc621-e153-425b-a614-7ac4af97eb6e | checkpoint | 3.1 Supervisor to update, collate, check documents, drawings and results then record . Monitor
3ea8d915-5675-486f-ae32-f1fde8b17aea | signoff | Signoff
f43cabae-4448-4679-9c6f-b0cdc7e1ffc3 | section | Documentation
75068ba4-6c51-4675-b4df-5ab3a2bbd416 | checkpoint | 4.1 Verify all drawings “As built” status . Confirmation
39259735-bfc1-434a-bb88-b6961cdd2a93 | checkpoint | 4.2 Verify that all necessary documentation has been signed by the appropriate persons . Confirmation
ee0f1fc8-25d3-4327-a9a1-da1344e06893 | checkpoint | 4.3 Collate and Deliver final reports. Confirmation
c06694d3-613d-4105-83ca-70bf4446cbaf | signoff | Signoff
4be14a0f-25be-4397-8139-a0dff8310754 | checklist | COC |  | COC
c8cbceba-e5aa-4612-bb11-3a770a9848c1 | section | Information
ff04e413-69e6-4b8a-9589-f88376e66eab | checkpoint-no-value | COC
05a4d874-0fe3-5a9b-89b0-a6ec5bf7e8ea | note | Project: P.0597875 - AIAL WP1
5ca76c81-a37e-5de5-af42-e618524f8814 | textbox | Area
065c128b-0132-52fd-a42a-01ad52504a81 | textbox | Item
1fc4a866-6926-4de4-a56c-006af814f27b | checklist | ELV Cable installation |  | ELV Cable installation
15a881c4-bb7d-4e24-846b-3dc5476e0343 | section | Pre-Installation
295083b3-a922-4289-9d67-44884a8de670 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Hold Point
ba6db4ff-00ab-458a-ad45-da9bf0e0fc55 | checkpoint | 1.02 Verify drawings latest revision. Hold Point
beaf017c-dba0-461a-8fd2-7f179346f874 | checkpoint | 1.03 Ensure ducting/trenches installed by others is checked prior to use. Hold Point
1929fc5f-ab95-4d52-b28d-6c17eed470d2 | signoff | Signoff
f89a38bc-16fc-4e18-99cd-c49e8f1dc660 | section | Installation
6283d13e-7fbd-45b0-ae8b-9415086f2211 | checkpoint | 2.01 Ensure cable drums are set up correctly and level - Jacks must be suitable for the load & size of drum. Monitor
dd5912ae-9518-4467-84c5-299dfa4f9b26 | checkpoint | 2.02 Ensure cable drums are set up in a location clear of personel and traffic. Monitor
3a89579b-80cb-4f5e-b4dd-7cf86bcf2981 | checkpoint | 2.03 Ensure any edges to trenches or ducts are smooth and chamfered or protected. Confirmation
8a7c248c-1b13-4e9f-a6a3-11ebd540c12c | checkpoint | 2.04 Minimise the amount of 'drag' across the ground when installing cables (ensure enough personnel are present). Monitor
4c101be6-6828-4c6a-9c39-be0ef3517f9b | checkpoint | 2.05 Ensure pulling tensions and bending radius' are not exceeded during installation. Confirmation
7d866c71-2571-4e47-972a-f49d21597593 | checkpoint | 2.06 Ensure that cables are grouped in a manner to reduce magnetic interference where possible. Confirmation
6d9a4a4f-f66b-4606-8007-978d6822e338 | checkpoint | 2.07 Ensure cables are supported along entire length. Confirmation
3d42ec39-b8ad-4a1d-824b-f69ef31e1a16 | checkpoint | 2.08 Confirm each cable is labelled appropirately at either end and enough length left for termination. Confirmation
bc3cc803-fd75-4cd6-84db-57daf5fda00a | checkpoint | 2.09 Confirm no damage has occurred to cabling during installation. Monitor
96b8b5a6-89fe-47b1-a12a-69ac83e87563 | checkpoint | 2.1 Ensure ends of cables are taped/capped until terminations unertaken. Confirmation
9de06f5e-aa53-42db-8160-6e985d4bcb26 | checkpoint | 2.11 Mark up "As built" drawings.. Confirmation
facb8470-8ee7-4403-80c5-21d364293acc | signoff | Signoff
31f98984-1422-4b0d-91c6-06f69348dad6 | checklist | Fibre Optic Cabling |  | Fibre Optic Cabling
f243c632-ffea-4cb9-8a31-497e52d79f92 | section | Planning
980d25d9-86f1-41e4-a023-cb8c157f1757 | checkpoint | 1.01 Review the existing cable tray layout and plan the routing of the fibre optic cables to minimize the bends.. Hold Point
1707a1a0-e2a2-425e-8a05-0164a5ebb06a | checkpoint | 1.02 Check the specifications of the fibre optic cables to be installed, including length, type, and any specific handling requirements.. Hold Point
5403b773-5d7e-48a7-9253-eea1bdca64ba | checkpoint | 1.03 Ensure all the necessary cable pulling tools are in good condition.. Confirmation
40590889-ba7c-4d61-a30e-2767951ad80b | checkpoint | 1.04 All staff and subcontractor briefed HSE & install methodology.. Confirmation
303815a7-39e4-4977-8c12-477ac197dcd5 | checkpoint | 1.05 Ensure that the installation area is clear of potential hazards.. Confirmation
45b63d48-5e41-4139-8137-a8bb0a9c005c | checkpoint | 1.06 Verify that the team members are equipped with appropriate PPE such as gloved, safety glasses, hard hats, and harnesses.. Confirmation
23f5fbd8-2b16-4935-8e81-d9621ee17364 | checkpoint | 1.07 Inspect the existing cable trays for any damage or debris that could hinder the installation.. Confirmation
12fab083-cd4b-4161-ac76-235f7d00c231 | signoff | Signoff
cdba51a1-51cf-48dc-8dfb-56129891fe52 | section | Install
11bf6f72-96eb-4d75-bc6e-9ca46af08f7d | checkpoint | 2.01 Unroll the fiber optic cables carefully to prevent twists and kinks. Confirmation
4fe4c3c5-a553-45b6-9055-3961b9ac0402 | checkpoint | 2.02 Verify the integrity of the cable sheath and ensure that it is free from any damage or defects.. Confirmation
9ba9775c-6a47-45f9-9c96-2d4e8d11c5db | checkpoint | 2.03 Attach pulling grips to the fiber optic cables and secure them properly.. Confirmation
88742c97-f02e-4153-be15-edb06f5c7318 | checkpoint | 2.04 Use appropriate pulling tension to avoid damaging the cables during installation.. Confirmation
ee6ac072-b6d4-42ce-a4c1-5b972e1dd150 | checkpoint | 2.05 Ensure that the cables are properly supported along the entire length of the cable tray.. Confirmation
7b29b4ff-a6dc-45da-a273-8cb90ee6760e | checkpoint | 2.06 Ensure at least 3-meter cable slack is available at each end to perform splicing and termination.. Confirmation
d33169b6-11bf-4e1b-8de4-a4fc9cef2020 | signoff | Signoff
b6fa5dee-ccd2-4081-8e79-8468b1edd512 | section | Confirmation of install
daaa8d63-4287-4fe7-8c37-b839f3117a76 | checkpoint | 3.01 Cables identified by a permanent marker at each end clearly.. Confirmation
04d711a6-22c8-467f-9f6d-6465299bf7ba | checkpoint | 3.02 Cables installed in vertical cable tray are secured to the cable tray at least every 1.5 m.. Confirmation
a5f8ea0c-b870-4812-bcda-177aee0f8893 | checkpoint | 3.03 Ensure the cable has no joints or connectors.. Confirmation
5252c20a-e1a4-460b-a5cf-1a7855dab84f | signoff | Signoff
bf5243b2-cbc5-4f06-ae75-24806fe45fad | section | Splicing and termination
337f80cd-d076-406b-8bc2-05637f01509f | checkpoint | 4.01 Follow the manufacturer's guidelines for splicing and terminating the fiber optic cables.. Confirmation
5c112e18-5423-426f-991e-4bb809413964 | checkpoint | 4.02 Use appropriate splicing tools and techniques to achieve low signal loss and ensure reliable connections.. Confirmation
f643a163-ae7b-49be-a591-864073b5cece | signoff | Signoff
aa09d0ac-744d-4441-a39a-ad3f551266c9 | section | Testing and verification
e58782db-8cf8-4397-bb0e-fa014dc3411f | checkpoint | 5.01 Conduct thorough testing using appropriate equipment to verify the integrity and performance of the installed fiber optic cables.. Confirmation
4622c4bb-a8d0-450c-9026-6a93b305756a | checkpoint | 5.02 Check for any signal loss, attenuation, or other issues that could affect the transmission quality.. Confirmation
80bde2e4-4781-476a-90f4-45df0058e817 | signoff | Signoff
e231a068-67ba-4282-87d6-04d9d6a4fb10 | section | Documentation
54d62400-7c42-4f7e-9b19-4e9f52d7e8c0 | checkpoint | 6.01 Record the test results. Confirmation
a26f32ba-b45b-48c4-bdcc-f09f1b160bbe | checkpoint | 6.02 Submit the ITPs to client.. Confirmation
b298c892-1566-4f00-b9c6-8e0e29f3b3fa | signoff | Signoff
55abdc58-de10-455f-83a3-7da64309b85b | checklist | HV Cable Installation |  | HV Cable Installation
ea4b46f8-1a66-4b65-bb09-f03c70751ad3 | section | Planning
8d353139-c49c-48d7-a6ee-d4ab7a0f0e25 | checkpoint | 1.01 Verify drawings latest revision.
41c99769-094f-4d58-bbc6-566958c5e69a | checkpoint | 1.02 Cable route/installation methodology: - Verify that cable Install design route suits site conditions. - Ensure the cable route has been assessed. (Cable hauling analysis) - Pulling, jointing, & termination pits have been correctly formed and positioned.
a1116186-1509-41ab-b64c-34a2e32d6f9c | checkpoint | 1.03 All required documents & permits have been approved and issued (PTW, TMP, SWMS, and methodology).
2386c262-452c-46c2-ae5b-7ccce5e8a0c8 | checkpoint | 1.04 All staff and subcontractor have been fully site inducted and briefed on HSE & install methodology.
6dfb064c-6d40-48fc-b3ea-d21b222493a4 | checkpoint | 1.05 Ensure that the pre-installation tests on the cable has been completed, reviewed, and accepted.
3d96976b-7cf6-4906-9eb5-c98e4294a9ce | signoff | Section Signoff
b9a8327d-6825-4078-8ee7-8637d0353837 | section | Pre-Installation
e5ae69bc-8c70-4c26-b080-fd5fc6604c40 | checkpoint | 2.01 Verify that cable pulling equipment are of adequate capacity to provide a steady continuous pull on the cable.
1c7fff13-1ade-45ee-a886-cf57da936543 | checkpoint | 2.02 All site modified sections of cable management have been correctly cut; filed and treated as required.
3af9a030-76b5-4a3a-900d-3c9c0282918b | checkpoint | 2.03 All conduit interiors should be free of burrs and have been cleaned after installation.
047887bd-03c5-4553-8bce-755c1ed9eae2 | checkpoint | 2.04 Sharp Edges of cable management have been rounded. All cut ends are neat, square and treated as required.
8f8b1497-1859-4e22-9acd-7b8a81d64dfb | checkpoint | 2.05 Ensure that cable duct has an appropriately rated draw wire or equivalent installed through the entirety of cable route.
a9c249ab-b611-4ca2-b5cd-b177a44221fa | checkpoint | 2.06 Verify that all cable ducts are free from water and debris. If open trench - ensure that trenches have a bedding layer in the base of the trench to the correct depth.
0189ce9b-f358-44a0-a608-ecdba3bfb4ec | checkpoint | 2.07 An appropriately-sized mandrel should be pulled through all underground ducts prior to cable pulling. Any abrasions or sharp edges that might damage the cable should be removed.
5b1db682-e3da-45bf-b56c-6b673482a3ee | checkpoint | 2.08 An appropriately-sized foam pig/squeegee should be pulled through all underground ducts prior to cable pulling.
a2c2beec-570a-456c-a74f-b4e8f4804733 | checkpoint | 2.09 Verify that a suitable feeder device is used to protect and guide the cable from the cable reel into the raceway. The radius of the feeder device should not be less than the minimum bending radius of the cable. If a feeder device is not used, the cable should be hand-guided into the raceway.
0a714ae0-d558-4d0e-b06d-6776e2c45de1 | checkpoint | 2.10 Ensure sufficient labour is available, and correctly positioned along the cable route
3fee1a18-1048-4fdd-a4fa-77a5173ace9f | checkpoint | 2.11 Ensure adequate communication method/supervision is available and agreed for the cable pull (two-way radio, line of sight, etc.)
1d0c7baf-d7f8-4134-a4e4-a9df2518b5ba | signoff | Section Signoff
9dbababa-acad-4b32-b093-48cc33b846b3 | section | Installation
4b19d624-c97b-4e09-90e0-59049d10e1f4 | checkpoint | 3.01 Any cable pushing devices should be monitored to synchronise with the tension of the cable winch to avoid kinking the cable.
79fc1abe-2904-42df-b4aa-3b55f763d8bf | checkpoint | 3.02 Pulling tension will be increased when the cable is pulled off the reel. Turn the reel and feed slack cable to the duct entrance to reduce the pulling tension. (If applicable)
21254249-49f6-454a-abb1-a6bb2a805d9b | checkpoint | 3.03 Log continuous readings of the dynamometer incorporated in the pulling arrangement to enable the actual pulling tension to be monitored. Pulling tension shall not exceed manufacturer's requirements. (If applicable)
80517ede-2e66-47fd-bcd0-ce0f57ed602b | checkpoint | 3.04 Ensure cable manufacturer’s minimum allowable bending radius and sidewall pressures for cable installations are not violated.
6604f5f8-0f76-4be2-ba35-5a9a8b8ec216 | checkpoint | 3.05 Cables identified by a permanent marker at each end in accordance with the design documents.
632bd85e-ca2d-4602-bb0d-713b164c7118 | signoff | Section Signoff
de81929b-8c59-4043-8bd9-cb3f116699f2 | section | Confirmation of install
c054dd95-4da8-4988-a178-6ce6b447544e | checkpoint | 4.01 Vertically run cables are supported by holding devices in the tray, in the ends of the conduit, or in boxes inserted at intervals in the conduit system. (If applicable)
6e062a34-84a6-4adb-b02b-5e4010991251 | checkpoint | 4.02 Cables installed in vertical cable tray are secured as per manufacturer's recommendation.
3be533ac-93fc-4b4b-b872-21014a4f4568 | checkpoint | 4.03 Cables installed in trays are neatly arranged to facilitate identification and removal and to maximize tray fill. (If applicable)
f2683723-8dc5-4b6b-9b8f-8062e89d113f | checkpoint | 4.04 Cables installed in trenches have a minimum separation distance as prescribed in the design drawing and not less than 150 mm
60d58927-f919-4c1c-9913-1a508a089478 | checkpoint | 4.05 Cables installed in trenches have polymeric cable protection complying with AS/NZS 4702 covers as prescribed in the design drawings.
3a9d4456-4924-4347-a2ad-48a1eb373125 | checkpoint | 4.06 Cables installed in reduced depth trenches have a capping of unreinforced concrete as prescribed in the design drawings. (If applicable)
037b2a3b-b557-4047-95a1-28d919eeb96f | checkpoint | 4.07 Cables installed in trenches have underground marking tape complying with AS/NZS 2648.1 as prescribed in the design drawings.
7e616141-e601-4bf5-a426-14035582167c | checkpoint | 4.08 Cable duct ends have been sealed with expanding foam or cable duct sealant. (where applicable)
e416ec22-74ad-435c-8d11-a5400087794f | checkpoint | 4.09 The exposed ends of all cables installed but not terminated shall be covered with a protective end cap.
3dc6d644-0502-4bed-b030-375c261ef1ca | checkpoint | 4.10 Lengths of cable cut from a drum or when the drum is not emptied completely, the ends of any cut length are sealed with an end cap, such as a heat shrink end cap, to prevent the ingress of moisture.
ded528cd-178b-47f6-b7c5-4dfa7ba3eb3b | checkpoint | 4.11 As built information completed and submitted for review.
e5d85cd9-b4d5-403c-ba73-ab9d8e279e13 | signoff | Section Signoff
dfe9640b-4d28-4f6c-a28a-c4ab44ff37cc | checklist | HV Cable Jointing |  | HV Cable Jointing
1caa0ba0-97f2-4c58-bdb3-661b3de5cca7 | section | Pre-Installation
05d79979-783e-4078-907c-fdb59d514cc1 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Ensure permits are valid and all parties are notified. Confirmation
7ac4750b-b153-4fd0-ad17-c0bbe993d3b6 | checkpoint | 1.02 Verify drawings is the latest revision Confirmation
aaf8b8f2-39dc-43e2-8f8f-78eeab470c37 | checkpoint | 1.03 Confirm correct cable joint kits supplied. Ensure voltage level, bushing type, indoor/outdoor, correct diameter. Confirmation
9970f927-5ea6-48d1-b05c-e0da18f56334 | checkpoint | 1.04 Termination pit dimensions suitable for cable joint Confirmation
9b41adbc-be5f-4485-a98d-295a784ffd0a | checkpoint | 1.05 Termination pit free of water, and adequate access provided Confirmation
14c6ae4b-e669-427f-92e3-753449af99a2 | checkpoint | 1.06 Existing cable correctly identified, isolated and or spiked and communicated to all parties. Confirmation
e8044e6e-cdb8-4514-a9d4-35297d931f86 | checkpoint | 1.07 Pre-joint cable test carried out and results recorded Hold Point
12037fd9-6754-4a2f-9415-72924bd5a445 | checkpoint | 1.08 Ensure Cable Jointers ITP's Template received and verified Witness
86d2b230-0f1e-4a2f-971b-2f9b119f082f | checkpoint | 1.09 Circuit breaker on either end are isolated of the relavant cable and LOTO procedure is applied. Hold Point
780aa6c3-3c92-48fe-8b64-5d3d30559627 | checkpoint | 1.10 Ensure cable is de-energised. Prove-Test-Prove. Confirm with the relavant party that the work can proceed. Hold Point
07dfe124-081b-40ae-9d6d-b6f99c567808 | signoff | Signoff
2946bdb2-8314-437a-be4d-d12fa789b8b6 | section | Installation
7b274c5e-c978-44b9-be4d-f6366e44e9f0 | checkpoint | 2.01 Ensure the cable is cut at the correct location. Confirmation
c72ccff4-0ac9-47fb-9a77-deee0694bad0 | checkpoint | 2.02 Ensure correct phase rotation matched for new and existing cable. Cable core identified by a label or marked Confirmation
67df31c7-cc63-41c8-998f-73b998527e2a | checkpoint | 2.03 Ensure HV cables are supported/clamped as necessary Confirmation
1291f447-529d-4e91-a122-713f899c9719 | checkpoint | 2.04 Ensure either side of the cable has a straight section for cable jointing and ensure no weight/pressure on the joint positions. Confirmation
e1476f9a-8e55-434d-ac7e-055bfa305c2d | checkpoint | 2.05 Prepare the cable joint in accordance with the instructions provided by the manufacturer joint kit. Confirmation
63477630-a9e6-4b52-b7d2-0699fa186b9d | checkpoint | 2.06 GPS location captured (if required) Confirmation
5845cce7-4823-44e0-91cb-9fc43e09b2b0 | checkpoint | 2.07 Photographic evidence taken and recorded Hold Point
560c971e-157b-46b4-b597-c8e81dc20b6e | signoff | Signoff
0a91346d-1332-483f-bfcf-6ce33ca86d1d | section | Confirmation of the installation
60059c28-eac1-4d53-baf7-a09bd8005956 | checkpoint | 3.01 Cable jointers completed and signed ITP received Hold Point
ea518e42-e7e7-4790-938a-44781e8a3708 | checkpoint | 3.02 Correct back fill carried out as per specifications Witness
42254681-577f-4ccf-ac53-21335f1a541b | checkpoint | 3.03 Termination chamber closed, sealed and no tools or detritus left inside. Confirmation
18ad2dbd-45fe-4bfc-b3f8-1ce78616861e | checkpoint | 3.02 Correct back fill carried out as per specifications (If applicable) Witness
81e93a00-6510-49dd-b06a-53a6b07d9bdb | checkpoint | 3.03 Termination chamber closed, sealed and no tools or detritus left inside. (If applicable) Confirmation
c584f3ac-7736-4b1b-8401-4a5c95d051b8 | signoff | Signoff
f334fdb9-ab63-4630-a697-df4199ae7067 | checklist | HV Cable Termination |  | HV Cable Termination
130de89c-d32f-4888-af61-2473ee1089a8 | section | Pre-Installation
39d66fa2-d96d-45a0-8395-a77ba294d481 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Confirmation
2ad9f1d4-1a9e-4748-bf16-8347fd3d0b92 | checkpoint | 1.02 Inspect that cables do not make contact with sharp-edged sheets in the switchgear. Cover sharp-edged spots, if required.. Confirmation
c3da56dd-794a-4544-9450-701402ce5326 | checkpoint | 1.03 Verify drawings latest revision. Confirmation
ed6d7bc4-0737-43f9-9b71-61a9c4ae717a | checkpoint | 1.04 Ensure the equipment is secured firmly to the earthing.. Confirmation
686a0831-f837-426f-9c7b-f9a662726ade | checkpoint | 1.05 Equipment frame connected to main earth bar.. Confirmation
e76ab271-0c80-4e59-b5a8-145b6a0ce7f8 | checkpoint | 1.06 Cable box bushing earthed by switching associated earthing switch to ON.. Confirmation
0a3f19c5-e618-4a26-bded-fae11dfa5757 | checkpoint | 1.07 Confirm correct cable termination kits supplied. Ensure voltage level, bushing type, indoor/outdoor, correct diameter.. Confirmation
9b6edb55-b453-4695-bb48-1f797961fe77 | checkpoint | 1.08 Cable box and switchgear terminations are suitable for the cable size.. Confirmation
e5f31b63-1b7a-451b-bc23-365801186f70 | checkpoint | 1.09 Verify that visible cable bends meet or exceed manufacturer's minimum published bending radius. Witness
df224a79-54bf-4324-ad63-f19a7eefa286 | checkpoint | 1.10 Inspect bolted electrical connections for high resistance using one or more of the following:
d56e7200-189d-5eb9-8902-87a2df55903f | note | - Use a low-resistance ohmmeter
d1fbb4fc-8233-51e4-a6cf-1599429b3ada | note | - Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer's published data. Hold Point
91d30d88-803c-469c-a5c3-8e85f400a123 | checkpoint | 1.11 Ensure Cable Terminations ITP's Template received and verified. Witness
62172691-e206-40db-aa26-334b6833fe43 | signoff | Signoff
e8310727-18e1-4e01-b0c7-36e6abb3da24 | section | Installation
42027abe-b106-4967-a215-08319ae53b26 | checkpoint | 2.01 Correct bend radii observed. Record cable bending radius. Witness
02450626-b2a6-42c1-b990-d560c0c8289d | checkpoint | 2.02 3-core breakout sheath installed at end of cable over sheath.. Confirmation
d73a7b12-fe94-481e-a815-bda8a97f4f8c | checkpoint | 2.03 For breakout outside termination chamber, verify gland plate is non-ferrous.. Confirmation
d1c23f7e-babe-4413-bd98-81a1b5277d32 | checkpoint | 2.04 Prepare cable gland plate, measured to the cable diameter (if not pre-cut).. Confirmation
413da495-c1f5-48c7-87d4-f272915ddab0 | checkpoint | 2.05 Ensure HV cables are supported/clamped as necessary. Confirmation
12ad42f6-0719-4c3a-99d8-3c312786f4f5 | checkpoint | 2.06 Ensure no weight/pressure on terminals/bushings. Confirmation
189fbba6-1e61-4d06-9d5b-3096796bbc71 | checkpoint | 2.07 Must be clamped prior to connected cable to bushing, to avoid damage to bushing.. Confirmation
a250bb15-ff03-44a0-be20-b98193860869 | checkpoint | 2.08 Ensure correct phase rotation is followed. Cable core identified by a label or marked. Monitor
87c27b5a-f30b-45c2-a080-7301422946cd | checkpoint | 2.09 Adjust the cut lengths of each cable to each phase, do not use a bar to pull and fit lugs.. Monitor
d26db76b-9e7e-4d71-82d1-bd95fdc35179 | checkpoint | 2.10 Unwind, braid and terminate the cable screen connect the cable to a suitably sized cable lug.. Confirmation
838f4d06-bb68-401e-ba30-8fa168bd5a3d | checkpoint | 2.11 Check all cable screens double-point bonded (connected at both ends).. Hold Point
a61a980b-8be3-445f-8664-99e9c9aa6d2f | checkpoint | 2.12 Prepare the cable termination in accordance with the instructions provided with the manufacturer's termination kit.. Monitor
d7501a97-08cf-4db7-a07c-005ee1cc43b6 | checkpoint | 2.13 Cable connections torqued to correct setting . Confirmation
55aee958-cf0b-426c-9e10-86d4ec4bb2dc | checkpoint | 2.14 Cable cores identified. Confirmation
2a4ad432-1540-49d0-9475-777983c2a860 | checkpoint | 2.15 Cable box connection screws are fastened according to specified torque. (M8 at 20Nm & M6 @ 8.5Nm). Confirmation
40db77d2-33d6-4eb8-a253-651a8585cc3e | checkpoint | 2.16 Photographic evidence taken and recorded. Hold Point
8e341c75-04e0-4068-bc36-8dc120b8780b | signoff | Signoff
ffb93a3e-8cf8-4a39-aed6-78f315011951 | section | Confirmation of the installation
b052677c-a5f9-48c5-9834-1e3295973d97 | checkpoint | 3.01 Cable termination completed and signed ITP received. Hold Point
f230799c-b164-4710-8674-59048435bd41 | checkpoint | 3.02 Correct bend radii observed. Record cable bending radius. Hold Point
55b51586-5550-4d9f-87d4-9efb9e63b6b8 | checkpoint | 3.03 Cable cores identified.. Hold Point
4379b0c3-eb48-4eed-a8d8-55b6329e1f60 | checkpoint | 3.04 Termination chamber closed, sealed and no tools or detritus left inside.. Hold Point
c93681cd-211b-437f-81c3-b144bae0e02a | signoff | Signoff
01cfe272-ca1a-42f9-a7a8-fb44d2f88c83 | checklist | LV Cable installation |  | LV Cable installation
7cd8c669-38ad-4cfd-8c6b-53a0c87c5840 | section | Pre-Installation
958f14b1-5451-4549-917c-ea8af6f4866b | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Hold Point
59999ac8-1ccc-4592-8d4d-bf3a7378244d | checkpoint | 1.02 Verify drawings latest revision. Hold Point
40fb89ac-f4d5-4f5a-a7ea-97a216130b84 | checkpoint | 1.03 Ensure ducting/trenches installed by others is checked prior to use. Hold Point
3ece9a89-9d0b-43c9-b566-12f62349faee | signoff | Signoff
f17d6699-92f1-4ae9-a2c6-c7e1a700fd71 | section | Installation
c7a8e545-7c83-4975-997b-af289edc708e | checkpoint | 2.01 Ensure cable drums are set up correctly and level - Jacks must be suitable for the load & size of drum. Witness
5470040e-b707-475c-9823-18aa066a6181 | checkpoint | 2.02 Ensure cable drums are set up in a location clear of personel and traffic. Confirmation
568f3292-1f06-4d7d-8277-1d0178d1412e | checkpoint | 2.03 Ensure any edges to trays are smooth and chamfered or protected. Confirmation
d275e1a4-4b0f-47a5-812f-6053f25f09b1 | checkpoint | 2.04 Minimise the amount of 'drag' across the ground when installing cables (ensure enough personnel are present). Confirmation
c5e2e4af-3e6b-4571-9227-353c4b485667 | checkpoint | 2.05 Ensure pulling tensions and bending radius' are not exceeded during installation. Confirmation
9f805928-f762-4df9-9fe2-b148ce9c5702 | checkpoint | 2.06 Ensure that cables are grouped in a manner to reduce magnetic interference where possible. Confirmation
00f0e53b-8a4b-4900-9d59-6272ee76e4d5 | checkpoint | 2.07 Ensure cables are supported along entire length. Confirmation
cb29be55-4ff0-45ed-ac1b-878dd2b9e6f5 | checkpoint | 2.08 Confirm each cable is labelled appropirately at either end and enough length left for termination. Monitor
f35f09f8-d50b-4318-9817-2a5d6187bbc0 | checkpoint | 2.09 Confirm no damage has occurred to cabling during installation. Monitor
13c0edf7-7d61-4b8c-a51e-c9206a407e29 | checkpoint | 2.1 Ensure ends of cables are taped/capped until terminations unertaken. Confirmation
73a2b287-a57f-46b5-b6f8-f141ef35804c | checkpoint | 2.11 Mark up "As built" drawings.. Monitor
cb67b1d5-95bc-412e-aa1d-09b2c9680887 | signoff | Signoff
1cf9fcf1-6132-4864-8ab0-890a3fbe7a77 | checklist | Manuals |  | Manuals
94c6583c-6233-4c9a-8eec-e504876fddfb | section | Information
fbdc1e2d-6fe9-4544-9e83-34983b0353df | checkpoint-no-value | Manuals Test Sheet
7d5ea74b-d69d-528d-bb6d-1bc3f63c6655 | note | Project: P.0597875 - AIAL WP1
69c67766-3ed9-597b-b14e-23f4c9487cb8 | textbox | Area
240d14cc-92af-5072-8a8f-849cfd89a3b1 | textbox | Item
a497fd2c-e3ef-4705-9d9c-b4de59a4a0f9 | checklist | PC69 Auxiliary Panel 1 |  | PC69 Auxiliary Panel 1
1e1f224c-f2ed-41c5-bace-b5d4e5339d3e | section | Pre-Installation
13763081-3d76-472c-aec8-658a6c8fe3bb | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure Hold Point
1c81cda9-702b-4102-8198-9ad37b1f175a | checkpoint | 1.02 Verify drawings latest revision Hold Point
9423bc8b-7ee6-4b11-abfa-e08517ecdcf9 | checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. Hold Point
dc99462c-acca-48ef-868d-68349c605236 | checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. Hold Point
700bf191-fe5d-4522-943e-ba633fcc4f2a | signoff | Signoff
6cf5de1f-1c1e-4c7e-bfeb-66816c027d5d | section | Installation
6b2d5ffe-b9c3-473d-8cd7-ad020426152b | checkpoint | 2.01 Ensure that the switchgear make/model is as per the design drawings. Confirmation
6245c85b-cdd7-4971-b6a1-4a7ef370168b | checkpoint | 2.02 Ensure that enclosure is relocated by the lifting hooks / points provided, the asset has been protected and no damage has been caused during movement. Monitor
fc227310-8d8c-4516-982f-2c090660a4e4 | checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required. Confirmation
973357df-5333-493f-baf1-cd948e1de263 | checkpoint | 2.04 Off-load the equipment and carefully move it into final position. Monitor
86204a54-d85e-4d9c-9398-919f278fe477 | checkpoint | 2.05 Install the switchgear over the appropriate wall space. Ensure to install the switchgear as per manufacturer's instructions. Confirmation
38018e09-e130-431b-a84e-3f6e4c44a8f8 | checkpoint | 2.06 Bolt down the switchgear assembly base frame with M12 bolts. Shim and grout if necessary to ensure level adjustment and alignment with adjacent panels. Confirmation
bb90265e-b915-48eb-8172-02bd5e476ee5 | signoff | Signoff
0421fb38-4f03-4d03-852d-5738a33c6faf | section | Switchgear Interconnection
6b46c38e-469a-4876-bf55-01085296427f | checkpoint | 3.01 Verfiy all switchgear interconnections have been made by the manufacturer and no on-site connections are required. Confirmation
a3a3b35a-f6fe-4cd9-9496-b70fd761ad55 | signoff | Signoff
58987fa8-5117-4217-8707-8730c47274b5 | section | Confirmation of installation & Documentation
409dcbb0-6320-49cf-82f4-02603c48d4e6 | checkpoint | 4.01 Confirm all accessories have been factory fitted. Confirmation
0dea23a3-ec6f-40c2-9fb9-08d3477c7bb2 | checkpoint | 4.02 Do Inspection after installation for complete switchgear assembly. Confirmation
2efa7d18-96d5-4942-8b42-54d52308adb6 | checkpoint | 4.03 Verify type main isolator rating Monitor
48c82d12-7d6d-404d-a9f2-762a9ba0efd0 | checkpoint | 4.04 Panel is ready for termination of Power cables & control cables. Holdpoint
b6ffd529-6790-4a78-9e7b-01465a3a650c | checkpoint | 4.05 Mark up "As built" drawings. Confirmation
7a381272-071d-4718-8f05-793f59c9c2ea | signoff | Signoff
267544c0-9245-414f-a109-b5670ed54347 | checklist | PC69 Auxiliary Panel 2 |  | PC69 Auxiliary Panel 2
150c04e9-d3bf-49ad-b337-b0f6e48bc69d | section | Pre-Installation
a851b377-d72a-463a-a015-6e0ca6b3cfa0 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure Hold Point
038101c2-f8aa-4aa6-b506-4aeb552f397f | checkpoint | 1.02 Verify drawings latest revision Hold Point
fa9be74e-b861-415e-b3f1-6d43fa6b5640 | checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. Hold Point
32346b9a-830b-4e66-be31-05edc1ebcfe5 | checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. Hold Point
3ebf6fa9-e9dc-4a2c-8639-774e51c0d8b2 | signoff | Signoff
4d79a883-4cd6-4807-9680-d36646c0bc72 | section | Installation
91d723f2-d289-42bc-978c-7011e2e8faf7 | checkpoint | 2.01 Ensure that the panel make/model is as per the design drawings. Confirmation
157ef87c-5c49-46e7-98f8-5713cf2302a7 | checkpoint | 2.02 Ensure that enclosure is relocated by the lifting hooks / points provided, the asset has been protected and no damage has been caused during movement. Monitor
170afa96-d49b-4815-b9b2-8960ff6e3805 | checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required. Confirmation
4f102f66-b02e-4102-ba5f-765d042c11b8 | checkpoint | 2.04 Off-load the equipment and carefully move it into final position. Monitor
4e1bc7f0-ee03-4981-ae5b-7f269ff4017c | checkpoint | 2.05 Install the panel over the appropriate wall space. Ensure to install the panel as per manufacturer's instructions. Confirmation
766e1e34-9bac-4b7b-950f-f0785621e44a | checkpoint | 2.06 Bolt down the base with M12 bolts. Shim and grout if necessary to ensure level adjustment and alignment with adjacent panels. Confirmation
a34a954f-c88a-4642-ba35-19606c946767 | signoff | Signoff
62a0b8b3-db4e-466f-9112-0bd9ffb6c1cf | section | Switchgear Interconnection
ecc9fe3e-a98b-4725-ba87-f380d63df01d | checkpoint | 3.01 Verfiy all switchgear interconnections have been made by the manufacturer and no on-site connections are required. Confirmation
dec533f1-34f9-44c4-983e-16a0389fbc8f | signoff | Signoff
0dcfd80c-d1a1-4dde-af7c-064582e60b78 | section | Confirmation of installation & Documentation
856e1496-fe86-4e7b-8f06-41dda4ca9e09 | checkpoint | 4.01 Confirm all accessories have been factory fitted. Confirmation
7d582314-5e7d-41d8-a4ea-67dcf599f133 | checkpoint | 4.02 Do Inspection after installation for complete switchgear assembly. Confirmation
2d7b5e03-6456-4fd4-b2dc-56119f35b608 | checkpoint | 4.03 Verify type main isolator rating Monitor
9e74f883-157e-4b23-84d9-44993a475115 | checkpoint | 4.04 Panel is ready for termination of Power cables & control cables. Hold Point
bb58113c-907e-4e24-8ddb-48a842ef80a8 | checkpoint | 4.05 Mark up "As built" drawings. Confirmation
a5188433-31fc-45aa-a676-2f7430ab43e7 | signoff | Signoff
454c90db-f7e0-450c-95ab-1ba4cf7e4e77 | checklist | Ripple plant installation |  | Ripple plant installation
87334dc8-a3d6-431d-bb5e-5e2b5faf61d7 | section | Pre-Installation
31544925-5e09-4ec1-9c1b-8ad748ec7f66 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure Hold Point
14ff2f23-e888-4d17-888e-33e71c7dddaa | checkpoint | 1.02 Verify drawings latest revision & all factory documents provided Hold Point
c3f3e2e3-78bb-456f-a26c-0540fa147618 | checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. Hold Point
565b10df-08ee-4217-bc4e-751e7cf67d73 | checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation. Hold Point
d5be64f1-4892-4526-8414-b195d8cb3458 | signoff | Signoff
6653764c-5e86-4477-9d21-f584defcfaf1 | section | Installation
87e4dc25-6eeb-4362-84ff-0d52dcb5c623 | checkpoint | 2.01 Ensure ripple plant make/model is as per the design. Confirmation
0a33992d-3c3f-47dd-99b0-a07b0621ba60 | checkpoint | 2.02 Ensure that R800 panel enclosure is relocated by the lifting hooks / points provided, the asset has been protected and no damage has been caused during movement. Confirmation
85b27c31-c0d2-40b6-93a9-e1c97b852484 | checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required. Confirmation
c6741502-c440-47ac-b33b-ede82e1cac2a | checkpoint | 2.04 Off-load the equipment and carefully move it into final position. Confirmation
924b1c55-db75-4b66-aa01-452127858911 | checkpoint | 2.05 Install the panel over the appropriate wall space. Ensure to install the panel as per manufacturer's instructions. Confirmation
6ef5769c-be10-49af-960e-db6061be8048 | checkpoint | 2.06 Bolt down the base with M12 bolts. Shim and grout if necessary to ensure level adjustment and alignment with adjacent panels. Confirmation
2d6fbc77-0926-4992-826b-9f1e29e87420 | checkpoint | 2.07 Ensure there is no mechanical stress on isolators of the coupling capacitors and isolating transformers. (Do not push, pull or lift the isolators. Confirmation
3239ae26-594f-408b-b615-94b3c2413680 | checkpoint | 2.08 The capacitor is designed for upright installation only. Other mounting positions must be discussed and agreed upon when placing the order. Confirmation
514982e5-8b78-44ba-83f8-701377c889ba | checkpoint | 2.09 To ensure proper cooling the distance between coupling capacitor units and if necessary to lateral walls should not be less than 70mm. Confirmation
c697d8bb-271b-4e18-8eda-bc59df1b6b42 | checkpoint | 2.10 The coupling capacitors should be installed in such a way that the name plate remains visible. Inputs and outputs are interchangeable. Confirmation
1863ffd6-4c89-4511-866c-9a229c314bf5 | checkpoint | 2.11 Connections to the capacitor terminals should be flexible. Confirmation
a5d3f29f-1c03-4fc7-88bc-93dc0315cfa5 | checkpoint | 2.12 The mounting of the tuning coils is options: veritical, horizontal or hanging. Double tuning coils must be installed vertically. Confirmation
19bc2e8b-db2f-4182-8211-bdad9c3ace42 | checkpoint | 2.13 Ensure the distance between tuning coilds have to be as big as possible. It must be possible to access the taps at all times. Confirmation
bcab42d1-d9d6-48f5-bb2d-56bcdc309443 | checkpoint | 2.14 The axis of the center tuning coil must be turned 90deg compared to the two exterior coils. Confirmation
5cd24fe0-d094-4f52-945b-130be4266cb0 | checkpoint | 2.15 The coils are marked with the direction of the magnetic field, the arrows of both the exterior coils must point in the same direction. Confirmation
f6ae302a-e905-4651-94ae-8f83ffc1ebe4 | checkpoint | 2.16 The isolating transformer must not be subjected to mechanical stress. Flexible connections are not essential. Confirmation
511d9684-cb97-4881-b955-95bc88a933fe | signoff | Signoff
6657540a-971e-4f4e-9fbb-608f820f99b0 | section | Switchgear Interconnections
a98d432f-c183-4c72-b469-34ee048824dd | checkpoint | 3.01 Connections to the capacitor terminals should be flexible. This can be achieved through suitable conductor routing or even better through flexible connecting elements. Confirmation
88f991c7-9349-4f4d-b80b-a85ee5c5e191 | checkpoint | 3.02 The outgoing connections of tuning coils are connected to the centre bolt. The connection nuts should be adjusted to the greatest possible distance from the movable strap to allow the setting to be readjusted with ease. Confirmation
6fa86ac3-90c7-46f7-8001-75fde9de269b | checkpoint | 3.03 After mounting, the accompanying warning signs are to be fixed at a well visible place. Confirmation
3cc06d35-fb83-40f2-8e8d-3b1585b3bc1a | checkpoint | 3.04 The isolating transformer low voltage side should be connected in such a way that the changeover to another connection can take place without difficulty. The neutral point of the low voltage side must not be connected. Confirmation
aaa7df7f-e12c-4370-b5dc-f1dc0e574bca | checkpoint | 3.05 Before putting into operation check the oil level with the oil level gauge and remove the transport gasket from the ventilator cap. Confirmation
8dfd9bcd-f18a-4c8c-8569-f962700fc98e | signoff | Signoff
7fce6bf6-cc84-4a22-bd3b-98bc29030022 | section | Confirmation of the installation
91d6a763-fb42-4119-82f6-946053adc6b0 | checkpoint | 4.01 Ensure the all components of Ripple plant are earthed to the earth studs. Hold Point
ac1c83ce-d902-4f5b-b72c-be087bbf861c | checkpoint | 4.02 Manufacturers rep sign off on completion of installation. Hold Point
fe5f0eb6-7ad9-44f1-a07d-6a257795d94f | checkpoint | 4.03 Ensure Landis+Gyr Test results and AS-Built drawings are received and verified. Hold Point
962c0785-37c0-4eaf-b6cc-5c53d5e3e1a8 | signoff | Signoff
d2cf93e3-9417-4839-89ec-74d9a2589858 | checklist | ROI |  | ROI
7f6b7a4f-f02b-4e03-aad2-7980c6eea005 | section | Information
325d046e-f08f-4e52-921f-f7db2bd73fd8 | checkpoint-no-value | ROI
ffab111c-c5a9-56eb-9452-db9b64e43d1c | note | Project: P.0597875 - AIAL WP1
4cae6e4f-4df3-5653-8d31-d773c26d33af | textbox | Area
e81cb24d-b597-5d02-906a-eb4e065ef6f2 | textbox | Item
441e1dd5-3106-413a-bc7c-c86833eb8d3c | checklist | Switchgear Inspection |  | Switchgear Inspection
18a6ea72-a329-4b60-a953-28e3f11d4655 | section | Inspection
146b87aa-e6c4-4a0e-a33b-8253d529eac4 | checkpoint | 1.01 Verify nameplate and other markings. Confirmation
b448d629-5a25-4cd7-8f89-6cac73933c37 | checkpoint | 1.02 Review manufacturer's drawings and schematics. Ensure that switchgear matches manufacturer's drawings and client specifications. Confirmation
7a85d0b3-3d5e-4f37-a03a-a944514a7580 | checkpoint | 1.03 Inspection for physical damage (dents & scratches), panel is true and square. Confirmation
fdca510a-3aa8-450a-84dc-4ec18d537597 | checkpoint | 1.04 Ensure that free issued switchgear is suitable for temporary building arrangments and fit for overall design intent.. Confirmation
b19a47e9-155e-44ff-b394-e8e3de307174 | checkpoint | 1.05 External & internal paint work is the specified colour and is clean and unblemished. Confirmation
d16393d0-6441-4905-accb-b15ad7c4f6a7 | checkpoint | 1.06 GPS location captured (if required). Confirmation
a036909c-a374-4bb4-8949-e317223998da | checkpoint | 1.07 Verify the end panel and rear panels are fitted correctly. Confirmation
3504ac8a-b183-46cc-9785-11bd20ef6754 | checkpoint | 1.08 Photographic evidence taken and recorded. Confirmation
503a614e-326c-45de-8ef2-ad04a82f5542 | checkpoint | 1.09 Verify earth bars are fitted and connected as required. Confirmation
7cdaac76-6505-4f47-b3cb-9d68fbbbb517 | checkpoint | 1.1 Correct number of door hinges and are hinged on the correct side. Confirmation
9cda12ea-e763-4fbc-b21c-fde674393813 | checkpoint | 1.11 Door handles and latches operate correctly and smoothly. Confirmation
53a69b13-0797-42fc-b0a6-8507048693aa | checkpoint | 1.12 Doors are mounted square, level, and parallel with each other and to the side frames. Confirmation
3963bffd-2048-4209-a19a-2d2983a5e346 | checkpoint | 1.13 Door locks are fitted correctly, and the correct key type is used. Confirmation
062ce0b5-fbca-405e-8f1b-816fb1eea169 | checkpoint | 1.14 Correct number of keys are provided with the cabinets. Confirmation
83ecf8f2-5f38-4466-808f-d87f3892f110 | checkpoint | 1.15 Door seals are fixed in place and continuous. Confirmation
b0ed87a7-4b44-4cc7-803c-87535fb08cc6 | checkpoint | 1.16 Doors are unobstructed in opening and enough clearance is provided. Confirmation
d9df96c0-f884-4816-999c-5bb9e9509a2e | checkpoint | 1.17 All mounting bolts/nuts/riv-nuts fitted and tight. Confirmation
19f58afe-223e-44c7-8b4d-9836084575bd | checkpoint | 1.18 All edges de-burred and holes clean. Confirmation
11a6b477-2b88-44b4-b1d1-cc5adc3a431d | checkpoint | 1.19 Ensure cabinet clean of any swarf. Confirmation
cccca8b5-8278-40b4-a5bc-50d3fe995f69 | checkpoint | 1.20 Verify all control fuse types, ratings and condition. Confirmation
fb0bdd44-0214-4452-9316-0324c40d2e03 | checkpoint | 1.21 Verify circuit breaker rating and condition. Confirmation
2f559617-c167-4ee0-a7ef-4518d2a5d06a | checkpoint | 1.22 Check assembly alignment, levelness and tightness. Confirmation
1d9b51f1-1381-43d8-a134-d3568c5fdc72 | checkpoint | 1.23 Photographic evidence taken and recorded. Confirmation
11998799-6f93-4a29-baaa-cc25a602e261 | checkpoint | 1.24 Ensure circuit breakers, CTs and VTs are installed in correct compartment . Confirmation
84288ceb-9bb3-4dc9-ab10-9f79721fd1f3 | checkpoint | 1.25 Check CTs/VTs rating and conditions. Record CT & VT ratio. Monitor
1aad3cb3-ab29-4f44-b248-5a2ceaff3ca0 | checkpoint | 1.26 Protection relays make and model matches manufacturer drawings. Record in the notes. Monitor
72e967dd-720a-40f6-be2f-cc56345124de | checkpoint | 1.27 Inspect bus for physycal damage, missing insulation, connections at joints. Confirmation
20a0606c-01a4-41f7-afa6-b76fb6524a9f | checkpoint | 1.28 Check condition of all insulation, especially for, damage, cracks, signs oftracking or blistering and any defects. Monitor
1045c71f-8811-4430-9843-4b5915c7cf1a | checkpoint | 1.29 Check that all wiring duct covers are fitted. Confirmation
3b55823a-36c4-4d59-9260-2a945166f7d0 | signoff | Signoff
6d76466d-b546-4f06-9b64-0fced380a7d1 | checklist | Switchgear Installation |  | Switchgear Installation
df5079f4-ab60-4b73-b82e-920b0f150132 | section | Pre-Installation
a60f2088-61af-4fd5-b81f-6855fd6500d6 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Hold Point
fad1fa1a-23e7-4ed9-ac20-983f0838cac2 | checkpoint | 1.02 Verify drawings latest revision & all factory documents provided. Hold Point
58c5eec5-1c55-433a-99e6-da700d20cd8d | checkpoint | 1.03 Confirm delivery & unloading plan for the switchgear is approved. . Hold Point
6c348941-5127-457b-9085-f7f5358dd297 | checkpoint | 1.04 Make sure traffic management plan is approved if required during transportation.. Hold Point
3d5789e7-57c1-4c09-a54c-378ae310f435 | signoff | Signoff
ab57e8a2-d641-4664-857e-107640e42147 | section | Installation
9dcac08c-4869-4c9d-bc98-9dcebfa907b8 | checkpoint | 2.01 Ensure the 11kV switchgear is Schneider manufacture. Confirmation
f9dee7ff-2983-47c7-bd0e-35789984c432 | checkpoint | 2.02 Uplift the switchgear and its ancillary items from the storage facility. Confirmation
5c38040e-fd35-4036-bcf9-10c94898a523 | checkpoint | 2.03 Ensure to provide lifting equipment at the site and obtain traffic management plans if required. Confirmation
4e2eb115-3f14-444f-87ca-884362a07550 | checkpoint | 2.04 Deliver the equipment as separate panels. Off-load the equipment and carefully move it into the switchroom. Confirmation
0270eed3-2d65-414e-9f39-f00d6b315fbd | checkpoint | 2.05 Ensure switchroom floor is as per switchgear installation manual and drawing requirement. Confirmation
3f9d41a7-aa23-4caa-8fc8-0b803e4e928c | checkpoint | 2.06 Install the switchgear over the appropriate floor opening, as shown in the substation layout drawings. Ensure to install the switchgear as per manufacturer's instructions. Confirmation
06bcc6e3-d4a9-40d4-bd95-59e70adad31e | checkpoint | 2.07 Ensure the installed rails/plinth are entirely suitable (levels, positions, etc) for mounting the switchgear. Confirmation
4ca8d542-c1f4-4d70-ad5f-d4e2231192a1 | checkpoint | 2.08 Confirm fixings are suitable and all seismic requirements met. Confirmation
0eef73bb-2708-46ff-8935-33a980e9fa49 | checkpoint | 2.09 Bolt down the panels as per manufacturer's instructions and under the supervision of a Schneider representative. Ensure the panels are accurately positioned due to minimal tolerances of ±1mm per meter and ±2mm for the entire length of the switchboard. Confirmation
15fa320e-ba91-41ea-9003-28300803bc9b | signoff | Signoff
e77d7549-5d1f-49ac-aa85-18a53a464138 | section | Switchgear Interconnections
5624cf56-8141-4f18-a780-4cb33074a54e | checkpoint | 3.01 Make sure all necessary secondary connections are made in line with the relevant schematic diagrams. Confirmation
ce95f7de-160d-4bd9-a04f-c269c2efeea3 | checkpoint | 3.02 Ensure to supply and install all the AC, DC, CT, VT, intertripping, SCADA and comms cabling to the switchgear panels as per the design drawings and cable schedules provided. Confirmation
ec38bea4-a127-4a8e-9cdf-32293bbe5ed0 | checkpoint | 3.03 Make sure all free-issued communication cables between relays are installed. Confirmation
b0eb479f-349a-4ffb-83a9-84fb25cc40d5 | signoff | Signoff
b6c9b1fe-42ef-4476-ad68-8dce5d12bfbd | section | Confirmation of the installation
f90a822c-d330-4ee9-998b-ce28741fd952 | checkpoint | 4.01 Manufacturers rep sign off on completion of installation. Hold Point
40587eee-892f-4f91-9b72-4d4d6e34b1e4 | checkpoint | 4.02 Ensure Schneider Test results and AS-Manufactured drawings are received and verified. Hold Point
e08fe36b-40d6-48a1-aac7-bdad5d6a8fb3 | signoff | Signoff
09b02d7b-e541-47f1-aa31-cbe9858062ef | checklist | Transformer Installation |  | Transformer Installation
da1e6486-415e-4a32-bc89-22c64ccda8a1 | section | Pre-Installation
87bb7fa1-2156-4464-8544-8a1455f36021 | checkpoint | 1.01 All staff briefed on safety requirements and installation procedure. Ensure position and orientation of the Transformer is understood and agreed. Confirmation
5a6b14e1-60a6-4306-bc93-15660174a3bc | checkpoint | 1.02 Transformer site agreed by the client. Ensure the base/foundation has attained required MPA strength . Hold Point
255dae8c-d34e-418f-89f9-9c7145bef64a | checkpoint | 1.03 Verify drawings latest revision. Confirmation
4088f612-71ed-4d8d-ae64-9f37ebd83017 | checkpoint | 1.04 Confirm nameplate data matches drawings/design. Hold Point
ce65529c-21e9-492d-8f9d-5d9c9571f79e | checkpoint | 1.05 Transformer Factory Acceptance Test (FAT) documents received from supplier. Confirmation
6ec691cf-1a0f-4ec0-be85-28e367ecc0fe | checkpoint | 1.06 Confirm delivery & unloading plan for the transformer is approved. . Hold Point
4fee7ad8-885c-4f84-aaf4-4cae699f1080 | checkpoint | 1.07 Make sure traffic management plan is approved if required during transportation.. Hold Point
fa82ee9e-a0e5-4638-8a69-107d54afa7f4 | checkpoint | 1.08 Inspect transformer and confirm no corrosion or damage to core, base or enclosure. Hold Point
54c6029c-caa4-4036-a4b5-541f4dadf5f5 | checkpoint | 1.09 Confirm oil level are adequate . Hold Point
c9b6f263-5efe-4c24-a870-0b39a35b12a3 | checkpoint | 1.1 Baseline oil sample taken for Dissolved Gas Analysis (DGA) (if required by client). Confirmation
426d26b7-34dc-4a92-b250-e460b9cf4831 | checkpoint | 1.11 Verify the bushings are clean. Witness
27058bde-24b1-48ad-b93a-1ae76530874d | checkpoint | 1.12 Confirm the transformer compound has been constructed to requirements and concrete structure is adequately cured and ready for load.. Hold Point
a76c48d1-1ddd-49d2-9726-fcf02d5fd49c | checkpoint | 1.13 Verify the HV and LV orientations. Witness
b1ccd77d-649c-4abe-803a-7af339f5821f | checkpoint | 1.14 Lift plan produced and reviewed by OMX and client where applicable. Hold Point
ff2f3a51-7994-4dca-a389-75953ca0ec41 | signoff | Signoff
ca4d3750-b046-4774-90b9-fab02dc64237 | section | Installation
ad542dcb-8c42-4ec7-addd-d0f5da5f17d3 | checkpoint | 2.01 Attach lifting hooks to the crate and perform all lifts using minimum two slings and lifting device, maintaining equal distance between the lifting hooks.. Monitor
5c47c175-b593-4831-a953-24215d9d9915 | checkpoint | 2.02 Off-load the equipment and carefully position into the compound. Verify the orientation of the HV and LV. Ensuring the alignment of any rigid cable duct (if applicable). Monitor
d9d39ba1-3dbf-4ef0-9220-f01b0522df86 | checkpoint | 2.03 Secure the transformer assembly base frame to the allocated site. Shim and grout if necessary to ensure level adjustment.. Confirmation
b9026800-a948-4288-97e3-dad751cd2cfc | checkpoint | 2.04 Confirm fixings are suitable and all seismic requirements met. Monitor
dab031a0-1441-4292-af20-9649a116aa56 | checkpoint | 2.05 Ensure clean terminal surface, winding casing and enclosure. Confirmation
78ee7805-00c7-471a-8544-2d0ebeb8fa5a | checkpoint | 2.06 Ensure all bolts tightened as specified including: holding down bolts, enclosure fixings, earth bonding connections, gland plates.. Confirmation
3e68d470-dd5a-4728-b12c-4fa1db9c1984 | checkpoint | 2.07 Photographic evidence taken and recorded. Confirmation
1245edf9-37ac-4e1c-9a83-e243bdad0fa6 | signoff | Signoff
f0a9ea9c-a801-4d8c-8ae2-5a2a285336c2 | section | Post Installation
cc475854-48f3-4f11-b43b-f46059a3c412 | checkpoint | 3.01 Inspect anchorage, alignment, and earthing. Confirmation
e92c7c15-d009-4de1-a346-acd36a51a8e5 | checkpoint | 3.02 Inspect bolted electrical connections for high resistance using one or more of the following:
4b6ea0a3-fcb0-5d87-83a8-c90ee279a986 | note | - Use a low-resistance ohmmeter
022101e5-32bc-5516-8153-81097323cbf4 | note | - Verify tightness of accessible bolted electrical connections by calibrated torque-wrench method in accordance with manufacturer's published data. Hold Point
b163e640-3e3e-4044-88b1-c93b8b9828d4 | signoff | Signoff