## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | ITP-HA0423-ELE-003 - Underground Ducts Below Slab | itp |  |  |  |  | ITP-HA0423-ELE-003 - Underground Ducts Below Slab - Rev C
section | 4. Process
checkpoint | 01 - Delivery inspection of HDPE ducts and fittings
label | Frequency - Each delivery
label | Spec/standard - AS/NZS 4130 / Manufacturer CoC 7.3.3.3 12.3.3, 12,3.4
label | Acceptance Criteria - Correct SDR, diameter and undamaged
label | Measuring Devices - Visual and CoC
label | Reporting Format - Delivery slip / CoC
label | HCL - R
label | SC - Sub
label | Consult - R
label | Hold Points Sign off - N/A
label | Remarks - Material CoC matches spec; no damage No damaged packing material.
checkpoint | 02 - Welder qualification check
label | Frequency - Before work start
label | Spec/standard - NZ Certifications; standards and industry training
label | Acceptance Criteria - Accept / reject
label | Measuring Devices - Document review
label | Reporting Format - Welder Qualification
label | HCL - R
label | SC - I
label | Consult - R
label | Hold Points Sign off - Hold Point
label | Remarks - Welder certification reviewed and approved prior works Hawkins- ITP-000061
holdpoint | HOLD POINT
checkpoint | 03 - Trenches and routes inspections
label | Frequency - Per section
label | Spec/standard - Drawings Spec 4.23.2/7.3.4.5/7.3.4.8
label | Acceptance Criteria - Installed as per project drawings and specifications
label | Measuring Devices - Visual
label | Reporting Format - Site coordination
label | HCL - I
label | SC - I
label | Consult - S
label | Remarks - Suitable route and bend allowances
checkpoint | 04 - Duct alignment check
label | Frequency - Per section
label | Spec/standard - Project drawings / layout 4.23.2
label | Acceptance Criteria - Installed as per drawing
label | Measuring Devices - Visual
label | Reporting Format - NA
label | HCL - M
label | SC - I
label | Consult - R
label | Remarks - No excessive bends or misalignments
checkpoint | 05 - Inspection of duct cleanliness and joint
label | Frequency - Before welding
label | Spec/standard - ISO 13954 5.10.3
label | Acceptance Criteria - Ends scraped, dry, and clean
label | Measuring Devices - Visual
label | Reporting Format - OMX Quality check sheet
label | HCL - M
label | SC - I
label | Consult - R
label | Remarks - Free of debris, scratches, moisture
checkpoint | 06 - Fusion setup – pipe end scraping, machine check
label | Frequency - Each weld
label | Spec/standard - ISO 13954 / ISO 13955
label | Acceptance Criteria - Scraping complete, scan barcode
label | Measuring Devices - Scraper / EF machine
label | Reporting Format - OMX Quality check sheet
label | HCL - M
label | SC - M
label | Consult - R
label | Remarks - Pre-weld approved by supervisor before fusion
checkpoint | 07 - Electrofusion weld execution
label | Frequency - Each weld
label | Spec/standard - ISO 13955 12.4.6. 12.5.2
label | Acceptance Criteria - Parameters met; uniform bead
label | Measuring Devices - EF machine logger
label | Reporting Format - Fusion log / OMX Quality check sheet
label | HCL - M
label | SC - Sub
label | Consult - R
label | Remarks - Fusion data logged and bead visually compliant Weld number time and date next to weld.
checkpoint | 08 - Post Weld visual inspection and cooling
label | Frequency - Each weld
label | Spec/standard - ISO 13955 / 13956
label | Acceptance Criteria - Bead uniform, cooled per spec
label | Measuring Devices - Visual
label | Reporting Format - OMX Quality check sheet
label | HCL - s
label | SC - R, Sub
label | Consult - R
label | Remarks - Cooling time respected; weld integrity confirmed.
checkpoint | 09 - Weld traceability and documentation
label | Frequency - Each weld
label | Spec/standard - 7.3.4.9
label | Acceptance Criteria - Barcode and weld ID logged
label | Measuring Devices - Log Sheet
label | Reporting Format - OMX Quality Check sheet
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Log completed and ID matched field location
checkpoint | 10 - Post Weld inspection
label | Frequency - Project Scope
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-001 12.5.2
label | Acceptance Criteria - CCTV footage of below ground ducting, duct contains no debris or penetrations that could damage cable sheath when pulled
label | Measuring Devices - CCTV
label | Reporting Format - Video
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Submission of CCTV footage before handover
checkpoint | 11 - Electro fusion welder calibration
label | Frequency - Project Scope
label | Spec/standard - As per manufactures specification
label | Acceptance Criteria - Electro fusion welder calibration certificate
label | Measuring Devices - Calibration certificate
label | Reporting Format - Certificate
label | HCL - S
label | SC - Sub
label | Consult - R
label | Remarks - Submission of calibration certificate before handover
checkpoint | 12 - Draw Cord
label | Frequency - Each conduit
label | Spec/standard - 12.3.8
label | Acceptance Criteria - 5 kn
label | Measuring Devices - N/A
label | Reporting Format - QC checklist/ photograph
label | HCL - M
label | SC - Sub
label | Consult - R
checkpoint | 13 - Hot Bending of HDPE Ducts
label | Frequency - Direction change
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-001 7.3.4.5
label | Acceptance Criteria - Minimum bending radius of 2m
label | Measuring Devices - Measuring tape
label | Reporting Format - QC checklist
label | HCL - I
label | Remarks - Heat apply using controlled hot air: duct support during bending. Cool down in place to retain shape
checkpoint | 14 - Installation of tracer wire
label | Frequency - Each installed duct
label | Spec/standard - DP001-MMD-SPC- EL-Z-Z-0017.3.3.11
label | Acceptance Criteria - Wire securely fixed on top of duct, continuous, accessible at both ends
label | Reporting Format - QC checklist Photograph
label | HCL - M
label | SC - T
label | Consult - R
label | Remarks - Tracer wire to be installed above duct, secured at 3m intervals. Ends terminated in accessible pits or boxes
checkpoint | 15 - Installation of Warning Tape and Polymeric Cover (Mag slab) during Backfilling
label | Frequency - Each installed duct
label | Spec/standard - AS/NZ3000. 2018
label | Acceptance Criteria - Install 300mm above top of duct.
label | Measuring Devices - Tape measure, visual check
label | Reporting Format - QA checklist / photograph
label | HCL - M
label | SC - W
label | Consult - S
label | Remarks - Materials supplied by Omexom, installation by civil contractor.
label | ○ Hold point required prior to backfilling. Supplier to verify delivery and provide installation guidance. Coordination required to ensure correct placement and documentation.
checkpoint | 16 - Pit to Duct Jointing Process
label | Frequency - Each duct at each pit
label | Spec/standard - DP001-MMD-SPC-EL-Z-Z-0017.3.3.12
label | Acceptance Criteria - Manufacturer’s installation guidelines and project specifications
label | Measuring Devices - Secure, watertight connection between duct and pit; no gaps or misalignment
label | Reporting Format - Visual check, QA checklist / photograph
label | HCL - S
label | SC - R
label | Consult - S
checkpoint | 17 - Coordination with Waterproofing and Concrete Encasing
label | Frequency - At each interface with waterproofing or encasement
label | Spec/standard - MMD DP Buildings Elec Spec July 2024 7.3.3.12
label | Acceptance Criteria - IFC drawings and Sika Details (by others)
label | Measuring Devices - N/A
label | Reporting Format - By others
label | HCL - S
label | SC - R
label | Consult - R
label | Remarks - By others
section | 5. Document Deliverables (The documents listed below shall be completed and compiled during the course of the construction)
checkpoint | Delivery Slip / Certificate of Conformance (CoC)
label | For delivery inspection of HDPE ducts and fittings.
checkpoint | Welder qualification checks.
checkpoint | Site Coordination Reports
label | For trenches and routes inspections.
checkpoint | QA Reports
label | For duct alignment checks.
checkpoint | Calibration Certificates
label | For electrofusion welder calibration.
checkpoint | Log Sheets
label | For weld traceability and documentation.
checkpoint | CCTV Footage
label | For post-weld inspection.
section | 6. Distribution Records
checkpoint | Distribution Records
holdpoint | Signature