## Table 1
ISSUE DATE 19TH August 2019 |  |  | AUTHORISED BY CHRISTOPHER CARROLL SNR |  |  |  |  | ISSUE NO V2
INSPECTION TEST PLAN: |  | SWITCHBOARD INSTALLATION – FINAL INSPECTION
SWITCHBOARD (IE. TX/MSB/MDB/DB |  |  |  |  | CLIENT: | BUILT
[5 empty] | PROJECT: | WESTERN PLAZA UPGRADE AFC & DPH
[5 empty] | PROJECT NO: | A5964
LOCATION/AREA: |  |  |  |  | DOCUMENT REF:
INSTALLATION AND ITP COMPLETED BY: |  |  |  |  | SPECIFICATION REF
ITEM | ACTIVITY STEP DESCRIPTION |  |  | ACCEPTANCE CRITERIA |  |  | RESPONSIBLITY |  | COMPLETION
[9 empty] | YES | NO | N/A
1 | Switchboard installation visual inspection |  |  | - Check for visible internal/external damage - Correct installation, level & mounting is satisfactory, - Segregation and clearances from other services are satisfactory -as per AS/NZS 3000 Standard |  |  | -TYRONE |  | ☐ | ☐ | ☐
2 | Doors, cable access, live parts access |  |  | -locks installed and in working condition -earthing to doors and escutcheons installed (if required) -ensure all insulated barriers, doors and escutcheons are installed and protection is adequate -as per switchboard drawings and regulatory requirements |  |  | -TYRONE |  | ☐ | ☐ | ☐
3 | MEN point |  |  | - installed and clearly identified (if applicable) |  |  | -TYRONE |  | ☐ | ☐ | ☐
4 | Cable glands/cabling switchboard entry |  |  | -switchboard meets required IP rating -sizes and type are correct/acceptable -no undue stress on glands/cable or gland lock ring -glands tightened/entry points sealed/completed -pole fillers installed/live parts protected |  |  | -TYRONE |  | ☐ | ☐ | ☐
5 | Metering and current transformers (CT)’s |  |  | - Check meter is configured to the installed CTs ie. ratios are correct. -Meter readings and communication to BMS have been checked and verified. - VTs and CT links are removed. |  |  | -TYRONE |  | ☐ | ☐ | ☐
6 | Identification, labelling & signage |  |  | - completed and correct as per regulatory requirements and switchboard drawings |  |  | -TYRONE |  | ☐ | ☐ | ☐
7 | Circuit schedule/switchboard legend |  |  | - Switchboard legend (if applicable) has been printed and installed inside door. No pen or pencil markup on the legend ie. all completed - or changes actioned for reprint and reinstallation. |  |  | -TYRONE |  | ☐ | ☐ | ☐
8 | Final Check |  |  | - Switchboard left clean and tidy - doors are installed and closed |  |  | -TYRONE |  | ☐ | ☐ | ☐
9 | Identify any outstanding or rectification works required |  |  | -provide details in the comments below |  |  | -TYRONE |  | ☐ | ☐ | ☐
10 | COMPLETION POINT: Installation completion |  |  | -all items above have been completed -any outstanding items, please make comments below for future action by undersigned -Completed ITP provided to site manager/ supervisor/commissioning manager |  |  | INSTALLED AND CHECKED BY TYRONE INSTALLER/REPRESENTATIVE:
NAME:
SIGN:
DATE:
11 | ITP/OM Manual documentation |  |  | -Final check of switchboard has been completed. - Issues/defects have been closed out/ documented for action. -All documents have been submitted |  |  | - TYRONE COMMISSIONING MANAGER/ SITE SUPERVISOR/ MANAGER: |  | ☐ | ☐ | ☐
COMMENTS: | [6 empty] | CHECKED APPROVED BY TYRONE COMMISSIONING MANAGER/ SITE SUPERVISOR/ MANAGER:
NAME:
SIGN:
DATE:
ISSUE DATE 19TH August 2019 |  |  | AUTHORISED BY CHRISTOPHER CARROLL SNR |  |  |  |  | ISSUE NO V2
Direction Looking: |  |  |  |  | Direction Looking:
Direction Looking: |  |  |  |  | Direction Looking:
ISSUE DATE 19TH August 2019 |  |  | AUTHORISED BY CHRISTOPHER CARROLL SNR |  |  |  |  | ISSUE NO V2
Direction Looking: |  |  |  |  | Direction Looking:
Direction Looking: |  |  |  |  | Direction Looking:
ISSUE DATE 19TH August 2019 |  |  | AUTHORISED BY CHRISTOPHER CARROLL SNR |  |  |  |  | ISSUE NO V2