## Table 1
Inspection & Test Checklist ITC: 4A MAINS AND SUBMAINS
Client: | John Holland Group |  |  | Project Name: |  | Shoalhaven Hospital Redevelopment |  |  |  |  | Job No: | NEC00140 |  | Sheet No:
Contract Manager: |  | Brett Lavarto |  | Project Manager: |  | Michael McGeehan |  |  | Site Supervisor: |  | Andrew Cairns |  |  | Date:
Check Authorised By: |  |  |  | Signature: |  |  |  |  | Check Delegated To: |  |  |  | Signature:
Submain Details
Area | [6 empty] | Drawing No.
From | [6 empty] | To
Cable No. |  |  | Cable Type |  |  |  | Cable Size |  |  |  | Length |  |  | Cores
MCCB Model |  |  | Rating (A) |  |  |  | Trip Unit |  |  |  | Trip Setting (A)
Visual Inspections (AS/NZS 3000)
1 | Visually Check Cable is - | [12 empty] | ✓
| Provided with adequate support, suspension and fixings? | [12 empty] | □
| Suited for the intended use? | [12 empty] | □
| Protected against mechanical damage, enviromental and other external influnece by enclosure? | [12 empty] | □
| Is the cable the correct type and size? | [12 empty] | □
| Is the cable terminated at both ends? | [12 empty] | □
| Are the connections tight, correct tension and marked? | [12 empty] | □
| Is the cable free of damaged? | [12 empty] | □
| Is the cable and terminations correctly labeled? | [12 empty] | □
Pre Energisation Checks (AS/NZS 3000)
| Bolt Tension Check/Bolt Lined and Tension noted? | [12 empty] | PASS | FAIL
| NM | [12 empty] | □ | □
2 | Earth Continuity (Value must be less than 0.5 ohms) | [12 empty] | PASS | FAIL
| Earth Size |  | FROM |  | TO |  |  | Point to Point Reading |  |  |  | Ω
[14 empty] | □ | □
3 | Insulation Resistance Test (AS/NZS 3000) | [12 empty] | PASS | FAIL
| RED TO WHITE |  |  |  | WHITE TO BLUE |  |  |  |  | BLUE TO RED |  |  |  | □ | □
| RED TO BLACK |  |  |  | WHITE TO BLACK |  |  |  |  | BLUE TO BLACK
| RED TO EARTH |  |  |  | WHITE TO EARTH |  |  |  |  | BLUE TO EARTH
4 | Polarity Test ✓ | [12 empty] | PASS | FAIL
| RED TO RED |  | WHITE TO WHITE |  | BLUE TO BLUE |  |  | BLACK TO BLACK | [5 empty] | □ | □
5 | Fault Loop Impedance (If Applicable) | [12 empty] | PASS | FAIL
| Cables have been installed as per design calculations. | [12 empty] | □ | □
Note, if FAIL seek design clarification to adjust circuit breaker tripping curve characteristics.
Post Engerisation Checks (AS/NZS 3000)
6 | Phase Rotation
| Clockwise → | [5 empty] | □ | Anti Clockwise ← | [6 empty] | □
7 | Voltage Checks (AS/NZS 3000) | [12 empty] | PASS | FAIL
| RED TO WHITE |  |  |  | WHITE TO BLUE |  |  |  |  | BLUE TO RED |  |  |  | □ | □
| RED TO BLACK |  |  |  | WHITE TO BLACK |  |  |  |  | BLUE TO BLACK
| RED TO EARTH |  |  |  | WHITE TO EARTH |  |  |  |  | BLUE TO EARTH
Test Equipment |  | Brand/Model |  |  | Serial No. |  |  |  | Calibration Due |  | Tester |  |  | Date
Multimeter
Insulation Resistance Tester
Phase Rotation Meter