## res
type | name | values | prefix | postfix | usage count | user addable | template name | Resource Id
checklist | Drawing Register (For Construction) | [5 empty] | ITC - (1) Drawing Register (For Construction)
section | Details
checkpoint-no-status | DRAWING REGISTER
date | Date:
textbox | DRAWING No.
textbox | DRAWING TITLE
textbox | REVISION / ISSUE
checkpoint-no-status | DISTRIBUTION:
textbox | SITE OFFICE
textbox | SITE
textbox | NCR No:
checkpoint | FINAL ACCEPTANCE:
textbox | HEYDAY GROUP (REPRESENTATIVE)
textbox | CLIENT (REPRESENTATIVE)
textbox | AUTHORITY (IF APPLICABLE)
holdpoint | Signoff
checklist | Level / Area: | [5 empty] | ITC - (2) Temporary Wiring-Temporary DB's
section | Details
checkpoint | EQUIPMENT LOCATED CORRECTLY
checkpoint | EQUIPMENT SECURE/BOLTED DOWN
checkpoint | WIRING INSTALLED CORRECTLY
checkpoint | WIRING MECHANICALLY PROTECTED
checkpoint | POLE FILLERS INSTALLED
checkpoint | ESCUTCHEON / COVERS CHECKED
checkpoint | LOCKABLE COVERS AND PADLOCKS
checkpoint | EQUIPMENT TESTED AND TAGGED
checkpoint | TEMPORARY BOARD NUMBERED
checkpoint | BOARD LABELLED FOR SOURCE OF SUPPLY
checkpoint | FINAL ACCEPTANCE:
textbox | HEYDAY GROUP (REPRESENTATIVE)
textbox | CLIENT (REPRESENTATIVE)
textbox | AUTHORITY (IF APPLICABLE)
holdpoint | Signoff
checklist | Board Type or Number or Area: | [5 empty] | ITC - (3) Main and Distribution Panels
section | Details
checkpoint | ACCEPTANCE CRITERIA
checkpoint | MFG QA
checkpoint | DAMAGE
checkpoint | LOCATION TO DRAWING
checkpoint | EQUIPMENT TO DRAWING
checkpoint | CONNECTIONS INCOMING & OUTGOING BY HEYDAY.
checkpoint | NEUTRAL CONNECTIONS CORRESPOND
checkpoint | CORRECT EARTHING AND SOLIDLY FIXED
checkpoint | POLE FILLERS INSTALLED
checkpoint | ALL CABLE ENTRIES WITH ESCUTCHEON PLATES AND SEALS FITTED
checkpoint | BOARD SEALED AND LOCKED FOR SAFETY INC: FRONT AND REAR PANELS
checkpoint | LABELS AND SCHEDULE LIST CORRECT AND INSTALLED
checkpoint | FINAL ACCEPTANCE:
textbox | HEYDAY GROUP (REPRESENTATIVE)
textbox | CLIENT (REPRESENTATIVE)
textbox | AUTHORITY (IF APPLICABLE)
holdpoint | Signoff
checklist | MSB AND DB's | [5 empty] | ITC - (3A) MSB and DB's TEST Sheet
section | Submain Details as per ITC 4A
checkpoint-no-status | Details
textbox | Area
textbox | From
textbox | Cable No.
textbox | MCCB Model
textbox | Cable Type
textbox | Rating (A)
textbox | Drawing No.
textbox | To
textbox | Cable Size
textbox | Trip Unit
textbox | Length
textbox | Trip Setting (A)
textbox | Cores
section | 1 - Checklist - Visually Check Cable is -
checkpoint | Approved Factory Acceptance Test completed?
checkpoint | Switchboard is secure and ready for Consumer Main/Submain Installation
checkpoint | Consumer Main/Submain Installed?
checkpoint | Verify C/B Trip Settings are Correct.
checkpoint | Consumer Main/Submain Test has been completed as per Heyday ITC-4A
checkpoint | Are the connections tight, correct tension and marked?
checkpoint | Switchboard is ready to be energised?
section | 2 - Pre Energisation Checks (AS/NZS 3000)
checkpoint | Earth Continuity (Value must be less than 0.5 ohms)
textbox | Earth Size:
textbox | FROM:
textbox | TO:
textbox | Point to Point Reading:
textbox | Ω
section | 3 - BUSBAR Insulation Resistance Test (AS/NZS 3000)
checkpoint | RED TO WHITE
textbox | RED TO WHITE:
checkpoint | RED TO BLACK
textbox | RED TO BLACK:
checkpoint | RED TO EARTH
textbox | RED TO EARTH:
checkpoint | WHITE TO BLUE
textbox | WHITE TO BLUE:
checkpoint | WHITE TO BLACK
textbox | WHITE TO BLACK:
checkpoint | WHITE TO EARTH
textbox | WHITE TO EARTH:
checkpoint | BLUE TO RED
textbox | BLUE TO RED:
checkpoint | BLUE TO BLACK
textbox | BLUE TO BLACK:
checkpoint | BLUE TO EARTH
textbox | BLUE TO EARTH:
section | 4 - Post Energisation Checks (AS/NZS 3000)
checkpoint | Phase Rotation
bool | Clockwise →
bool | Anti Clockwise ←
section | 5 - Voltage Checks (AS/NZS 3000)
checkpoint | RED TO WHITE
textbox | RED TO WHITE:
checkpoint | RED TO BLACK
textbox | RED TO BLACK:
checkpoint | RED TO EARTH
textbox | RED TO EARTH:
checkpoint | WHITE TO BLUE
textbox | WHITE TO BLUE:
checkpoint | WHITE TO BLACK
textbox | WHITE TO BLACK:
checkpoint | WHITE TO EARTH
textbox | WHITE TO EARTH:
checkpoint | BLUE TO RED
textbox | BLUE TO RED:
checkpoint | BLUE TO BLACK
textbox | BLUE TO BLACK:
checkpoint | BLUE TO EARTH
textbox | BLUE TO EARTH:
section | Test Equipment
checkpoint | Multimeter
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date:
checkpoint | Insulation Resistance Tester
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date:
checkpoint | Phase Rotation Meter
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date:
checklist | MAINS AND SUBMAINS | [5 empty] | ITC - (4) Main and Submain
section | Details
checkpoint-no-status | Details
textbox | LEVEL
textbox | AREA
textbox | FED FROM
textbox | TO DB No
checkpoint | COMPLIES TO SPEC AND LATEST DRG
checkpoint | SIZE CORRECT
checkpoint | INSTALLED CORRECT
checkpoint | TERMINATED
checkpoint | TESTED AS PER ITC 4A
checkpoint | NOEW SUBMITTED TO COUNCIL
checkpoint-no-status | REMARKS/Submain ID
textbox | REMARKS/Submain ID:
checkpoint | FINAL ACCEPTANCE:
textbox | HEYDAY GROUP (REPRESENTATIVE)
textbox | CLIENT (REPRESENTATIVE)
textbox | AUTHORITY (IF APPLICABLE)
holdpoint | Signoff
checklist | MAINS AND SUBMAINS | [5 empty] | ITC - (4A) Mains and Submains Test Results
section | Details
checkpoint-no-status | Details
textbox | Area
textbox | From
textbox | Cable No.
textbox | MCCB Model
textbox | Cable Type
textbox | Rating (A)
textbox | Drawing No.
textbox | To
textbox | Cable Size
textbox | Trip Unit
textbox | Length
textbox | Trip Setting (A)
textbox | Cores
section | 1 - Visual Inspections (AS/NZS 3000) - Visually Check Cable is -
checkpoint | Provided with adequate support, suspension and fixings?
checkpoint | Suited for the intended use?
checkpoint | Protected against mechanical damage, enviromental and other external influnece by enclosure?
checkpoint | Is the cable the correct type and size?
checkpoint | Is the cable terminated at both ends?
checkpoint | Are the connections tight, correct tension and marked?
checkpoint | Is the cable free of damaged?
checkpoint | Is the cable and terminations correctly labeled?
section | 2 - Pre Energisation Checks (AS/NZS 3000)
checkpoint | Bolt Tension Check/Bolt Lined and Tension noted?
textbox | NM
section | 3 - Insulation Resistance Test (AS/NZS 3000)
checkpoint | RED TO WHITE
textbox | RED TO WHITE:
checkpoint | RED TO BLACK
textbox | RED TO BLACK:
checkpoint | RED TO EARTH
textbox | RED TO EARTH:
checkpoint | WHITE TO BLUE
textbox | WHITE TO BLUE:
checkpoint | WHITE TO BLACK
textbox | WHITE TO BLACK:
checkpoint | WHITE TO EARTH
textbox | WHITE TO EARTH:
checkpoint | BLUE TO RED
textbox | BLUE TO RED:
checkpoint | BLUE TO BLACK
textbox | BLUE TO BLACK:
checkpoint | BLUE TO EARTH
textbox | BLUE TO EARTH:
section | 4 - Polarity Test
checkpoint | RED TO RED
textbox | RED TO RED:
checkpoint | WHITE TO WHITE
textbox | WHITE TO WHITE:
checkpoint | BLUE TO BLUE
textbox | BLUE TO BLUE:
checkpoint | BLACK TO BLACK
textbox | BLACK TO BLACK:
section | 5 - Fault Loop Impedance (If Applicable)
checkpoint | Cables have been installed as per design calculations.
label | Note, if FAIL seek design clarification to adjust circuit breaker tripping curve characteristics.
section | 6 - Post Engerisation Checks (AS/NZS 3000) - Phase Rotation
checkpoint | Phase Rotation
bool | Clockwise →
bool | Anti Clockwise ←
section | 7 - Voltage Checks (AS/NZS 3000)
checkpoint | RED TO WHITE
textbox | RED TO WHITE:
checkpoint | RED TO BLACK
textbox | RED TO BLACK:
checkpoint | RED TO EARTH
textbox | RED TO EARTH:
checkpoint | WHITE TO BLUE
textbox | WHITE TO BLUE:
checkpoint | WHITE TO BLACK
textbox | WHITE TO BLACK:
checkpoint | WHITE TO EARTH
textbox | WHITE TO EARTH:
checkpoint | BLUE TO RED
textbox | BLUE TO RED:
checkpoint | BLUE TO BLACK
textbox | BLUE TO BLACK:
checkpoint | BLUE TO EARTH
textbox | BLUE TO EARTH:
section | Test Equipment
checkpoint | Multimeter
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date:
checkpoint | Insulation Resistance Tester
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date:
checkpoint | Phase Rotation Meter
textbox | Brand/Model
textbox | Serial No.
textbox | Calibration Due
textbox | Tester
date | Date: