## Master List Templates
Id | Type | Name | Values | Prompting Name
4f727a59-4299-4227-9052-e8b429dd1fd6 | checklist | Fire Dampers |  | Fire Dampers
3e7f85da-877b-4efa-b47b-efce9a349cce | section | Pre-Start Fire Damper
a125b3ab-1bd0-4c4d-8c71-2051fddc6705 | checkpoint | Area clear, access good, enough space for install
6ba5c600-debb-430a-a872-ca1c59e0c7a7 | checkpoint | Duct Route clear, Penetrations complete
79b55644-e611-4038-81bf-3c09f44b52a3 | section | First Fix Fire Damper
7eb77dd2-6432-4ae1-9810-c78af312c5e5 | checkpoint | Correct Fire Damper installed. (Insert Photo)
edb13b58-7d6c-4d0f-a300-f69795250fb9 | checkpoint | Fire Damper installed straight and level with correct orientation.
02e08761-75ee-43d2-9591-b920d72f825a | checkpoint | Breakaway joints either side of fire dampers, taped then cable tied.
d697b986-ba81-4a91-8993-ce055e73dfab | checkpoint | Fire Dampers installed to manufacturers specifications. Drop tested where applicable
cb49af99-b40d-4d66-97f2-46692fef3658 | checkpoint | Access Panels in duct for fire dampers.
28cba624-b158-4d97-8a03-bfa1a24e76d4 | checkpoint | Building Access Panel requirements are marked and given to builders
6a38b280-855c-4c00-8255-23a3f8cf5289 | checkpoint | Plans marked up for As Builts with Access Panel locations
d33ba6eb-28c8-4854-8b42-2940a154e9b8 | section | Second Fix Fire Damper
1d369191-28df-40f0-9afa-3521d492b676 | checkpoint | Fire Damper Label affixed, Asset Number applied.
99fcfadd-4ea2-45ef-b749-c0a4c1d2672b | checkpoint | Fire Dampers Access Panels still accessible for maintenance
5d2eb6ef-1c00-4070-a498-8e46333efb04 | checkpoint | Area left clean and tidy, finger prints removed
ae2acbc5-9afe-4989-8c9f-a1b92fad8b30 | checkpoint | Fire Damper sealed to structure both sides.
f68972b4-6d81-41aa-aa09-4be60adafed1 | section | Commission Fire Damper
35abf88d-b375-479f-8b77-924971281f8a | checkpoint | Drop Tested as applicable
3399aa37-48d7-492c-8a16-93ef940f0411 | checkpoint | Drop Test Motorised Fire Dampers with Fire Engineer.
7be34150-c368-48a3-ba66-611937573253 | checkpoint | Fire Damper Label filled out, photo uploaded.
40670fb4-21e7-4227-bdb5-faa6329dd3e3 | checkpoint | Form TSL05.8A, Fire/Smoke Damper Test Sheet, updated for Project Completion
91a77d34-03fe-4f7c-b402-578d38b427d1 | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
81f0f114-2c9e-432c-a8c0-88faee810925 | checklist | Commission AHU |  | Commission AHU
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
76b3144a-4748-4898-80b2-37d842fabe5b | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager
813e758e-827d-4454-87b1-eaecae590f23 | checkpoint | Electrical testing complete
fa23c06f-cf38-4416-b31e-9348eddbcaa3 | checkpoint | COC issued
993c02cf-dad0-4220-a6b1-a3a4fbe4f3fd | checklist | First Fix AHU |  | First Fix AHU
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
7eacc2fe-34c3-46ba-9a08-dcd55c942b2b | checkpoint | Unit installed straight and level and correct orientation.
7c3ba45d-e3f6-435e-80e7-f60d97ae279c | checkpoint | Unit bolted in place, seismically restrained and vibration isolated
f9383b9d-a298-410c-9bcc-9542e8cee3ac | checkpoint | Correct Unit installed
86464bec-3554-4bb3-b109-972ea8267536 | checkpoint | Unit serial No. recorded
c0470147-ecee-4d97-a7ef-238726259a52 | checkpoint | Good access to Service access panel
8bb39ee9-2c14-41c9-92cb-5fc80f320f1e | checkpoint | Fire dampers installed to manufacturers instructions. Drop tested where applicable
d74eb988-070b-482c-af33-60cdd0219048 | checkpoint | Breakaway joins either side of fire dampers
198acdd1-f687-4809-81eb-84c71f7601ac | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
6a33a191-6fd5-4600-a845-0a2a2837b126 | checkpoint | Ductwork straight/level and well supported incl any seismic restraints
c05daaab-263b-42e1-8a17-377ac98829b0 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
e29b6210-6a84-499a-83c5-43ef9a517543 | checkpoint | Balancing Dampers locked open and accessible
4944b224-0ef3-47fa-ac6b-3fa094e21e2d | checkpoint | Flexible ducts run straight/tight/well supported/secured close to grille location
e59aab07-7d73-4f78-a803-e0b336a0d7c0 | checkpoint | Flexible ducts taped then cable tied
53ffaa6c-8fbd-4a16-9564-a7347ccb627a | checkpoint | Supply cable installed correctly, protected and secured
c13b5514-211e-40b7-bd1e-c2516047f07c | checkpoint | Supply cable type, size and manufacturer
69eafa55-0377-40b0-a40a-7e43dd01c758 | checkpoint | Circuit protection type and rating
cef68385-16d6-4573-882a-cda4eeb9d9a5 | checkpoint | Correctly rated isolator installed to standards
48be4a50-c326-49c7-8585-398737a18941 | checkpoint | Interconnecting cables correctly installed and protected
d73b4887-bd24-4bf6-a88e-fc23fa56b1f3 | checkpoint | Control cables correct rating and type
8a952c1a-215c-44af-ad2a-1937ab179a77 | checkpoint | Screened cables drain to earth as per specifications
bad7d31a-9bf3-467f-ba99-e03cb6d000a1 | checkpoint | Control cables maintain minimum distance from power cables
5e658ec2-fa85-4ac6-abf9-de5c66a86606 | checkpoint | Daisy chain loops complete and correct
91fa9679-b0c8-436a-b4bb-30f59139cd6b | checkpoint | Remote controller cable installed
4098e8da-35b0-4d1d-864f-1fba353bb252 | checkpoint | Building Access Panel requirements are marked and given to builders
6b813996-b6ac-4677-b66b-04e149deb597 | checklist | Pre-Start AHU |  | Pre-Start AHU
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
2538f70e-e89a-43ec-b825-7da71b3fe845 | checkpoint | Area clear, access good, enough space for install
8aedc816-b91f-45b1-b979-1fc4dbfd05f9 | checkpoint | Duct Route clear, Penetrations complete
697d2161-2304-4689-85fb-70a4f479dfa8 | checkpoint | Nogs/Supports in place
3dccf641-65e1-423f-a0ae-893106acd230 | checklist | Second Fix AHU |  | Second Fix AHU
45e8814a-82cf-423b-a9fd-c3a56e777229 | section | Details
5026ba86-fb34-470e-9113-d5d792ec4a5e | checkpoint | Grilles installed square and level
f0228ebf-bb05-4ad8-8a7a-63c147f1aa36 | checkpoint | Flexible ducts taped then cable tied to grilles/boots
4190c827-2f54-481d-a77b-0b02dd98fc82 | checkpoint | Boots sealed to grilles
1f5d9178-cb1f-4268-95c8-7ac352e8bc72 | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
8593c67a-d30a-4a34-8a2a-5b6be33fd851 | checkpoint | Controllers fitted off. Heater Bank THT set
ca5c7049-6cb6-42b8-b561-8c62deb676c5 | checkpoint | Power fitted off
97bcb992-e417-4da3-b976-858f804d65b2 | checkpoint | Area left clean and tidy, finger prints removed
75d0a535-ad20-4d63-b602-6a19adb014e5 | checkpoint | Plant and controllers labelled