## Master List Templates
Id | Type | Name | Values | Prompting Name
4f727a59-4299-4227-9052-e8b429dd1fd6 | checklist | Fire Dampers |  | Fire Dampers
3e7f85da-877b-4efa-b47b-efce9a349cce | section | Pre-Start Fire Damper
a125b3ab-1bd0-4c4d-8c71-2051fddc6705 | checkpoint | Area clear, access good, enough space for install
6ba5c600-debb-430a-a872-ca1c59e0c7a7 | checkpoint | Duct Route clear, Penetrations complete
79b55644-e611-4038-81bf-3c09f44b52a3 | section | First Fix Fire Damper
7eb77dd2-6432-4ae1-9810-c78af312c5e5 | checkpoint | Correct Fire Damper installed. (Insert Photo)
edb13b58-7d6c-4d0f-a300-f69795250fb9 | checkpoint | Fire Damper installed straight and level with correct orientation.
02e08761-75ee-43d2-9591-b920d72f825a | checkpoint | Breakaway joints either side of fire dampers, taped then cable tied.
d697b986-ba81-4a91-8993-ce055e73dfab | checkpoint | Fire Dampers installed to manufacturers specifications. Drop tested where applicable
cb49af99-b40d-4d66-97f2-46692fef3658 | checkpoint | Access Panels in duct for fire dampers.
28cba624-b158-4d97-8a03-bfa1a24e76d4 | checkpoint | Building Access Panel requirements are marked and given to builders
6a38b280-855c-4c00-8255-23a3f8cf5289 | checkpoint | Plans marked up for As Builts with Access Panel locations
d33ba6eb-28c8-4854-8b42-2940a154e9b8 | section | Second Fix Fire Damper
1d369191-28df-40f0-9afa-3521d492b676 | checkpoint | Fire Damper Label affixed, Asset Number applied.
99fcfadd-4ea2-45ef-b749-c0a4c1d2672b | checkpoint | Fire Dampers Access Panels still accessible for maintenance
5d2eb6ef-1c00-4070-a498-8e46333efb04 | checkpoint | Area left clean and tidy, finger prints removed
ae2acbc5-9afe-4989-8c9f-a1b92fad8b30 | checkpoint | Fire Damper sealed to structure both sides.
f68972b4-6d81-41aa-aa09-4be60adafed1 | section | Commission Fire Damper
35abf88d-b375-479f-8b77-924971281f8a | checkpoint | Drop Tested as applicable
3399aa37-48d7-492c-8a16-93ef940f0411 | checkpoint | Drop Test Motorised Fire Dampers with Fire Engineer.
7be34150-c368-48a3-ba66-611937573253 | checkpoint | Fire Damper Label filled out, photo uploaded.
40670fb4-21e7-4227-bdb5-faa6329dd3e3 | checkpoint | Form TSL05.8A, Fire/Smoke Damper Test Sheet, updated for Project Completion
91a77d34-03fe-4f7c-b402-578d38b427d1 | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
19afb7aa-21d9-404d-ba73-1e590ca99e72 | checklist | Compliance / Completion Documentation |  | Compliance / Completion Documentation
d16748e0-dcb2-4305-98b7-961bbc23b35c | checkpoint | All relevant Compliance Documentation completed and attached below
5c9747de-21e6-5913-a4b3-473282d089fb | button | LBP Memorandum/ Record of works filled out, signed and attached | Yes,No
dd38c06b-ca93-5022-ad20-c5b5063612e6 | button | As-built plans attached | Yes,No
4d9c7323-3e03-5bb8-ae79-dc026ec69b6f | button | Any Additional Compliance Documentation - completed and attached (Warranties) | Yes,No
71e240be-73e3-5afe-b173-230c96ffc9ba | note | Do not select "Pass" HERE until all requirements have been marked as "Yes" & attached or you have selected "N/A"
8b5ac5f5-0e3a-41bd-9055-566ceab0c7fc | signoff | Request Sign Off
648d0b2f-0975-4170-99dc-4055db344331 | checklist | S - S - Ventilation - Apartment Ventilation |  | S - S - Ventilation - Apartment Ventilation
f49df266-c95f-4d27-929d-6bbd8e357f00 | section | Pre-start checks
c71b6a35-76a0-40d8-9345-3af66a69b5f2 | checkpoint | Penetrations done in floors and walls (if needed)
5cf74d9b-bdb1-4a13-a9c7-60747a422dac | checkpoint | Space for ducting (no trades in the way)
717c51f1-227e-44fc-a927-24c3d865d3d7 | checkpoint | Pipe through exterior wall installed by RHC to connect to
1030dca6-8ff7-4f42-8aca-0152f9578885 | checkpoint | Drawings and work scope confirmed
90d67b9b-b724-4030-a2b8-14d19ba8ad52 | section | First Fix
f9297bcd-c218-4220-a0e7-47982feb9169 | checkpoint | Ductwork run straight level and well supported
a79963f8-f3f2-458f-9fce-428700b6c1f3 | checkpoint | All ductwork joints sealed
78343bb3-4bb9-4685-a380-666817996399 | checkpoint | All SAB joints sealed and taped
c8388f3c-183f-4992-9e2d-73eb60de8355 | checkpoint | All flexible ducts cable tied and taped to duct
f53940a9-d926-43b6-9c7d-325a8b2404f1 | checkpoint | Identify locations and correct model of Fire damper to be installed
1c3f54f0-3e3f-45d0-8b67-c9822285f98b | checkpoint | Inform RHC PM Fire Dampers are ready for sealing
0c533401-e5ea-419d-aa8d-dd2f0bbd2002 | checkpoint | Using damper handle and fusible link, test damper operation and then set blade to required position
0d9ac0dd-3bfd-4c51-99b0-5016b40ef51f | checkpoint | Understand the requirements of the Seismic PS1 and identify the locations where engineered bracing is required
e3407389-1356-4fb0-8482-4b6421956e09 | checkpoint | Install using Materials specified in the PS1
184ad262-bb84-420b-9c41-81020ed1ce1c | checkpoint | Upload Photos of Install
e2fd8811-ad04-459b-bf91-079fac988ce3 | checkpoint | Refer back to Seismic Engineer for PS4 Production.
0de0266a-ed82-4a50-b708-8f0f1c18066f | checkpoint | Flexible ducts fixed in place to grille location
951ca6ea-4338-4461-986a-382e6ae9c517 | checkpoint | Identify Fan Upgrade Requirement
5afb5c3a-7208-4dfa-bd87-9725ef79f3f6 | checkpoint | Area Clear for Install of Ducting, Fan, and Control Box
faf861f7-9bb1-4c71-b643-f72b4f87fe98 | checkpoint | Install Fan, ducting and control box as per spec.
934ea566-971f-47c4-a8f4-bc399c73648a | checkpoint | Grille locations/access panels marked on plans
945f0f9d-b9ed-4299-b611-6d9f701d4c2f | checkpoint | Mechanical First Fix complete
b9c64c92-4b8d-4e15-9457-b44a2ca77752 | section | Second Fix
e3de83ac-0a70-4040-a17b-2ae106ec8660 | checkpoint | Ceiling fans installed square and level
919a85e3-6bf2-4eae-8f4f-2b1c88ea6ae1 | checkpoint | Kitchen range hood installed by RHC to connect to
cb0375d2-f4e9-4210-a871-091d90d3f52a | checkpoint | Fingerprints removed from grilles/walls/ceilings
b0c0ac01-c3f6-49d9-a049-ed9e5b130463 | checkpoint | Fan plugged in before install to ceiling
31fedf30-94ce-4417-a6b3-bca3d04eb1a8 | checkpoint | External louver supplied by TSL, installed by RHC completed
434e317e-e2f1-4d30-8d0d-876472e17cee | checkpoint | Commissioning form completed & given to TSL
3b4e18ab-ddb6-4750-b109-0eed9cc84244 | checkpoint | Mechanical Second Fix complete
20eeb212-5a7c-4d61-a6b4-6010301b260f | section | Commissioning
dc85f73e-88e9-4330-97c2-241d1bb48d19 | checkpoint | Correct product used as per requirements
9f0ed708-7345-47a9-80fe-4355c9269aab | checkpoint | Correct design followed as per drawings
fabc2207-dd08-41ab-a769-5ffec735a6f2 | checkpoint | Mechanical Plant commissioned
e6adc8df-5063-40d6-b842-7bc7185734cf | checkpoint | Inspections completed and issued to Foreman
e8e3722c-fcbb-447b-a4b8-db400ea31643 | signoff | CLICK AND SEND EMAIL TO FOREMAN TO SIGN FOR RECEIPT OF THE INSPECTION RESULTS
1691aeb2-a952-4f50-89b9-557139aa1713 | checklist | S - S - Ventilation - Carpark Ventilation - Jet Pulse Fan |  | S - S - Ventilation - Carpark Ventilation - Jet Pulse Fan
879ce160-7957-4674-a2d4-c5c4c4f73c12 | section | Pre-start check
a90bfbe8-dccb-4e26-a73c-63b76dd720ea | checkpoint | Area clear, access god, enough space for install
f882c456-7b04-4e03-acbc-341fda99182b | checkpoint | Duct Route clear, Penetrations completed
a0f00382-5e4e-44ed-8ca9-add2d98e367b | checkpoint | Nogs/Supports in place
fdf9f008-0d1c-4a0e-9600-3d0dfb1f3d23 | section | First Fix
9b9151c0-af59-47df-8714-c13ad2c3abdb | checkpoint | Access Panel requirements marked up on drawings and submitted to client
44e8ea96-97e1-4a60-ae1d-d3ffb61ee3a1 | checkpoint | All works from builders or other trades to enable Mechanical First fix to be completed (e.g.. drains, framing, penetrations)
c15b3ce4-e406-4929-b57d-93a03ffeda35 | checkpoint | Understand the requirements of the Seismic PS1 and identify the locations where engineered bracing is required
430ea837-7f63-4da1-8463-515b54197f6d | checkpoint | Install using Materials specified in the PS1
27a6f459-d377-488f-8f65-24fa99ee0a9a | checkpoint | Upload Photos of Install
f7e19e17-69cf-43ec-8a67-2b04b862e0d9 | checkpoint | Refer back to Seismic Engineer for PS4 Production.
75ccb2a9-fe9a-4485-b5de-8814d5ac8d7b | checkpoint | All seismic restraints in place (if needed)
f69157d4-977f-40f2-885c-547e3ed330ad | checkpoint | Mechanical First Fix complete
6d66aba8-e868-4c54-9167-ffcaa1729618 | section | Second Fix
a93afdec-c354-4984-be94-d8af4601e781 | checkpoint | All works from builders or other trades to enable Mechanical second fix to be completed (e.g.. painting, waterproofing...)
9d89bc99-4f34-484c-8ba9-3847499ff01f | checkpoint | Mechanical Second Fix complete
cef8d8b6-8830-4527-9535-f09c2d1a0186 | section | Commissioning
eb0a7ade-db07-434a-b1a3-dbddf1e4d6b6 | checkpoint | Good access to all areas of building
ecf148b1-0eb4-4c37-b198-c601c97dae25 | checkpoint | Power live to Mechanical Plant
fc5f0f49-dbc3-4311-ad70-f14f8fd57a8f | checkpoint | Mechanical Plant commissioned
8c9481e0-dc92-4afc-bb39-0d8877a31541 | checkpoint | Inspections completed and issued to Foreman
e86f9742-fb57-4e33-9d5e-795a195e9daf | signoff | CLICK AND SEND EMAIL TO FOREMAN TO SIGN FOR RECEIPT OF THE INSPECTION RESULTS
ee80adbf-8d5e-48df-b86b-52b2f5cb68b4 | checklist | S - S - Ventilation - Corridors Ventilation |  | S - S - Ventilation - Corridors Ventilation
1b6ddc6c-f618-4b48-a015-a9a74850ed36 | section | Pre-start checks
48c977fe-e21e-4d91-8e20-3157c7f7e993 | checkpoint | Area clear, access god, enough space for install
4569d304-7c77-4bcb-82c4-9fb3f19157ed | checkpoint | Duct Route clear, Penetrations completed
07c25554-7c11-4a01-8774-1ff1773c4683 | checkpoint | Nogs/Supports in place
1d3149e0-21bb-4d28-a5ad-9152b2889d8d | section | First Fix
bfa2bf89-a248-43a7-bc06-52304db76bc4 | checkpoint | Access Panel requirements marked up on drawings and submitted to client
7bc7a6ba-a707-45b1-abe1-cb3bd3524c1e | checkpoint | All works from builders or other trades to enable Mechanical First fix to be completed (e.g.. drains, framing, penetrations)
3d957a68-c04a-4beb-a01e-f768e2e099f9 | checkpoint | All flexible ducts cable tied and taped to duct
66b7960e-f237-49ca-900d-242d455d1956 | checkpoint | Identify locations and correct model of Fire damper to be installed
c6cf1c76-fb81-4eec-bde5-19388735a60b | checkpoint | Install to Manufacturers Specifications
fb568164-55ec-4dd5-8e78-a744b18d5450 | checkpoint | Inform RHC PM Fire Dampers are ready for sealing
5bbad070-aaba-4ba4-9c27-f431bce69d1b | checkpoint | Using damper handle and fusible link, test damper operation and then set blade to required position
60fe0764-0f53-4d8b-a161-1eec9b473631 | checkpoint | Understand the requirements of the Seismic PS1 and identify the locations where engineered bracing is required
f0dcc32d-4f70-4514-ae53-d11f7ea2c9d4 | checkpoint | Install using Materials specified in the PS1
c30af342-88bc-4a4e-a2eb-049b3e4c6a63 | checkpoint | Upload Photos of Install
5320f330-869b-4d04-9f1a-0e50d2269f75 | checkpoint | Refer back to Seismic Engineer for PS4 Production.
a666c2b7-7d39-4c58-a91e-462458a583cc | checkpoint | Mechanical First Fix complete
9c044002-e71f-4d52-a4af-e716300972d5 | section | Second Fix
4a5711d1-fb77-4cf5-afa8-c99c085858f3 | checkpoint | All works from builders or other trades to enable Mechanical second fix to be completed (e.g.. painting, waterproofing...)
1a42eb08-d207-4b1b-a681-e842c8d7b196 | checkpoint | Mechanical Second Fix complete
35e7a71b-bc6d-48fd-a4a0-f51d532e42fb | section | Commissioning
c514953c-25f9-4cf7-9824-e25c3bf2fa39 | checkpoint | Mechanical Plant commissioned
746259e7-d0ce-4539-9e4f-ebf12456eb95 | checkpoint | Inspections completed and issued to Foreman
8970f13a-10dd-4cd1-80d1-f2450cfcb3c3 | signoff | CLICK AND SEND EMAIL TO FOREMAN TO SIGN FOR RECEIPT OF THE INSPECTION RESULTS
558aae4e-56b8-48ac-869c-52f41e94e826 | checklist | Split HW |  | Split HW
f1a0891d-5e04-4049-b831-423660ea5358 | section | Pre-start
43275f81-e1d6-4c59-bdb2-98c73d398703 | checkpoint | Area clear, access good, enough space for install
bfd29da9-01d4-458e-9b24-84bcdc8fd98e | checkpoint | Area/base/wall ready for outdoor unit
36272e48-9118-4a7c-9389-866cdb133ead | checkpoint | Any required drains for outdoor unit in place
b504004b-38c8-4da5-b71f-fdf805866ba9 | checkpoint | Pipework route all clear, penetrations complete (2-3 Photos attached)
2127454a-2035-4d59-94bc-ef576bc23137 | checkpoint | Nogs in place (2-3 Photos attached)
ac010d44-4924-45d2-907a-698ceef8a797 | checkpoint | Drain 1m from Indoor unit location by plumber
9a1a6354-d789-4889-977d-ae35a87b1637 | section | First Fix
520145f8-068a-4b1d-ad42-0b29cb91f5e5 | checkpoint | Access Panel requirements marked up on drawings and submitted to client
ba05768c-9da5-4363-a114-bbfc5c9c3255 | checkpoint | All works from builders or other trades to enable Mechanical First is to be completed (e.g. drains, framing, penetration)
274fc2b5-89b3-4cdb-aa42-c9a8ec8ac5eb | checkpoint | Mechanical First Fix completed (2-3 Photos attached)
1c2b41c5-f23f-41e1-99ef-f28b4b3c3d25 | signoff | Request sign off
d30f99e9-1b5f-4c65-b55c-4aaa4ce5163b | section | Second Fix
a1c022ec-a8d3-4104-a857-5969e6da28ac | checkpoint | Area clear and access good for Second Fix
9019493d-a738-49fe-baf7-38de65e8a9f2 | checkpoint | All works from builders or other trades to enable Mechanical second fix to be completed (e.g. painting, waterproofing)
b570c648-7f52-4392-84c7-425c47362185 | checkpoint | Mechanical Second Fix completed (2-3 Photos attached)
ac783328-8354-4d7b-bdb0-1b4b567fc1bc | signoff | Request sign off
c8193483-801f-4251-8333-8b130f314efd | section | Commission
3b29f1e3-6c62-4be5-9bf4-12fbfff90b23 | checkpoint | Good access to all areas of building
b7440dfb-2fc8-4df4-83eb-4387ecf59d48 | checkpoint | Power live to Mechanical Plant
fcee8c52-d2b3-47b8-9be5-a6fc16871c4c | checkpoint | Mechanical Plant commissioned (2-3 Photos attached)
a08fa05c-b182-4ec9-8705-f3a0cd8ed1af | signoff | Request sign off
8381598f-89bf-4419-899a-689c02a0ed21 | checklist | Ventilation, Ducting, Fans |  | Ventilation, ducting , fans
1a56e4ce-5cd4-4588-a291-74c1e8a8dcb7 | section | Pre-start: SA Fan
e6acd12c-6e86-4ba6-a213-43e9e69d9520 | checkpoint | Area clear, access good, enough space for install
30727556-a669-4009-98ea-89e37ea1c400 | checkpoint | Duct route clear, Penetrations complete
d11117b1-9126-4b45-957f-65d422c108c2 | checkpoint | Nogs/Supports in place
baa6be73-ea93-41cc-b929-fa8da8ef726b | signoff | Request sign off
4196b8d8-dbc9-4cf3-8f3a-ba52866b4068 | section | First Fix: SA Fan
3576bf44-cbaf-4483-a640-3d554c400f36 | checkpoint | Access Panel requirements marked up on drawings and submitted to client
38c67de5-8a86-457d-8ace-f359b16397f0 | checkpoint | All works from builders or other trades to enable Mechanical First fix to be completed (e.g. drains, framing, penetrations…)
5ff42edc-9d14-4af8-aead-7340eda463ee | checkpoint | Mechanical First Fix completed
086f1f25-49f8-4159-8e14-2fc784dc0e7c | signoff | Request sign off
f8eb70ed-acc3-4b50-98f8-2a5bbcd9d036 | section | Second Fix:SA Fan
edbcdb00-6f04-4ccf-a75d-ba577f93857c | checkpoint | Area clear and access good for Second Fix
3b7282e7-6ea2-4a7e-9d11-11888ed63910 | checkpoint | All works from builders or other trades to enable Mechanical second fix to be completed (e.g. painting, waterproofing...)
acb5a105-2d17-4618-973e-cec78cb4c7eb | checkpoint | Mechanical Second Fix completed
2748799e-de1d-4f04-b769-92ab44a024a4 | signoff | Request sign off
ca1e797f-cfde-4042-993d-d6786bca9eec | section | Commission:SA Fan
1bf33edf-038b-4fcd-bed0-036cbcabd31c | checkpoint | Clear access to all areas of building
89b37990-2755-4f04-a7eb-16a84cee6522 | checkpoint | Power live to Mechanical Plant
471f0699-3d26-4e6a-a0fc-39fced423d7b | checkpoint | Mechanical Plant commissioned
6b7c61de-d168-4293-af56-7395de6d551e | signoff | Request sign off