## Master List Templates
Id | Type | Name | Values | Prompting Name
4f727a59-4299-4227-9052-e8b429dd1fd6 | checklist | Fire Dampers |  | Fire Dampers
3e7f85da-877b-4efa-b47b-efce9a349cce | section | Pre-Start Fire Damper
a125b3ab-1bd0-4c4d-8c71-2051fddc6705 | checkpoint | Area clear, access good, enough space for install
6ba5c600-debb-430a-a872-ca1c59e0c7a7 | checkpoint | Duct Route clear, Penetrations complete
79b55644-e611-4038-81bf-3c09f44b52a3 | section | First Fix Fire Damper
7eb77dd2-6432-4ae1-9810-c78af312c5e5 | checkpoint | Correct Fire Damper installed. (Insert Photo)
edb13b58-7d6c-4d0f-a300-f69795250fb9 | checkpoint | Fire Damper installed straight and level with correct orientation.
02e08761-75ee-43d2-9591-b920d72f825a | checkpoint | Breakaway joints either side of fire dampers, taped then cable tied.
d697b986-ba81-4a91-8993-ce055e73dfab | checkpoint | Fire Dampers installed to manufacturers specifications. Drop tested where applicable
cb49af99-b40d-4d66-97f2-46692fef3658 | checkpoint | Access Panels in duct for fire dampers.
28cba624-b158-4d97-8a03-bfa1a24e76d4 | checkpoint | Building Access Panel requirements are marked and given to builders
6a38b280-855c-4c00-8255-23a3f8cf5289 | checkpoint | Plans marked up for As Builts with Access Panel locations
d33ba6eb-28c8-4854-8b42-2940a154e9b8 | section | Second Fix Fire Damper
1d369191-28df-40f0-9afa-3521d492b676 | checkpoint | Fire Damper Label affixed, Asset Number applied.
99fcfadd-4ea2-45ef-b749-c0a4c1d2672b | checkpoint | Fire Dampers Access Panels still accessible for maintenance
5d2eb6ef-1c00-4070-a498-8e46333efb04 | checkpoint | Area left clean and tidy, finger prints removed
ae2acbc5-9afe-4989-8c9f-a1b92fad8b30 | checkpoint | Fire Damper sealed to structure both sides.
f68972b4-6d81-41aa-aa09-4be60adafed1 | section | Commission Fire Damper
35abf88d-b375-479f-8b77-924971281f8a | checkpoint | Drop Tested as applicable
3399aa37-48d7-492c-8a16-93ef940f0411 | checkpoint | Drop Test Motorised Fire Dampers with Fire Engineer.
7be34150-c368-48a3-ba66-611937573253 | checkpoint | Fire Damper Label filled out, photo uploaded.
40670fb4-21e7-4227-bdb5-faa6329dd3e3 | checkpoint | Form TSL05.8A, Fire/Smoke Damper Test Sheet, updated for Project Completion
91a77d34-03fe-4f7c-b402-578d38b427d1 | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager

## Project Checklist Templates
Id | Type | Name | Values | Prompting Name
ed6d0f97-3a1f-4a54-83d6-110a694c9693 | checklist | Extract Fan |  | Extract Fan
2d958b72-993a-443f-bfee-69d37e7b2148 | section | Pre-Start Ext Fan
bf4ec18a-63f1-4ad2-b825-b9ccc721ccb5 | checkpoint | Area clear, access good, enough space for install
28a00440-40e3-4211-b922-0068b03aa735 | checkpoint | Duct Route clear, Penetrations complete
09185524-4679-4c96-b1f7-1fc983c427f8 | checkpoint | Nogs/Supports in place
b6259fb6-62e2-4974-958b-7da830780024 | section | First Fix Ext Fan
40241736-0de6-4bdf-b837-5849b0212e91 | checkpoint | Fan installed straight and level and correct orientation.
26d446ec-81db-4bc5-aef5-09ed774232e1 | checkpoint | Fan or Cowl sealed to Upstand
f62171d1-ffed-4c42-93a5-af0fe49cf070 | checkpoint | Correct Fan installed
51f3c227-0142-4145-bae7-e2a8c4718d86 | checkpoint | Fan serial No. recorded
44dee849-92b3-4d3c-8cb7-c0d32ee97d6b | checkpoint | Access Panels in duct for fire dampers, filters, cleaning etc
7f438686-59e8-43e5-b912-03066155d599 | checkpoint | Duct fittings/joins sealed and mechanically fixed to duct. SAB joins sealed
2f1755c6-5e26-4eed-be19-bdb68cfbd365 | checkpoint | Flexible ducts run straight/tight/well supported/secured close to grille location
5e1fe1e7-2d60-42fe-90e3-a5839c0d7c4a | checkpoint | Flexible ducts taped then cable tied
771f40ea-f4d2-4102-b2ba-36c7acf2edbb | checkpoint | Supply cable installed correctly, protected and secured
4e8a3252-bf1f-4855-9da4-5e7171e1a628 | checkpoint | Interconnecting cables correctly installed and protected
30ec1458-711f-493b-9213-4b7c0e64e9a8 | checkpoint | Plans marked up for As Builts and 2nd fix grille locations
0119c945-b461-4bc0-9d68-d19b1238112e | section | Second Fix Ext Fan
0978fe18-441b-403f-ab59-d8e4ae9bd863 | checkpoint | Grilles installed square and level
788da450-a205-4006-b744-b12e0dace608 | checkpoint | Flexible ducts taped then cable tied to grilles/boots
3ed7195e-3685-4a8b-b72b-4aea91cde6cd | checkpoint | Boots sealed to grilles
e9c6b893-ffdd-4757-8d7d-f124c7362b77 | checkpoint | Fans/Filters/Dampers/Access Panels etc all still accessible for maintenance
d79dea2e-691c-4e25-a4fe-3ef34e0add48 | checkpoint | Controllers fitted off
c6a4b01e-98ec-440a-ac24-34c26d71d5f1 | checkpoint | Power fitted off
5ca9c28b-4460-4416-b7ce-38ea8e2afd47 | checkpoint | Area left clean and tidy, fingerprints removed
6f8bbe4e-618c-4448-9834-b4e9a44f9f24 | checkpoint | Plant and controllers labelled
bbf93f71-2097-4787-8e32-e9c1783bb1ca | section | Commission Ext Fan
42563e82-fd68-476e-a404-61719271534c | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager
3f94319e-bf38-426b-8697-e6fc2e90c9d1 | checkpoint | Electrical testing complete
0c756328-18cf-493a-8349-9b8064408692 | checkpoint | COC issued
cc0bb5fd-ac3d-4bb7-8be5-644da19459f2 | checklist | Split High Wall |  | Split High Wall
210c0aad-b3a7-42de-a2ba-40ff35fd28cc | section | Pre-Start HW
446f60b2-0ba4-4419-9940-3dfabe7bdceb | checkpoint | Area clear, access good, enough space for install
d9f2c88f-33b2-42d9-a3b3-d137bd401d8f | checkpoint | Area/base ready for outdoor unit
0a434c11-1601-4473-a02a-ce18dbe8bcf7 | checkpoint | Any required drains for outdoor unit in place
fcd22486-c1ff-42b2-9c0a-fd4a6e4f39bd | checkpoint | Pipework route all clear, penetrations complete
e3110a39-36dc-406f-890e-423fdeacc445 | checkpoint | Nogs in place
2ec51b43-211b-47c2-9d7b-c533b2456435 | checkpoint | Drain 1m from Indoor unit location by plumber
a3fb0290-c03b-4efc-bbfc-6223c4edb083 | section | First Fix HW
d8bf9f21-2319-4956-931b-b1efe5dfbfc5 | checkpoint | Pipework Insulated complete length
a4c948e2-bc60-412b-9c66-778f51c302aa | checkpoint | Drain installed and insulated
99ebad0a-2f2c-49a1-9024-402c9da0dfee | checkpoint | Supply cable installed correctly, protected and secured
0e3ac2bd-beaa-4bfd-8085-088e457efbb1 | checkpoint | Interconnecting cables correctly installed and protected
c0dfb070-68df-4552-b6e8-807981ebc025 | section | Second Fix HW
05175d0d-fba4-4c8d-8f61-d0efb42c4e9b | checkpoint | System pressure checked and still holding 1st fix pressure
5241e948-a7fe-4a48-b706-30e53c28b036 | checkpoint | Indoor unit secure, level and tight to wall
8a3d212c-ac59-4b42-9081-bb8919ca1bc1 | checkpoint | Correct Indoor unit installed
f79280f6-12b9-45ea-8147-59ec1158b5cb | checkpoint | Outdoor unit secure and level
b712e7a6-10f7-431d-949a-7357b979b9ed | checkpoint | Correct Outdoor unit installed
7b798420-90a5-4083-8b2e-023836ec0d7f | checkpoint | Indoor unit serial no. recorded
b1d63154-fc79-435e-9d7c-4a4283d428aa | checkpoint | Outdoor Unit serial no. recorded
57cbda1a-04c2-43f1-8e4b-5599482aa9de | checkpoint | Area left clean and tidy, fingerprints removed
7500681d-b631-4835-ae72-4fbf96039ece | section | Commission
dac0ab3d-6cee-4847-8521-125fe63c44ee | checkpoint | Installer confirmed commissioned and paperwork submitted
44b0d794-5747-41a1-81be-4513f0d85b09 | checkpoint | Commissioning paperwork reviewed and accepted by Project Manager
a90120b9-b174-4a02-a696-d6ab17f1adc7 | checkpoint | Electrical testing complete